- INTENT OF SPECIFICATION:

This specification covers design manufacture, testing at Vendor’s works and delivery of L.T. Power Cables.

- APPLICABLE STANDARDS:

IS 9968 Part-I (1988)	: Specification for Elastomer / Ethylene Propylene

Rubber(EPR) insulated cables

IS 8130 (1984)		: Specification for conductors of insulated electrical cables 				 and flexible cords.

IS 6380			: Specification for elastomer / EPR insulation and sheath of 					  electric cables

- CLASS F3 CABLE CONSTRUCTION REQUIREMENTS:

  - Voltage grade		:	1100 V.

  - Conductor		:	Conductor shall be tinned annealed Copper 					wires complying with requirements of IS : 					8130 – 1984.

  - Separator Tape	:	A separator tape made of suitable material 					shall be applied over the conductor.

  - Insulation		:	Insulation shall be of elastomeric/EPR 							compound conforming to Type IE - 2 of 						IS: 6380- 1984.

  - Core identification	:	As per IEC

  - Tape			:	Proofed tape or PETP tape or plastic tape or 					any other suitable tape may be applied over 					insulation. The tape when provided shall be 					applied with an overlap.

  - Braiding			:	Braiding of suitable material shall be applied 					reasonably close, but not so tight as to 						damage the insulation.

  - Compounding and 	:	Proper Compounding and Varnishing shall be Varnishing			done.

  - Laying of cores	:	Cores shall be laid together with a suitable 					right hand lay. Fillers in interstices shall be 					used to provide reasonable circularity of laid 					up cable.

  - Binder Tape		:	Proofed Tape or PETP tape or Plastic tape or 					any other suitable tape over laid up cores 					shall be applied.

  - Sheath			:	Sheath shall be applied by extrusion process 					and the colour of sheath shall be black. 						Sheath shall consist of elastomeric compound 					complying with requirements of type SE – 4 of 					IS : 6380

- TESTS:

All acceptance tests and routine tests shall be carried out on all cables as per IS 9968 part 1, at vendor’s work in the presence of purchaser’s representative. Type test reports of similar cables wherever they are called for shall be furnished.

- CABLE IDENTIFICATION, PACKING AND MARKING

Manufacturer and cable identification shall be done through out the length of the cable by printing or indenting or embossing or any other suitable method. Distance between any two consecutive printings shall be not more than 1 metre.

Cables shall be delivered in neatly rolled on wooden drums, with both ends sealed with moisture proof sealing.

All information regarding cable shall be marked on cable drum.

- DOCUMENTATION:

  - 2 Copies of filled-up Technical data sheets to be furnished along with the bid.

  - Quality Assurance Schedules.

  - 3 Copies of Test Certificates within one week after the inspection.

  - 5 Sets of final documents comprising of TDS, catalogues & certificates.

  - Cables offered by Non-Indian vendors shall comply with IEC 502 & other relevant IEC specifications.

TECHNICAL DATA SHEETS

(To be filled in and sent along with the bid for each type of cable)

S.No.	Description

Make

Type

Applicable Standard

Voltage Grade

Max. Conductor temperature:

Continuous Deg. C.

Short time Deg. C.

CONDUCTOR:

Material

Size (Sq. mm)

No. of wires & diameter of each wire (No. / mm)

INSULATION:

Material

Size (sq. mm)

Thickness(normal ) mm.

INNER SHEATH:

Material

Type

Thickness (normal) mm.

Extruded (Yes/No.)

Approx. outside dia over inner sheath (mm).

Thickness (normal) mm

OVERALL SHEATH:

Material

Type

Thickness (nominal) mm.

APPROX OVERALL DIAMETER (MM):

CONTINUOUS CURRENT RATING FOR STANDARD IS CONDITION LAID

DIRECT : (Amps)

In ground

In duct

In all

SHORT CIRCUIT CURRENT FOR 1 Sec (KA)

ELECTRICAL PARAMETERS AT Max. OPERATING TEMP (Ohm/km)

Resistance (DC/AC)

Reactance at 50 Hz.

Capacitance.

TOTAL LOSSES (WATTS/METER):