## Sheet1
Design ,engineering, supply,erection,testing and commissioning of 4 TPH Boiler with necessary accessories,mountings,fittings,pipe lines and other necessary requirements.
4 TPH , 10.5 KG/cm2 (g) , 180 deg C, Natural GAS / LPG / HFO fired Steam Boiler
REQUIREMENTS
S.No | BHEL SPECIFICATIONS |  | VENDOR ACCEPTANCE | VENDOR OFFERED | REMARKS
1 | Feed water temperature (Available) | 280 C | VENDOR TO CONFIRM
2 | Net steam required | 3.5 TPH* (Not F&A 1000 C (i.e Net)) | VENDOR TO CONFIRM
3 | Normal Operating pressure | 10.5 Kg/cm2 (Gauge) * (Not design pressure) | VENDOR TO CONFIRM
4 | Dryness fraction | 0.98 and above | VENDOR TO CONFIRM
5 | Turn down Ratio required | 0.33333 | VENDOR TO CONFIRM
6 | Temperature at min load required | 1700 C | VENDOR TO CONFIRM
7 | Temperature at MCR | 1800 C | VENDOR TO CONFIRM
8 | Emission levels | As per APPCB Standards, Hyderabad | VENDOR TO CONFIRM
9 | Design Code | IBR 1950 with latest amendments | VENDOR TO CONFIRM
10 | Available Instrument air pressure | 3 Kg/Cm2(g) | VENDOR TO CONFIRM
11 | Electrical explosion proof intrinsic safety requirements are needed for all electric equipments | All motors, electrical devices and panels | VENDOR TO CONFIRM
12 | IBR statutory formalities | All to be taken care by Vendor | VENDOR TO CONFIRM
13 | Location of Boiler | Ramachandrapuram,Hyderabad, All transportation charges will be in the scope of vendor | VENDOR TO CONFIRM
14 | Silencers for air vents and Safety valves required | < 85 dB | VENDOR TO CONFIRM
15 | Sound from FD fan ( 1Mtr distance ) | < 85 dB | VENDOR TO CONFIRM
16 | Automatic combustion control required | Auto regulation is required for Air, Fuel (HFO/Natural gas/LPG) for complete combustion of fuel by maintaining O2% below 4.5% | VENDOR TO CONFIRM
17 | Type of Fuel to be used | Natural Gas/LPG/HFO, (Dual Burner Is to be supplied by the vendor for these fuels) | VENDOR TO CONFIRM
18 | Three element controller is required for Drum level, Steam flow and Water flow | Operator will close/open range valve while stop valve will be kept in full open condition. Hence as per the steam requirement water flow, Fuel flow, air flow inputs to boiler are to be regulated automatically. | VENDOR TO CONFIRM
19 | Existing DM Plant to be used | Approximately 750 meters distance from existing DM plant to new packaged boiler | VENDOR TO CONFIRM
20 | Max and Min ambient temperatures | 52 / 18 deg C | VENDOR TO CONFIRM
21 | Plant altitude | 556.5 Meters | VENDOR TO CONFIRM
22 | TDS of feed water(Available) | < 5PPM | VENDOR TO CONFIRM
23 | Available LPG Gas pressure | 1+/- 0.5 Kg/cm2 @500 m3/hr | VENDOR TO CONFIRM
24 | DM storage tank at new boiler should be having capacity of 30 KL and should work as atmospheric de-aerator. |  | VENDOR TO CONFIRM
25 | HFO storage tank capacity should be 25 KL with necessary required electric heaters to raise the temperature up to 120 deg C |  | VENDOR TO CONFIRM
26 | Both DM/HFO tanks should be having necessary stair cases along with railings with level gauges and safety fittings. |  | VENDOR TO CONFIRM
Material Specification for Shell and Shell attachments
27 | Shell,Furnace,Reversal Chamber and Tube Plates | SA 515/516 | VENDOR TO SPECIFY
28 | Furnace access Tube | SA 515/516 | VENDOR TO SPECIFY
29 | Stay bars | IBR1950 | VENDOR TO SPECIFY
30 | Plain and stay tubes | BS 3059 ERW 320 | VENDOR TO SPECIFY
31 | Man door Head holes, mud door lifting lug | A-531 Cl-1 | VENDOR TO SPECIFY
32 | Pads (Valves) | SA 515-70 | VENDOR TO SPECIFY
33 | Bosses | SA 515-70 | VENDOR TO SPECIFY
34 | Stand pipes | SA 106 GRB | VENDOR TO SPECIFY
35 | Inter connecting piping | IS 1239 ERW | VENDOR TO SPECIFY
36 | Boiler internal dry pan & perforated Tray | SS | VENDOR TO SPECIFY
37 | Valves | IBR certified for steam service | VENDOR TO SPECIFY
ERECTION & SUPPLY
38 | All Electrical items required to be supplied and installed by vendor |  | VENDOR TO CONFIRM
39 | RTD’s,Thermocouples,Level controllers with indicator, Flow controllers(For HFO,Steam,Natural gas/LPG,water,condensate,air),online conductivity meter,I/P’s,solenoid valves, Transmitters etc required are to be supplied and installed by vendor |  | VENDOR TO CONFIRM
40 | Gas train for controlling LPG/Natural Gas is to be supplied and installed by vendor |  | VENDOR TO CONFIRM
41 | Expansion joints required in steam line are to be supplied and installed by vendor |  | VENDOR TO CONFIRM
42 | Stop valve, Range valve, Bypass valves, Auto control valves, safety valves, drain valves, traps etc required are to be supplied and installed by vendor. |  | VENDOR TO CONFIRM
43 | All civil foundation, Boundary wall, shed for Boiler covering all associated equipments with supply of required material will be in the scope of Vendor |  | VENDOR TO CONFIRM
44 | DM tank (Atmospheric De-aerator) with level indicator and controller is to be supplied and installed by vendor.All inlet and outlet connections along with supply of material is to be done by vendor. |  | VENDOR TO CONFIRM
45 | Boiler steam out let should be connected to existing 02 shop steam line with necessary valves and fittings. |  | VENDOR TO SPECIFY
46 | All necessary paintings and insulation material required will be in the scope of vendor. |  | VENDOR TO SPECIFY
47 | Feed water, Boiler water, Steam sampling Unit along with coolers and associated Piping are to be supplied and installed by vendor |  | VENDOR TO SPECIFY EQUIPMENT DETAILS
48 | All Electrical/Instrumentation cabling and earthling is to be supplied and installed by vendor | Standard cabling and earthing is to be supplied and installed by the vendor | VENDOR TO CONFIRM
49 | Deminaralized water pumps(1R+1S), valves, fittings, structural supports and piping upto 4tph Boiler Location along with isolating valves at existing DM Plant is to be supplied and installed by the vendor | 4tph Boiler to be installed at 750metres away from existing DM Plant | VENDOR TO CONFIRM
50 | Auto control valve station for DM Water along with isolation valves (after DM Pumps in existing Boiler House) with required Pipeline is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
51 | By pass valves for the above (Point No.. 50) auto control valve station with pipe line is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
52 | DM Storage tank (SS304) at 4tph (New Boiler location) of capacity 30KL to handle DM Water upto 900C is to be supplied and installed by the vendor. Condensate return will enter into this tank, hence necessary safety fittings to be arranged. | Suitable condensate return pumps along with ss pipe lining is to be designed and erected.DM water to new boiler storage tank will be supplied from existing DM plant. Suitable pumps,valves,fittings and ss pipe lining are to be designed and to be erected. | VENDOR TO CONFIRM
53 | Centrifugal boiler feed water pumps(1R+1S) along with isolating valves is to be supplied with Balancing disc, and installed by vendor | not with piston (KSB make) | VENDOR TO CONFIRM
54 | Auto control valve station along with isolating valves after DM storage tank for feed water pumping to boiler along with pipeline is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
55 | By pass valves for the above (Point No.. 54) auto control valve station with pipe line is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
56 | Flow meter along with integrator is to be arranged after above auto control valve station. |  | VENDOR TO CONFIRM
57 | Audio Visual alarms for abnormal working conditions to be provided by vendor |  | VENDOR TO CONFIRM
58 | Platforms and ladders to be provided by vendor |  | VENDOR TO CONFIRM
59 | Control panel with switches,relays,contactors,fuses,dust & vermin proof is to be supplied and installed by vendor |  | VENDOR TO CONFIRM
60 | Flue gas ducting from Boiler outlet to existing chimney is to be supplied and installed by vendor | with IS Standard | VENDOR TO SPECIFY
61 | LPG lining from Main line to Boiler is to be supplied by vendor with an isolating valve before auto regulation |  | VENDOR TO CONFIRM
62 | Gas train is to be supplied and installed by vendor |  | VENDOR TO CONFIRM
63 | Suitable non corrosive HFO tank (25KL)near by new packaged boiler with inbuilt electric heaters to raise the temperature of HFO up to 1200 C is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
64 | Fuel oil filters (1R+1S) along with isolating valves and pipelining after HFO tank is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
65 | HFO oil pumps (1R+1S) with isolating valves is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
66 | Auto Control valve station with isolating valves and necessary piping after HFO Pumps is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
67 | By pass valves for the above (Point No.. 66) auto control valve station with pipe line is to be supplied and installed by the vendor |  | VENDOR TO CONFIRM
68 | All steam, blow down, drain piping and safety valve along with inlet and outlet piping is to be supplied and installed by vendor |  | VENDOR TO CONFIRM
69 | Steam Traps and along with drain valves at required locations are to be supplied and installed by vendor |  | VENDOR TO CONFIRM
70 | All Insulation / cladding material is to supplied and installed by vendor | Standard Insulation | VENDOR TO SPECIFY
71 | All Spares required for three years to be supplied by vendor |  | VENDOR TO SPECIFY
72 | All standard painting works to be done by vendor along with supply of material |  | VENDOR TO SPECIFY
73 | LPG leak detectors along with Interlocks are to be provided |  | VENDOR TO SPECIFY
74 | Well designed shed to be erected with all rigid supports to cover boiler,auxiallaries,DM storage tank,HFO storage tank, Operator control room consisting controlling panel and it should not allow any rainy water to enter inside shed |  | VENDOR TO CONFIRM
Pressure gauges are to be supplied and installed at following locations
75 | FD fan delivery | standard pressure gauge | VENDOR TO SPECIFY
76 | Boiler main steam | standard pressure gauge | VENDOR TO SPECIFY
77 | Feed water pumps discharge | standard pressure gauge | VENDOR TO SPECIFY
78 | Feed water pumps strainers diff pressure | standard pressure gauge | VENDOR TO SPECIFY
79 | DM pumps discharge line | standard pressure gauge | VENDOR TO SPECIFY
80 | Before and after gas train | standard pressure gauge | VENDOR TO SPECIFY
81 | Air Inlet to Boiler | standard pressure gauge | VENDOR TO SPECIFY
82 | HFO line before burner | standard pressure gauge | VENDOR TO SPECIFY
83 | Before Chimney | standard pressure gauge | VENDOR TO SPECIFY
84 | DM storage tank 30KL (Atmospheric De-aerator) | standard pressure gauge | VENDOR TO SPECIFY
Temperature gauges are to be supplied and installed at the following points
85 | Before chimney | Standard temperature gauge | VENDOR TO SPECIFY
86 | DM storage tank 30KL | Standard temperature gauge | VENDOR TO SPECIFY
87 | Feed water to boiler | Standard temperature gauge | VENDOR TO SPECIFY
88 | Boiler outlet steam | Standard temperature gauge | VENDOR TO SPECIFY
89 | HFO line before burner | Standard temperature gauge | VENDOR TO SPECIFY
Level indicators are to be supplied and installed at following locations
90 | DM tank near new Boiler |  | VENDOR TO SPECIFY
91 | HFO Tank near new Boiler |  | VENDOR TO SPECIFY
Level indicators with controllers required at following locations (Three element) along with Integrators are to be supplied and installed
92 | Drum level, steam flow, water flow |  | VENDOR TO SPECIFY
Flow meters with integrators required at following locations are to be supplied and installed
93 | Feed water(After FW control valve station) |  | VENDOR TO SPECIFY
94 | Steam (After stop valve) |  | VENDOR TO SPECIFY
95 | HFO line before burners |  | VENDOR TO SPECIFY
96 | Gas line before gas train |  | VENDOR TO SPECIFY
Auto control valves, isolating valves, bypass lines are to be supplied and installed at following locations
97 | Feed water inlet to boiler |  | VENDOR TO SPECIFY
98 | Condensate return drain valve | Should be linked to condensate conductivity < 15 micro S/CM | VENDOR TO SPECIFY
99 | HFO inlet to burner |  | VENDOR TO SPECIFY
100 | Online Conductivity meter(0 to 50 micro S/CM) for condensate return line is to be supplied and installed by vendor |  | VENDOR TO SPECIFY
| Following Safeties are to be supplied and installed in Boiler | Instrument Action
101 | Low water level in the boiler | Level controller-1 Alarm & Burner Trip | VENDOR TO CONFIRM
102 | Extra low water level in the boiler | Level controller-2 Alarm & Burner Trip | VENDOR TO CONFIRM
103 | Very extra low water level | Fusible plug Fusible plug blow & burner trip | VENDOR TO CONFIRM
104 | Flame failure | Flame sensor Alarm & Burner Trip | VENDOR TO CONFIRM
105 | Steam pressure high | safety valve Lift | VENDOR TO CONFIRM
106 | Stack temp high | Temperature switch Alarm & Burner Trip | VENDOR TO CONFIRM
107 | Gas pressure low | pressure switch Alarm & Burner Trip | VENDOR TO CONFIRM
108 | Combustion air pressure low | pressure switch Alarm & Burner Trip | VENDOR TO CONFIRM
109 | Gas leak sensor | sensor Boiler Trip & Alarm | VENDOR TO CONFIRM
| Equipment | MAKES to be supplied and installed by vendor
Our selection
110 | Burner ( Dual Type ) (1No.s) | Oilon /Eclips/Oertli | VENDOR TO CONFIRM
111 | Feed Water Pumps (2No.s) | KSB | VENDOR TO CONFIRM
112 | Fuel oil pumps (2No.s) | Entees | VENDOR TO CONFIRM
113 | FD Fan (1No.s) | Your approved vendor | VENDOR TO CONFIRM
114 | All motors (should be energy efficient) | LHP / Siemens / ABB | VENDOR TO CONFIRM
115 | Blow down Valves | Hudco/Levcon | VENDOR TO CONFIRM
116 | Gate/Globe valves on water and steam lines | Hudco/Levcon | VENDOR TO CONFIRM
117 | Non return valves on water line | Hudco/Levcon/Expert | VENDOR TO CONFIRM
118 | Boiler single port spring loaded safety valves(2No.s) | Tyco sanmar/Fainger leser/sempell | VENDOR TO CONFIRM
119 | Temperature Indicator controller | Siemens/Yokogawa | VENDOR TO CONFIRM
120 | Level indicator | Siemens/Yokogawa | VENDOR TO CONFIRM
121 | Level controller | Siemens/Yokogawa | VENDOR TO CONFIRM
122 | Sequence controller | Siemens/Yokogawa | VENDOR TO CONFIRM
123 | Flame sensor(photocell) | Siemens | VENDOR TO CONFIRM
124 | Gas Train components | Dungs / Kromschroder | VENDOR TO CONFIRM
125 | PID controller | Seimens/yokogowa/Honeywell | VENDOR TO CONFIRM
126 | Pressure gauges | Gluck/GIC/Forbes marshall | VENDOR TO CONFIRM
127 | Pressure switches | Vasutech/Switzer | VENDOR TO CONFIRM
128 | RTDs | GIC/Nutech | VENDOR TO CONFIRM
129 | All electrical wiring | Polycab | VENDOR TO CONFIRM
130 | Switch gears | L&T | VENDOR TO CONFIRM
131 | Steam Flow meter(Vortex type) | Yokogawa/Emerson | VENDOR TO CONFIRM
132 | Water Flow meter(Vortex type) | Yokogawa/Emerson | VENDOR TO CONFIRM
133 | Air Flow meter | Standard | VENDOR TO SPECIFY
134 | Access doors | Standard | VENDOR TO SPECIFY
135 | Vendors Scope starts from our existing DM water tanks outlet to New boiler. |  | VENDOR TO CONFIRM
136 | All necessary calculations to be done by the vendor a) for pumping DM water to New boiler storage tank.b) for pumping condensate from 02shop to existing new boiler DM water storage tank |  | VENDOR TO CONFIRM
137 | The layout is to be designed by vendor by giving proper place around the boiler and its auxiliaries covering storage tanks and control room. Finally it should satisfy our requirement and acceptable to us |  | VENDOR TO SPECIFY
138 | All level,pressure,flow,temperature indications should be given in control panel. |  | VENDOR TO CONFIRM
139 | Submission of final IBR documentation folder duly signed by Director of Boilers, Andhra Pradesh will be in the scope of vendor |  | VENDOR TO CONFIRM
140 | Packing, marking, and Transporting all material to BHEL, RC puram, Hyderabad will be in the scope of vendor |  | VENDOR TO CONFIRM
141 | If any exclusions other than below will not be accepted and quotations will be rejected at technical evaluation |  | VENDOR TO CONFIRM
142 | Vendor should satisfy all other general terms and conditions of our tender document. |  | VENDOR TO CONFIRM
143 | All electrical,Instrumentation,mechanical,Civil works along with supply of material will be in the scope of vendor |  | VENDOR TO CONFIRM
144 | Vendor should submit all specs of boiler,equipment details,PID drawings,performance data etc along with quotation. |  | VENDOR TO SUBMIT
145 | Suitable FD fan with required suction and delivery ducts is to be supplied and installed by vender. |  | VENDOR TO CONFIRM
146 | All mountings on the boiler like gauge glass,safety valves,pressure gauges, fusible plug, temperature gauges,,moburey are to be supplied and installed by vendor |  | VENDOR TO CONFIRM
147 | Ducting upto chimney is to be supplied and erected by vendor. |  | VENDOR TO CONFIRM
OPTIONAL ITEMS
148 | Supplying and erecting suitable chimney with IS standard and as per norms of APPCB,hyderabad,Andhrapradesh. |  | VENDOR TO CONFIRM
149 | If we don’t place order for new chimney, the boiler outlet connection to be given to nearby existing chimney and the painting should be done upto chimney. |  | VENDOR TO CONFIRM
150 | DM water line (SS304)from existing boiler house to new boiler(750m distance approx)is to be supplied and erected with necessary valves by the vendor. |  | VENDOR TO CONFIRM
151 | Condensate return water line (SS304)from new boiler to Existing boiler house(750m distance approx)is to be supplied and erected with necessary valves by the vendor. |  | VENDOR TO CONFIRM
DELIVERY,COMMISSIONING & PERFORMANCE
152 | The delivery period for supplying the boiler will be 6 months from the date of placing order |  | VENDOR TO CONFIRM
153 | Erection and commissioning should be completed with in three months from date of supply of Boiler. |  | VENDOR TO CONFIRM
154 | Thermal Efficiency of boiler on NCV required | 92% as per BS 845 part 1-Indirect method | VENDOR TO CONFIRM
155 | Warranty required for all equipments and Motors | 1 year | VENDOR TO CONFIRM
156 | Documents Required | Three Copies of Operation and Maintenance manual for Boiler and accessories | VENDOR TO CONFIRM
157 | Drawings required for all equipments,ductings,PID,MCC cabling,layout,steam pipe line, condensate line, feed water line etc | Three hard copy sets of each and one soft copy of each along with supply of Boiler. One soft copy of all drawings to be submitted along with tender (Quotation) documents. | VENDOR TO CONFIRM
158 | Inspection | will be done by customer at required Intervals | VENDOR TO CONFIRM
159 | Safety valves testing | will be witnessed by customer at works before dispatch | VENDOR TO CONFIRM
160 | Specification of all boiler pressure parts, Boiler auxiallaries,Scope of supply | details to be furnished by vendor | VENDOR TO CONFIRM
161 | Velocity profile, Pressure profile, Temperature profile, Draft profile of flue gas/Air/water/steam | details to be furnished by vendor | VENDOR TO SPECIFY
162 | Manufacturing, Inspection and testing of Equipment should be as per IBR and Preparation of necessary drawings and calculations for getting approval from Director of Boilers, Andhra Pradesh will be in the scope of vendor. |  | VENDOR TO CONFIRM
163 | Training on operation of the boiler is to be given to all our operators for 15 days |  | VENDOR TO CONFIRM
QUALIFYING CRITERIA
164 | Vendor should be having experience in manufacturing of Oil/Gas fired Boilers and should have supplied similar boilers in last five years. |  | VENDOR TO CONFIRM
165 | Vendor should have IBR certificate for manufacturing of Boilers and should be familiar with IBR formalities. |  | VENDOR TO CONFIRM
166 | List of customers and contact numbers for whom similar boilers(since last 2 years in working condition) are supplied, to be given along with quotation |  | VENDOR TO SUBMIT
EXCLUSIONS
The following are only Exclusions and all other necessary material,tools&tackles,structurals (civil/mechanical), electrical cabling with required panels, instrumentation including control panels,IBR liaison and other necessary requirements etc will be in the scope of vendor.
167 | Water treatment plant(DM plant) |  | VENDOR TO CONFIRM
168 | Power supply |  | VENDOR TO CONFIRM
169 | Water supply |  | VENDOR TO CONFIRM
170 | Air supply |  | VENDOR TO CONFIRM
171 | Fuels and chemicals supply |  | VENDOR TO CONFIRM