## VIN-V (SG PKG)
| TITLE : |  |  | SPECIFICATION NO. |  |  | PE-TS-388/389-179-N001 (Rev 0)
| PRICE SCHEDULE |  |  | 1X500MW VINDHYACHAL STAGE-V (SG PKG)
Applicable for Foreign Bidders (Bidder to indicate their Currency)
SL. No. | DESCRIPTIONS OF WORKS OR EQUIPMENT |  |  | UNIT | QTY. | UNIT FOB PRICE | TOTAL FOB PRICE
1 | 2 |  |  | 3 | 4 | 5 | 6=4*5
A) | Prices inclusive for Design, manufacture, assembly, inspection and testing, at manufacturer's and / or his sub contractor's works, properly packed and painted for transportation and delivery for following as specified in the Technical specification PE-TS-388/389-179-N001 (Rev 0) complete with all accessories, commissioning spares (if any), counter flanges with nuts, bolts, gaskets and coatings (wherever necessary) on as required basis of PHE. |  |  | Nos. | 2
PHE for SG Aux.
B) | Total Lumpsum price of special tools and tackles (if required) :
Item-wise breakup with item-wise price to be given as per “Schedule for Erection & Maintenance Tools & Tackles” enclosed under Vol. III of Technical Specification. (Break up to be furnished by Bidder separately).
C) | Lumpsum price for Mandatory Spares as specified in DataSheet
| i) Plates |  |  | % | 2% of each type and size
| ii) Gaskets |  |  | % | 10% of total requirement of each type & size.
| iii) Fasteners |  |  | % | 10% of each type and size
Total of C
D) | Total (A+B+C)
E) | Lumpsum Site Performance Testing of all PHE's for all Unit. |  |  |  |  | Unit Price | Total Price | Service Tax (in terms of ...%) on PG test (Currently 12.36%) | Total Price including Service Tax
F) | Grand Total (D+E)
| Recommended Spares (Optional) |  |  | UNIT | QTY. | UNIT FOB PRICE | TOTAL FOB PRICE
G) | Recommended spares item-wise breakup with item-wise price to be given as per “Schedule of Recommended Spares” enclosed under Vol. III of Technical Specification. Recommended spares are only for reference purpose and not be combined for evaluation and ordering purpose. (Break up to be furnished by Bidder separately)
NOTES :
| i) | Unit price quoted by bidder, as above, shall be binding for any quantity variation, which is at the discretion of purchaser.
| ii) | Price of commissioning & erection spares and other accessories not listed above shall be included in the price of equipment & shall be supplied with the equipment.
| iii) | Indicate all taxes, duties etc. stating whether included/ excluded in above prices.
| iv) | Price break up for items not asked are deemed to be included in A).
| v) | Recommended Spares are optional and will not be taken in evaluation, evaluation will be done on Grand Total (F=D+E) only.
Bidder shall furnish this price Schedule in his price offer only.
PARTICULARS OF BIDDER/ AUTHORISED REPRESENTATIVE.
NAME |  |  | DESIGNATION | SIGNATURE |  |  | DATE |  | COMPANY SEAL

## ecwbending (hidden)
TALCHER STPP - 4X 500 MW
PIPE THICKNESS CLACULATIONS - ECW SYSTEM
TRANSVERSE BENDING BETWEEN SUPPORTS FOR PIPE AND FLUID WEIGHT
( ALLOWABLE STRESS : 1518 KG/CM2 FOR IS-2062 , WEIGHT DENSITY : 7850 KG/M3 )
PIPE SIZE | O.D. | THK | SPAN | I.D. | WEIGHT / M | MOMENT AT MIDDLE | MOMENT OF INERTIA | SECTION MODULUS | BENDING STRESS
( NB ) | ( MM ) | ( MM ) | MAX (M) | ( MM ) | ( KG / M ) | ( KG M ) | ( CM4 ) | ( CM3 ) | ( KG/CM2)
| D | t | L | d | W | M | I | Z | sb
200 | 219.1 | 6.4 | 5 | 206.3 | 66.9975 | 209.3672 | 2420.6687 | 220.9647 | 94.7514
250 | 273 | 6.4 | 5 | 260.2 | 95.2531 | 297.6658 | 4765.0833 | 349.0904 | 85.269
300 | 323.9 | 6.4 | 6 | 311.1 | 126.1255 | 567.5649 | 8047.2497 | 496.8972 | 114.2218
350 | 355.6 | 6 | 8 | 343.6 | 144.4548 | 1155.6386 | 10070.5528 | 566.3978 | 204.033
400 | 406.4 | 6 | 8 | 394.4 | 181.4165 | 1451.3324 | 15128.3252 | 744.5042 | 194.9394
450 | 457.2 | 6 | 8 | 445.2 | 222.4319 | 1779.4554 | 21646.8745 | 946.9324 | 187.9179
500 | 508 | 6 | 10.5 | 496 | 267.501 | 3686.4976 | 29811.534 | 1173.6824 | 314.0967
550 | 558.8 | 6 | 10.5 | 546.8 | 316.6237 | 4363.4698 | 39807.637 | 1424.7544 | 306.2612
600 | 610 | 8 | 10.5 | 594 | 395.8865 | 5455.8114 | 68551.3537 | 2247.5854 | 242.741
700 | 711.2 | 6 | 12 | 699.2 | 488.3137 | 8789.6467 | 82637.9403 | 2323.9016 | 378.228
800 | 813 | 10 | 12 | 793 | 691.9287 | 12454.7168 | 203363.9032 | 5002.802 | 248.9548
ACTUAL BENDING STRESSES AS CALCULATED ABOVE ARE MUCH LESS THAN THE ALLOWABLE BENDING STRESSES OF 1518 KG/CM2, HENCE ALL THE SELECTED PIPE THICKNESSES ARE SAFE FROM TRANSVERSE BENDING STRESSES FOR THE ABOVE CONSIDERED MAXIMUM SPANS..

## ecwsample (hidden)
| TITLE: | [7 empty] | DOCUMENT NO. PE-SC-188-165-0101
| ACW / ECW SYSTEM | [7 empty] | REV. NO. 00
| PIPE THICKNESS CALCULATIONS | [7 empty] | DATE. 02/05/2000
| 4 X 500 MW TALCHER STPP | [7 empty] | SHEET OF
A: CALCULATIONS FOR INTERNAL PRESSURE
Ref. AWWA M-11 CL. 4.1
Material |  |  | = | IS-2062 Carbon Steel encased in plane concrete
Tensile Strength ( Re ) |  |  | = | 4100 | kg/cm2
Yield Strength ( Rm ) |  |  | = | 2500 | kg/cm2
Allowable Stress ( S ) |  |  | = | 1518 | kg/cm2 (Allowable stress is lower of Re/2.7 or Rm/1.5)
Design Pressure ( P ) |  |  | = | 4 | kg/cm2 ( g )
|  |  | & | 0.1 | kg/cm2 ( a ) vacuum
| t |  | = | p x d
2 x s
| d |  | = | Outer dia. in mm
| t |  | = | Minimum specified wall thickness
| p |  | = | Pressure
| S |  | = | Allowable stress
| Pipe Nb |  | = | 2100 | mm
| OD |  | = | 2120 | mm
| t |  | = | 4 x 2120
2 x 1518
|  |  | = | 2.7931 | mm
Selected thickness |  |  | = | 14 | mm
Hence selected thickness is O.K.
B: CW SUPPLY TO CONDENSER
CALCULATION FOR EARTH LOAD AND BUOYANCY LOAD
| Pipe O.D. |  | = | 2120 | mm
|  |  | = | 6.9554 | feet
|  |  | = | 83.4646 | inch
| Radius |  | = | 41.7323 | inch
Note: | As per AWWA M11 for fabricated pipe lines buried underground,
deflection & buckling loads are the design check criteria.
B-1 : Deflection Criteria :
· Depth of Cover |  |  |  |  | = | 1.94 | M
[5 empty] | = | 6.3648 | ft.
· Pipe thickness considered |  |  |  |  | = | 14 | mm
· Pipe Material as per IS 2062
· Manufacturing tol. as per IS 2062 |  |  |  |  | = | ± | 10%
· Hence, net min. thickness available |  |  |  |  | = | 14 | - | 1.4
[5 empty] | = | 12.6
The deflection allowed in pipe line |  |  |  |  | = | 5% of pipe diameter (Refer Cl. 6.2 of AWWA M-11)
|  | Deflection Dx |  |  | = | D1 [(KWr3)/ [( EI + 0.061 E’r3)]] (As per Cl. 6.2 of AWWA M -11)
Where:
| Dx |  | = | Horizontal deflection of pipe (inch)
| D1 |  | = | Deflection lag factor (1.0 - 1.5)
| K |  | = | Bedding constant (0.1)
| W |  | = | Load/ unit of pipe length (lb/ linear inch of pipe)
| r |  | = | Radius (inch)
| EI |  | = | pipe wall stiffness (in - lb)
Where:
|  | E | = | Modulus of elasticity
|  |  | = | 30000000 |  | psi for steel
|  | I | = | Transverse moment of inertia per unit length of pipe wall
|  |  | = | t3 /12 Where ‘t’ is min. pipe thickness in inches
|  |  | = | (12.6/ 25.4)3/ 12
|  |  | = | 0.010173 |  | in3
| E’ |  | = | Modulus of soil reaction (lb/ inches2)
|  |  | = | 1000 | psi
(As per table 6.1 on page 59 of AWWA M -11)
| W |  | = | Load/ unit of pipe length
|  |  | = | Load due to soil wt. + load due to truck load
|  |  | = | (WS.HC + WT) BC
|  |  | = | (WS1.HC1 + WS2.HC2 + WT) BC
Where:
|  | WS1 | = | Unit wt. of fill (lbs/ Cu ft)
|  |  | = | 2000 | kg/M3 ( approx. )
|  |  | = | 2000 X 2.205
(3.2808)3
|  |  | = | 124.8818 | lbs/ft3
|  | WS2 | = | Unit wt. of concrete
|  |  | = | 2500 | kg/M3
|  |  | = | 2000 X 2.205
(3.2808)3
|  |  | = | 156.1023 | lbs/ft3
|  | HC1 | = | ht. Of fill above concrete on pipe approx.
|  |  | = | 1.94 | M
|  |  | = | 6.3648 | ft
|  | HC2 | = | ht. Of concrete above pipe
|  |  | = | 0 | M
|  |  | = | 0 | ft
|  | HC | = | HC1 + HC2
|  |  | = | 6.3648 | ft
|  | WT | = | Surcharge load = |  |  | 0 | psf
|  |  | = | 0 | psf as per Table 6.3 on page C-22 of AWWA M-11.
|  | BC | = | Dia of pipe
|  |  | = | 2.12 | M
|  |  | = | 6.9554 | ft
|  |  | = | 83.4646 | in
| \ W |  | = | [(125 x 5.05 + 156 x 1.64) + 2.84] x 6.96
|  |  | = | 5528.4958 |  | lbs/ ft
|  |  | = | 460.708 | lbs/ inch
| \Dx |  | = | 1.5 [ (0.1x516x 41.73 )/{(30x 106x 0.0102)+(0.061x 600x41.73)}]
|  |  | = | 1.0599 |  | in
| Dx/ D |  | = | (1.89)/(83.5 )
|  |  | = | 0.012699
|  |  | = | 1.2699 | % which is less than 5%, hence thickness selected
as 14 mm meets the deflection criteria.
B-2 : Buckling Criteria :
Allowable buckling pressure,
| qa |  | = | 1/FS (32.RW.B’.E’. EI/D3)1/2
(Refer Cl. 6.3 of AWWA - M11)
| FS |  | = | design factor
|  |  | = | 2.5 | for h/D ³ 2
|  |  | = | 3 | for h/D < 2
Where:
|  | h | = | ht. of ground surface above top of pipe (inches)
|  | D | = | dia of pipe (inches)
|  | FS | = | 6.69 / 6.96
|  |  | = | 0.91509
|  | Hence Fs | = | 3
| RW |  | = | Water bouyancy factor
|  |  | = | 1 - 0.33 (hW/h)
Where
|  | hW | = | height of water surface above top of pipe (inch)
Since in our case,
|  | hW | = | 0
| \RW |  | = | 1-0.33(hW/h)
|  |  | = | 1
| B’ |  | = | Emperical coefficient of elastic support (dimensionless)
|  |  | = | 1/ [1 + 4e ( - 0.065 H)]
Where
|  | H | = | height of fill above pipe (ft.)
| B' |  | = | 1/ [1 + 4e ( - 0.065 x 6.69)]
|  |  | = | 0.27437
| E’ |  | = | 1000 | psi
| E |  | = | 30000000 |  | psi
| qa |  | = | (1/3) [(32 x 1 x 0.28 x 600 x 30 x 106 x 0.0102)/ (83.5)3]1/2
|  |  | = | 22.6277 | psi
| Actual load |  | = | W/D
|  |  | = | 497 / 83.46
|  |  | = | 5.5198
Since allowable buckling press (qa) is higher than the actual load, hence
14mm thickness is safe in buckling.
B-3 : CHECK FOR BUCKLING UNDER COMBINED LOAD
Clause 6.3 AWWA M-11
Water load + Soil load + Vac. load £ Allowable Buckling Pressure
rw x hw x 12 + (Rw x W)/D + Pv £ qa
Where:
| rw |  | = | Specific weight of water
|  |  | = | 0.0361 |  | lb / inch3
| Pv |  | = | 0.1 | Kg/cm2 (Vacuum)
|  |  | = | 0.9 x 14.22 |  | psi
|  |  | = | 12.798 | psi
L.H.S.
|  |  | = | 0.0361 x 0.0 x 12 + (1 x 497 )/83.5 + 12.8
|  |  | = | 18.3178 | psi
R.H.S
|  |  | = | 22.6277 | psi
| \ | L.H.S. | < | R.H.S
Since allowable buckling press (qa) is higher than the combined load, hence
14mm thickness is safe.
C : CALCULATION FOR VACUUM CONDITION:
As per AWWA M-11
|  | Pc | = | 2Ex(t/D)3
(1-n2)
Where:
| Pc |  | = | Collapsing pressure (psi)
|  |  | = | 0.1 | Kg/cm2 (Vacuum)
|  |  | = | 0.9 x 14.22 |  | psi
|  |  | = | 12.798 | psi
| E |  | = | Modulus of elasticity
|  |  | = | 30000000 |  | psi for steel
| n |  | = | poisson's ratio
|  |  | = | 0.3
| t |  | = | Wall thickness (in)
| D |  | = | Pipe diameter (in)
|  |  | = | 2100 | mm
|  |  | = | 82.74 | in
using the above values in the formula, we get
| Pc |  | = | 65934065.9341 |  | x(t/D)3 psi
using a more coservative approach to account for wall thickness variation, out-of-roundness, and other
manufacturing tolerances, we get: Stewart Formula
| Pc |  | = | 50200000 |  | x(t/D)3 psi
or,
|  | t | = | (Pc / 5.02E+07)1/3xD |  |  |  | in
| \ | t | = | (12.8 / 5.02E+07)1/3 x 82.74 |  |  |  |  | in
|  |  | = | 0.52464 |  | in
|  |  | = | 13.3259 | mm
Selected thickness |  |  | = | 14 | mm
Hence selected thickness is O.K.

## VIN-V (STG PKG)
| TITLE : |  |  | SPECIFICATION NO. |  |  | PE-TS-388/389-179-N001 (Rev 0)
| PRICE SCHEDULE |  |  | 1X500MW VINDHYACHAL STAGE-V (STG PKG)
Applicable for Foreign Bidders (Bidder to indicate their Currency)
SL. No. | DESCRIPTIONS OF WORKS OR EQUIPMENT |  |  | UNIT | QTY. | UNIT FOB PRICE | TOTAL FOB PRICE
1 | 2 |  |  | 3 | 4 | 5 | 6=4*5
A) | Prices inclusive for Design, manufacture, assembly, inspection and testing, at manufacturer's and / or his sub contractor's works, properly packed and painted for transportation and delivery for following as specified in the Technical specification PE-TS-388/389-179-N001 (Rev 0) complete with all accessories, commissioning spares (if any), counter flanges with nuts, bolts, gaskets and coatings (wherever necessary) on as required basis of PHE. |  |  | Nos. | 3
PHE for TG Aux.
B) | Total Lumpsum price of special tools and tackles (if required) :
Item-wise breakup with item-wise price to be given as per “Schedule for Erection & Maintenance Tools & Tackles” enclosed under Vol. III of Technical Specification. (Break up to be furnished by Bidder separately).
C) | Lumpsum price for Mandatory Spares as specified in DataSheet
| i) Plates |  |  | % | NIL
| ii) Gaskets |  |  | % | NIL
| iii) Fasteners |  |  | % | NIL
Total of C
D) | Total (A+B+C)
E) | Lumpsum Site Performance Testing of all PHE's for all Unit. |  |  |  |  | Unit Price | Total Price | Service tax (in terms of ...%) on PG test (Currently 12.36%) | Total Price including Service Tax
F) | Grand Total (D+E)
| Recommended Spares (Optional) |  |  | UNIT | QTY. | UNIT FOB PRICE | TOTAL FOB PRICE
G) | Recommended spares item-wise breakup with item-wise price to be given as per “Schedule of Recommended Spares” enclosed under Vol. III of Technical Specification. Recommended spares are only for reference purpose and not be combined for evaluation and ordering purpose. (Break up to be furnished by Bidder separately)
NOTES :
| i) | Unit price quoted by bidder, as above, shall be binding for any quantity variation, which is at the discretion of purchaser.
| ii) | Price of commissioning & erection spares and other accessories not listed above shall be included in the price of equipment & shall be supplied with the equipment.
| iii) | Indicate all taxes, duties etc. stating whether included/ excluded in above prices.
| iv) | Price break up for items not asked are deemed to be included in A).
| v) | Recommended Spares are optional and will not be taken in evaluation, evaluation will be done on Grand Total (F=D+E) only.
Bidder shall furnish this price Schedule in his price offer only
PARTICULARS OF BIDDER/ AUTHORISED REPRESENTATIVE
NAME |  |  | DESIGNATION | SIGNATURE |  |  | DATE |  | COMPANY SEAL