B H A R A T     H E A V Y     E L E C T R I C A L S     L I M I T E D

Heavy Power Equipment Plant, Ramachandrapuram, Hyderabad – 502032

Phone Nos. 23182391,23184408

PROJECTS DEPARTMENT – M&S

TENDER NOTICE NO: PROJ-E&C/ELEC/0T/2006-07/02		    DATE : 07-07-06

Sealed tenders in separate cover, are invited by the Dy. General Manager ( M&S / Projects ), from the reputed contractors, experienced in Electrical / Mechanical works with Government of India, Government of Andhra Pradesh, Railway, Military Engineering Services, Public Sector Undertakings for the following works so as to reach the office of Dy. General Manager  (M&S / Projects ), Factory civil  shed., Bharat Heavy Electricals Limited, Ramachandrapuram, Hyderabad-502032 up to 13.00 Hrs on the dates specified and the tenders will be opened on the same day by 13.30 Hours in the office of the Dy. General Manager ( M&S / Projects ).

The tenders will be issued on all working days between 9.00 Hours to 14.00 Hours at the office of Dy. General Manager ( M&S/Projects ).

| Sl.No. | Name of the Work | Aprrox. Estimate Amount ( Rs. In Lakhs ) | Earnest Money Deposit in Rs. | Period of contract | Cost of Tender Document in Rs. | Sale of Tenders |  | Last date for receipt & opening of tenders. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | From | To |  |
| 1 | Erection of UTM machine at 29 Building | 0.15 | - Nil - | 2 Months | 250/- | 14-07-06 | 21-07-06 | 28-07-06 |
| 2 | Removal of Floor plates, shifting & erection of Floor plates & N.C.Rotary table at 51 shop. | 1.27 | 10000/- | 6 Months | 250/- | 14-07-06 | 21-07-06 | 28-07-06 |
| 3 | Mechanical service lines for Fr9FA Test facilities. | 4.98 | 10000/- | 6 Months | 250/- | 14-07-06 | 07-08-06 | 18-08-06 |
| 4 | Shifting, erection and leveling of clamping bars for Fr9FA Test facilities | 0.79 | - Nil - | 6 Months | 250/- | 14-07-06 | 07-08-06 | 18-08-06 |
| 5 | E&C of HT & LT equipments ( 132 KV ) for Fr9FA Test facilities. | 41.39 | 100000/- | 12 Months | 500/- | 14-07-06 | 07-08-06 | 18-08-06 |
| 6 | Establishment of New Steam Turbine Test facilities at 01 shop. | 5.33 | 25000/- | 8 Months | 500/- | 14-07-06 | 07-08-06 | 18-08-06 |

The tender must posses P.F. and ESI code No. for all works and VAT Reg. for works exceeding more than Rs. 5.00 Lakhs and above. Documentary proof of minimum turn over, experience, labour  license, PAN No. , APGST Reg. shall be submitted as demanded in the techno-commercial Bid.For item No. 5 above, tenderers having valid license of “ Exceeding 33 KV all voltages” only need to quote. For full details and tender documents, please visit our web site http://www.bhel.com on the above mentioned dates.

( DY.GENERAL MANAGER/PROJECTS

PRE-QUALIFICATION

- The following conditions have to be satisfied by the tenderer, with documentary proof to be enclosed with tender bid(Technical).

  - Average annual financial turnover during the last 3 years, ending 31st March of the previous financial year, should be at least 30% of the estimated cost.

  - Particulars of experience / credentials for the works executed of similar nature during last 7 years.( Completion certificate of the works  to be enclosed ) ending last day of month previous to the one in which applications are invited should be either of the following:

- Three similar completed works costing not less than the amount equal to 40% of the estimated cost  OR

- Two similar completed works costing not less than the amount equal to 50% of the estimated cost      OR

- One similar completed work costing not less than the amount equal to 80% of the estimated cost.

  - (a)	ESI Code

    - P.F.Code No.

  - Labour License ( Central / State Government ) before commencement of work.

  - APGST ( Incase not available, proof of having applied with acknowledgement from concerned authority) ( It is required to furnish VAT registration certificate issued by Commissioner, Commercial Taxes, AP Govt., in respect of all works costing more than Rs. 5.00 Lakhs each.).

  - PAN No. ( Incase not available, proof of having applied with acknowledgement from concerned authority).

  - EMD / Cost of document (if down loaded from WEB) RECEIPT/DD.

- Tender documents can also be had through BHEL Web site ( http:/www.bhel.com), cost of document shall be paid in the form of Demand Draft or Bankers cheque or Pay Order and separately enclosed to the tender bid.

- The requisition for tender documents shall be given in person to Dy.General Manager ( M&S-Projects) BHEL, Ramachandrapuram, Hyderabad-502032 along with Demand Draft / Bankers cheque drawn in favour of “BHARAT HEAVY ELECTRICALS LIMITED, HYDERABAD” or payment of cash in BHEL Cash Office ( No other mode of payment will be accepted).Tender documents shall be collected in person by the contractor or his representative. In case of tender application & tender documents downloaded from WEB SITE, the tenderer shall pay cost of tender documents and EMD ( if applicable ) for item of work he is tendering separately by means of two separate DDs ( in favour of BHEL, R.C.Puram, Hyderabad) one towards cost of tender documents and second towards EMD ( if applicable). Both DDs shall be enclosed along with tender documents / Technical Bid ( as the case may be).

- Penalty: 0.5% of the gross value of the work will be levied for every weeks delay by the agency, subject to a maximum of 10% value of the work.

- Quotation should be valid for a period of 90 days.

- Period of completion of work is 8 months.

- Tenderers not fulfilling the above conditions, the offer is liable for rejection.

DY.GENERAL MANAGER/ PROJECTS

TENDER BOX IS AVAILABLE AT CISF CONTROL ROOM AT “F” GATE FOR DROPPING FILLED TENDERS UPTO DUE DATE (13.00 HRS).

B H A R A T  H E A V Y  E L E C T R I C A L S  L I M I T E D

RAMACHANDRAPURAM : : HYDERABAD – 502032

CIVIL FACTORY DEPARTMENT

TELEGRAM:  BHARATELEC   TELEPHONE NO. 23184389 & 23182391

FAX NO. 040 – 23020154

TENDER NOTICE NO. PROJ-E&C/ELEC/2006-07/02           DATED: 07-07-2006

(Item No6)

1.         Name of work				:    Establishment of New Steam Turbine Test

Facilities.

- Earnest Money Deposit		:    Rs.25,000/-

- Time of Completion			:    8 Months

- Maintenance period			:    6  Months

- Last date of receipt of tenders		:    18-08-2006   upto 13.00 hrs.

- Date and time of opening of tenders	:    18-08-2006   13.30   hrs.

- Cost of tender documents		:   Rs. 500.00

Including S.T.

Name & Address:

---------------------------------------------------------------

---------------------------------------------------------------

---------------------------------------------------------------

----------------------------------------------------------

EMD PAID / NOT PAID

TENDERING PROCESS

- Tender box will be kept in CISF CONTROL ROOM ADJACENT

TO   DUTY   OFFICER   SEAT.    AT    F   GATE UPTO DUE DATE.

- Tender documents are issued in two bid system.

1.    Technical bid

2.     Price bid

C.    Tender opening

On the day of tender opening i.e., 18-08-2006     at 13.30

hrs.) only technical bids will be opened and evaluated.

After scrutiny and acceptance of the technical bids, price bids

of accepted  parties only will be opened and date of openingof

price bids will be intimated separately.

- The technical bid consists of technical schedule & General    Conditions requiring  documentary proof. In case the agency has  not satisfied all the conditions along with documentary

proof,  the tender will be rejected.

- Technical and price bids  must be in separate covers and

superscribed as "Technical bid"  and "Price Bid"

separately with item Nos.  clearly written on the covers.

Tenders received  mixed  (with price and technical bids)

will be rejected.      Every page of the price bid

document shall be signed by   the tenderer at the bottom

of the page.

- In case of tender application and tender documents

downloaded from web site, the tenderer shall pay cost of

tender documents and EMD(if applicable) for item of work he

is tendering separately  by means of two separate DDs (in

favour of  BHEL,R.C.PURAM,HYD) one towards cost of tender documents  and second towards EMD(if applicable). Both DD's shall be enclosed  along with the Technical  bid.DD’s may be drawn for cost of tender documents upto last date of receipt of tenders.

…2/-

#### :: 2 ::

#### TECHNICAL BID

Name of the contractor             :

1.   Name of work                          :     Establishment of New Steam Turbine Test

Facilities at 01 Shop.

2.    Tender Notice no &                 :   PROJ-E&C/ELEC/2006-07/02 DATED:

Date,  Item No.                            7-7-2006     (Item No.6)

3.    Details of DD/Cash Receipt     :

a) D.D or Cash receipt No. for EMD :    Rs. 25,000/-

b)DD/Cash recpt. for cost of tender documents   :

when downloaded. (to be  enclosed along with

this bid).

4.  Particulars of experience/credentials  as detailed in notice.

5)   ESI NO.  (Copy to be enclosed)   :

6)  PF CODE  NO. (Copy to be enclosed)

7)   PAN NO (in case not available,  proof of having applied

with acknowledgement from concerned authorities).

- APGST NO. (in case not available,  proof of having applied

with acknowledgement from concerned authorities).

- LABOUR LICENCE (In case not available, proof of having applied

With acknowledgement from concerned authorities).

NOTE:

1.  Without  PAN and APGST No. contractors bills cannot be   processed and

payments will be held up.

- Technical bids will be scrutinised on the same day.  Incase the   agency has not satisfied all the above conditions with documentary     proof the bid will be rejected and their price bid will not be opened.

- Incase of a firm,   shall be in the name of the firm.   However in case of sole proprietor or individuals these can be  on the name of the sole proprietor or individual.

- Though some of above documents are available with BHEL for those agencies who are presently working with BHEL, they also should submit one copy of the same. Otherwise the  offer will be rejected.

- All the columns shall be filled with proper information.

Signature of Contractor(s).

BHARAT  HEAVY  ELECTRICALS  LIMITED

RAMACHNADRAPURAM : : HYDERABAD – 32.

# TENDER  DOCUMENTS

I N D E X

- Directions to Parties for Tendering

- Tender for the work

- Tenderer’s and Contractor’s Certificate

- General terms and conditions

5.	Special conditions (Safety)   & Tidiness at  Site

- Schedule – A  :	Schedule of rates and approximate quantities.

(PRICE BID)

### CONTRACTOR(S)					ISSUING OFFICER

DIRECTIONS TO PARTIES FOR TENDERING

1.	 Subsidiary items such as water for work, clearing and marking out site, hire of tools

and plants should be separately entered.  If such items are not so entered, it will be

assumed that the rates quoted, in the schedule include provision for them also.

- Each tenderer must also send a certificate of Current Income Tax Clearance from the appropriate Income Tax Authority in the form prescribed therefor.  In the case of proprietary firm, it will be necessary to produce the certificate aforementioned for the proprietor or proprietors and for each of the partners as the case may be.

- Every tenderer is expected, before quoting his rates to inspect the site of the proposed work. He should also inspect the quarries, and satisfy himself about the quality and availability of materials.  The best class of materials shall be used on the work.  In every case, the materials as comply with the relevant standards specifications

- Time shall be considered as the essence of the contract.  The rate of progress as mutually agreed to is required to be maintained.  Date of commencement of this programme will be the date on which the site (or premises) is handed to the contractor.

- The tenderer should quote specific rates for each item in the schedule and the rates should be in rupees and paise.  The units and rates should be written both in words and figures.  The schedule accompanying the tender shall be written legibly and free from  erasures, over writings or corrections of figures.  Corrections where unavoidable should be made by crossing out, initialing, dating and rewriting.  No alterations which is made by the tenderer in the agreement form, the conditions of agreement, the drawings or specifications accompanying the same will be recognise4dand if any such alterations are made, the tender will be void.

SIGNATURE OF CONTRACTORS(S)     		        ACCEPTING AUTHORITY

TENDER FOR THE  WORK

I/We_____________________________________________do hereby tender to execute works of the under mentioned description and in accordance with the conditions noted below in consideration of payment being made for the quantity of work executed at the respective rates specified in the following schedule.

I / We hereby distinctly and expressly declare and acknowledge that before the submission of my / our tender I / We carefully followed the instructions in the tender notice and have read the  Andhra Pradesh Standard specification and the clauses of the preliminary specifications an that I /We have made such examination of the contract documents and of the specifications etc., and of the location where the said work is to be done and such investigation of the work required to be done and in regard to the material required to be furnished as to enable me/us thoroughly to understand the intention of same and the requirements, covenants, agreements, stipulations  and restrictions contained in the contract and in the said specifications and distinctly agree that I /We will not hereafter make any claim or demand upon the Bharat Heavy Electricals Limited based  upon or arising out of the said requirements, covenants, agreements, stipulations, restrictions and conditions I /We, _______________________ enclose a income tax verifications certificate.  I /We ________________________________________ have already produced  income  tax verification certificate during the current calendar year in respect of (here particulars of the previous occasion on which the certificate was produced should be given ______________________________________________________________________________________________________________________________________________________.

Signature of Contractor (S)

Address

TENDERER’S AND CONTRACTOR’S CERTIFICATE

- I hereby declare that I have perused in detail and examined closely the Andra Pradesh Standard Specifications and it’s addenda volume and also BHEL General Conditions of contract. I agree to be bound by and comply with all specifications contained in Andhra Pradesh  Standard Specification and General Conditions of contract, for the various items of works specified in the      Schedule “A” and the work as a whole.

- I hereby declare that I shall pay the statutory minimum wages to my workers as applicable from time to time.

I shall  also adhere to all the statutory obligations under Contract Labour (Regulation and Abolition) Act 1971 and Rules framed thereunder with subsequent revisions if any .

Date _________________                            SIGNATURE OF CONTRACTOR(S)

GENERAL  CONDITIONS  APPLICABLE  TO  ELECTRICAL  & MECHANICAL WORKS CONTRACTS.

Following are the “ General conditions applicable to Electrical & Mechanical  Works Contracts”.  Contractors shall be basically bound by the clauses mentioned herein.  However,  contractors shall also be bound by such of the clauses mentioned in General conditions of contract for supply,  supervision, erection of equipment and electrical installations annexed with this, which are not incorporated in the first said general conditions and which are applicable to Work Contracts.

- Before submitting the tender, the tenderer shall be deemed to have carefully examined the tender documents (specifications, general conditions) and have satisfied himself by actual inspection of the site of the work and also conditions liable to be encountered during the execution of works are taken into account and the rates quoted are adequate and also inclusive.

- Should a tenderer find discrepancies in or omissions from the drawings or any of the tender documents or should he be in doubt as to their meaning he should at once obtain the clarification from the accepting authority.  It shall be understood that every endeavor has been made to avoid any error which can materially effect the basis of the tender and the successful tenderer shall take upon himself and provide for the risk of any error which may subsequently be noticed and shall make no subsequent claim or account thereof.

- Words imparting the singular number shall also include the plural and vice-versa where the context requires.

- Before submitting the tender, tenderers should sign on each and every page of the tender documents including drawings.

- POWER TO VARY OR OIMIT WORK: The tenderer shall quote  his rates with reference to each item of the scheduled in figures as well as in words and must quote for all items.  In case of any difference in rates quoted in figures and in words,  the lower of the rates will be considered as the tendered rate.  Rates quoted shall include excise duty, local and or central sales tax and any other taxes/levies chargeable under State and or Central Governments rules.  While quoting the rates, tenderers are advised  to take care of market fluctuation during the period of validity of contract.  No claim shall be entertained on account of any extra expenditure.  The quantities indicated in the Schedule are approximate and the Contractor must be prepared to execute the job or decrease of quantities, Company shall pay/deduct from Contract at the rates mentioned in the scheduled enclosed with Letter of Intent. Minimum quantities are not guaranteed against any item of the schedule.  Where an item or items are not appearing in the tender schedule and where the rates are not given in the schedule, they shall be settled by the BHEL and Contractor jointly.

- Any erasures and or alterations in the tender documents must be attested by the tenderer, otherwise the tender is liable for rejection.

- If the tenderer furnished wrong information for the acceptance of the tender, the BHEL reserves the right to reject such an offer and or cancel the contract at any stage of work.

..2

CONTRACTOR				ACCEPTING AUTHORITY

::2::

- The tenderers shall keep the offer for a period of 90 days from the date of  opening the tender within which period, if the contractor revokes his offer or increase the prices, the offer is liable for rejection by forfeiting the Earnest Money Deposit.

- If the tenderer expires after the submission of his tender or after acceptance of this, the BHEL shall deem such tender as cancelled.  If a partner of the firm expires, after the submission of their tender or after the acceptance of their tender, the BHEL shall deem such tenders as cancelled unless the firm retains its character.

- Tenderers are advised to note incase of negotiations, such negotiations shall not amount to cancellation of original offer.  The original offer however shall be binding till the expiry of the validity period.

11.	 TERMS OF PAYMENTS

Subject to any recoveries or deduction, which the Company may be entitled or authorised to make under this contract or otherwise the Company will pay: -

- 75% of the value of non- perishable materials as Secured Advance after

Storing the required materials on site and certified by the Engineer incharge against INDEMINITY BOND in the prescribed proforma.

- 100% of the value of the portion of work completed in all respects of any of the items of the Scheduled on progressive execution.

- Amount of the extent of 10%of the agreed rate against each items of the schedule will be deducted towards testing and commissioning wherever necessary and the same will be paid after actual handing  over the Installation duly tested and commissioned.

12.	The Earnest Money Deposited by the unsuccessful tenderer will be refunded within a reasonable time.  The Earnest Money deposited by the successful tenderer will be adjusted towards part of Security Deposit.  In the event of successful tenderers not responding to execute the agreement within the stipulated time as mentioned in the Letter of Intent,  the Company may decide such tenderer has abandoned the Contract and there upon his tender and acceptance shall be null and void and the Company shall be entitled to forfeit the EMD/Security Deposit.

- The successful tenderer has to execute an agreement in the prescribed proforma on a non-judicial stamp paper worth Rs.10/-, Rs.50/-, Rs.100/- (applicable as per value of contract)  purchased at Hyderabad with BHEL and the expenses of completing the agreement shall be borne by the Contractor.  Copy of  the Agreement will be given to the Contractor after its approval by the Accepting Department  of BHEL.

14.	The successful  tenderer at the time of executing the agreement is required to produce the following:

i)   Income tax clearance certificate or a sworn affidavit duly counter     signed by the Income Tax Authority.

ii)   Affidavit or Partnership Deed or Memorandum and Articles of  Association.

iii)   Power of attorney.

..3

CONTRACTOR			ACCEPTING AUTHORITY

::3::

15.	SECURITY DEPOSIT

15.1   Security Deposite shall be collected from the successful tenderer.  The rate of Security Deposit will be as below:

Upto Rs.10 Lakhs		-  10%

Above Rs.10 Lakhs upto 	-  1 Lakh + 7.5% of the amount  excee-

Rs.50 Lakhs	              ding Rs.10 Lakhs.

Above Rs.50 Lakhs	           -  Rs.4 LLakhs + 5% of the amount

Exceeding Rs.50 Lakhs.

Before commencement of work, the contractor has to deposit the

Security Deposit.

15.2	Security Deposit may be furnished in any one of the following forms:

i)    Cash (as permissible under the income Tax Act)

ii)   Pay Order, Demand Draft in favour of BHEL.

- Local cheques of Scheduled banks, subject to realization.

- Securities available from Post Offices such as Natiional Savings Certificates, Kisan Vikas Patras etc.(Certificates should be held in the name of Contractor furnishing the Security and duly pledged in favour of BHEL and discharged on the back).

- Bank Guarantee from Scheduled Banks/Public Financial Institutions as defined in the Companies Act subject to a maximum of 50% of the total security deposit value.  The balance 50% has to be remitted either by cash or in the other form of Security.  The Bank Guarantee format should have the approval of BHEL.

- Fixed Deposit Receipt issued by Scheduled Banks / Public Financial Institutions as defined in the Companies Act.  The FDR should be in the name of the Contractor, A/C BHEL, duly discharged on the back.

- Security Deposit will also be recovered at the rate of 10% from the running bills.  However, in such cases at least 50% of the Security Deposit will be collected before start of the work and the balance 50% will be recovered from the running bills.

- EMD of the successful tenderer will be converted and adjusted against the Security Deposit.

- The Security deposit shall not carry any interest.

NOTE:  Acceptance of Security Deposit against Sl.No.(iv) and (vi) will be subject to hypothecation or endorsement on the documents in favour of BHEL.  However, BHEL will not be liable or responsible in any manner for the collection of interest or renewal of the documents or in any other matter connected therewith.

15.3.   Security deposit will be not be refunded to the Contractor except in accor-	dance  with the terms of the contract.

- The work so far as it is to be carried out in the Company’s premises shall be   carried out at such time as the Company may approve and so as not to interfere with the conduct of Company’s business, but the Company shall given the contractor all reasonable facilities for carrying out the work.

….4

CONTRACTOR				ACCEPTING AUTHORITY

::4::

- PROGRAMME OF WORKING:

The Contractor at the time of executing the agreement shall submit the programme of working i.e. procurement of materials ( date of placing the order, expected date of arrival of material) and executing with the date of commissioning and probable date of completion .

18.	If the Contractor fails to commence the work as stipulated in the agreement and or if the progress of work is not satisfactory the agreement is liable for cancellation after informing the Contractor by forfeiting the Security Deposit.  The job will be executed by another agency and the excess cost involved in getting  the job executed either by another Contractor or departmentally is liable for recovery from payment that are due to the Contractor in connection with the same work or any other work or by recourse to legal action .

19.	TIME OF COMPLEION & EXTENSION OF TIME:

The work shall be completed in all respects and handed over, with in time stipulated in the agreement.  Extension of time shall be allowed without any penalty in case of the progress of work gets delayed by any act of BHEL or by any other contractor employees by BHEL or any reasons beyond our control which BHEL feels justified no extension of time shall be allowed unless as an applications made in writing by the Contractor in the prescribed proforma.

- PENALTY

If  the Contractor fails to execute the job within the specified period as per the agreement or any extension of time thereof, he shall be liable for unconditional penalty at ½% of the Contract value per week of delay or part thereof subject to maximum to 10% of the total value of  the finished contract amount and without prejudice to any other relief or compensation under any other conditions of contract.

21.	The Contractor will ensure adherence to all the Statutory requirements under the State Rules in respect of Service  conditions for the employment of Contract Labour including those contained in Labour Commissioner’s Notification No.D1/8385/79.  Any violation in respect of observance of Statutory requirements under the Contract Labour  (Regulation Abolition) Act, 1970 will make the Agreement liable for immediate termination.

22.	CO-OPERATION WITH OTHER CONTRACTORS:

The Contractor shall cooperate with the Company’s other Contractors in order to execute the job in an economical and efficient way of avoiding unnecessary duplication or reducing of the work.

23.	POSSESSION PRIOR TO COMPLETIONS :

The Company shall have the right to take possession of any partially or fully completed part of the work. Such possession shall not be deemed to be acceptance of any work not in accordance with the Contract.

……5

CONTRACTOR				ACCEPTING AUTHORITY

::5::

24.	Work shall be executed in accordance with the requirements of Indian Electricity Act, 1937 Rules with all statutory modifications thereof to date and as per relevant Indian Standard specifications amended upto date.

25.	The Contractor is not permitted to sub-contract the work without the prior  permission of competent authority of BHEL.  Even in such cases where the sub-contract is permitted, the whole responsibility  of executing the work as per agreement lies with the contractor who entered into the agreement.

26.	The work shall be maintained for a period 6/12 month from the date of satisfactory completion, testing and handing over the  complete installation by the contractor and he shall make good any defects, faults and imperfection (which may appear) at his own cost.

27	In case where the work is to be subjected for inspection of the electrical inspector, the contractor should be present at the time of inspection and or any defects pointed out by the electrical inspector should be rectified by the contractor at free of cost.

28	Final layout as well as foundation drawings should be submitted in advance for execution of Civil works.

29	 SAFETY MEASURES:

Contractors are advised to issue all necessary safety equipments to workers and see that they are properly used by them.  Contractors are advised to follow all necessary safety precaution such as providing sign boards and touching the installation with prior permission of the competent authority.

All sorts of  safety measures to be taken shall be deemed to form an integral part of agreement.

30 	INSPECTION & TESTING AT CONTRACTOR’S PREMISES:

The Engineer incharge of the work or his authorised representative shall have all reasonable times access to the Contractor’s premises or works.  In case of work being executed at other premises, the Contractor shall obtain the permission for inspection of the same by the Engineer incharge of work as if the work is being executed at the Contractor’s own premises.

31	 In respect of materials supplied by the Contractor for which any guarantee has been given by the manufacturer for a period more than the maintenance,  period for which the contractor is responsible,  the Company shall be entitled to such guarantee and the same shall have to be transferred by the Contractor to the Company.

- All minor jobs whether specified separately or not in the specifications but required for efficient working shall be executed by the contractor with prices quoted.

..6

CONTRACTOR				ACCEPTING AUTHORITY

::6::

33.	A R B I T R A T I O N  :

If at any time any question, dispute or difference whatsoever shall arise between the Company and the Contractor upon, or in connection with the Contract, either party may forthwith give to the other notice in writing of the existence of such question, dispute or difference and the same shall be referred do the adjudication of two arbitrators, one to be nominated by the Company and the other to be nominated by the Contractor or in the case of the said arbitrators not agreeing then to the adjudication of the Umpire to be appointed by the arbitrators, in writing before proceeding with the reference and the award of arbitrators or in the event of their not agreeing of the Umpire appointed by them, shall be final and binding on the parties, and the provisions of the Indian Arbitration  Act, 1940, and of the Rules thereunder and any Statutory modification  thereof shall be deemed to apply to and be incorporated in this Contract.

Upon every or any such reference, the costs of and incidental to the reference and award respectively shall be in the discretion  of the arbitrators or of the Umpire, as the case may be   who may determine the amount thereof, or direct the same to be taxed as between solicitor and Client, or as between Party and Party and shall direct by whom and to whom and in what manner the same shall be borne and paid.

Work under the Contract shall be continued  by the Contractor during the arbitration proceeding unless otherwise directed in writing by the Company or unless the matter is such that the Works cannot possible to be continued until the decision of the arbitrators of the Umpire as the case may be is obtained and save has those which are otherwise expressly provided in the Contract no payment due or payable by the Company shall be withheld on account of such arbitration proceeding unless it is the subject matters thereof.

- The daily wages payable to the Contract Labour will conform to the rates as prescribed by the State Labour  Department from time to time for unskilled, semi-skilled and skilled workers.

- That the said contractor has agreed to perform the said work according to the latest Indian Electricity Act & Rules, the code of practice etc.,for electrical wiring,the fitting in buildings Indian Standard IS: 732/1963 as amended upto date and such other conditions as as contained in all the specification contained in the contract documents.

- That all  charges on account of octroi, terminal or Sales tax both State & Central and any other rate or charges imposed by any Government or Local Authority on the materials obtained for or in respect of the execution of the said work shall be borne by the Contractor.

..7/-

CONTRACTOR				ACCEPTING AUTHORITY

:7:

- The contractor shall fully comply with the following enactments:

- Contractor Labour (R&A) Act,  1971.

- Wage Rates not less than that notified by State Labour department from time to time.

- Payment of Wages Act.

- ESI Act,  1948.

- EPF Act,  1952.

- Workmen’s Compensation Act, 1923.

- The company’s instructions as issued from time to time in regard to working hours, wages, leave, holidays etc.

- The Contractor shall obtain license from the Assistant Labour Commissioner (Central), or appropriate Government if he engages 20 (Twenty) or more workmen only.

- The contractor shall produce the following Registers and forms before commencement of work, verification by the Executing Officer of the company.

a.	Form XIII	-	Register of workmen employed by contractor (Rule 75).

- b.	Form XIV 	-	Employment card issued by contractor (Rule 76).

- c.	Form XVI	-	Muster Roll (Rule 78 (1) (a) (i)).

- d.	Form XVII	-	Register of Wages (Rule 78 (1) (a) (i)).

- e.	Form XVII	-	Register of wages - cum Muster Roll (in case

- of weekly payment).

- f.	Form XIX	-	Wage slip (Rule 78 (b)).

- g.	Form XX	-	Register of deduction for damages or loss

- (Rule 78 (1) (a) (ii)).

- h.	Form XXI	-	Register for fines  (Rule 78 (1) (a) (ii)).

- i.	Form XXII	-	Register of advances  (Rule 78 (1) (a) (ii)).

- j.	Form XXIII	-	Register of overtime (Rule 78 (1) (a) (iii)).

- k.	Form XXIV	-	Register to be sent by the contractor to licensing

- officer (Rule 82 ) (1).

The contractor shall maintain the above neatly, completely an legibly for inspection by various statutory authorities and the company officials even at short notice.

40.	The contractor shall observe

- (a) 	Weekly rest day.

- (b)	The company list of holidays.

- Contractor shall obtain complete bio-data of the labour, employment certificate and Antecedent verification in the prescribed form for each labour and supervisor  engaged  by him and shall submit the same to the Personnel Department / IR section through the contract executing officers before commencement of the work.

..8/-

CONTRACTOR			ACCELPTING AUTHORITY

:8:

- The Entry permits are to be issued to the Contract Labour by Assistant Commandant /   CISF (Plant), based on the requisition submitted by Contract Executing Officer and forwarded by Dy. General manager / Personnel.

- Every contractor shall submit a notice regarding commencement and completion, of work in form – VI A&B [Rule 25 (VIII) & 81 (3)] to Personnel Department, IR section through his contract executing officer, for forwarding the same to State Labour Department.

- The contractor shall make himself of his representative available at the work spot everyday during execution of work, for effective supervision.

- The contractor shall attend to all inspections notified / conducted by the Personnel Department, Labour Department, P.F. authorities. Factory Inspectors ESI Inspectors, or any other such authorities under the act.

- Non – compliance of any provisions under the act/ rule/instructions / guidelines shall make the contractor liable for penal action including termination of contract.

- Contractor shall furnish in a separate letter his place of residence and postal address. The delivery at the above named place or posting in a Post box regularly maintained by the post and telegraph Department or sending letters registered for acknowledgement of any notice,  letter or other communication to the contractor. Change in address shall come into force at any time by an instrument executed by the contractor and delivered to the Company official who has signed the contract.

- The contractor must satisfy himself by personal study and examination of the drawings / specifications furnished and understand thoroughly the scope of proposed work in detail and all conditions affecting the work before entering into the contract. There shall not be at any time dispute / complaint of any misunderstanding with regard to scope  of work and interpretation of specifications or any misunderstanding with regard to nature or omission of the work to be done not shall any application for compensation in terms of time and money shall be accepted by company regarding the above.

- Contractor shall in his absence keep competent agent constantly on the works and any directions or explanations given by the “Contract Signing Officer” or his representative to such agent shall be held to have been given  to the contractor himself.

- Contractor on the advise of company official shall immediately remove any person employed by him, who may in the opinion of the company official is incompetent or misc. conducts himself and such persons shall not be again employed on the works without permission of the company official.

51.	The contractor shall erect and maintain at his own cost temporary weather proof sheds at such places approved by the company for keeping  materials under cover.

CONTRACTOR				ACCEPTING AUTHORITY

::9::

GENERAL TECHNICAL CONDITIIONS

UNLESS OTHERWISE SPECIFIED IN THE TENDER SCHEDULE

- Tenderers are advised to mention the make/brand against each item of their offer.  Only standard and reputed makes or brands acceptable.  The choice of make is at the discretions  of BHEL.

- Supply and installation of switch fuse or fuse switches or existing switch boards includes with all necessary “Standard accessories” required for executing  the job in a better way

- Only laying or supply and laying  of cable in existing cable trenches including the removal and putting back the existing RCC trench covers.

- Supply and laying of chord/cable includes standard way of end terminations.

- Supply and installation of fuse distribution boards includes along with switch fuse or fuse switch (Whichever may be the case) and necessary standard cable entry boxes.

- Cable is to be run through suitable conduit at every switchboard above ground level (Power & lighting ) ,  distribution board and independently mounted switch fuses.

- All the switch boards (  power & lighting ) and distribution fuse boards or MCB Board ( Power & lighting ) must be earthed  to the nearest earth flat or earth pit ( conforming to IS ) by means of Two runs of 8 SWG GI. Wire should not be used unless otherwise specified..

- Earth wire is to be run along the cable above the conduit pipe inside the block or building  with suitable clamping and 500 mm below the ground in cases it is to be laid outside.

- Earth wire is to be terminated at both end with  suitable T.C. Copper lugs, and fixed with copper earthing clamps  at every 12”.

- Cable route marking are to be provided for (LT &HT cable ).

- In  case of (open / concealed ) conduit wiring conduit of 16 gauge must be used conforming to IS: 1653.

- Fan points must be terminated in ceiling roses and supply is to be taken by means of 3 core copper flexible cable of not less than I sq. mm (32/02 mm).

- Each point is to be independently controlled by a separate  switch fixed on a steel box and the switch should be located at a convenient point  as desired by the engineer in charge  of the work.

- All the light fittings should be supplied along with necessary  tubes / lamps.

…..9

CONTRACTOR				ACCEPTING AUTHORITY

::10::

- In wiring straight through or twist joints should be avoided.

- In wiring colour code is to be followed i.e. Red, Yellow, Blue, Black and White.

- Wires at the terminating points should be terminated with sufficient looping.

- Any openings to be made in the existing structure for the purpose of carrying out the electrical work should be closed without any extra cost.

- All the works executed and or material supplied must conform to relevant Indian Standards wherever necessary the test certificates of the equipment, cables etc. must be obtained from the original suppliers and handed over to BHEL.

- Number of wires in each size of steel conduit pipe should be as per I.S.Specifiction.

- Number of points in each circuit should not be more than 7 and total load of each circuit should not be more than 700 Watts, whichever is less is to be adhered to.

- 15 Amps. And above capacity sockets should be wired with a separate circuit of load and return wires independently.

NOTE    THE RATES QUOTED IS PRESUMED TO HAVE INCLUDED THE COST OF ALL THE ASSOCIATED/REQUIRED/CONNECTED MATERIALS

- Fore every electrical work, various test results, test certificates, the actual layout and schematic circuit drawing & (Blue pringts + original – 5 copies) in quadruplicate should be handed over to BHEL for submission to the Chief Electrical Inspector’s approval, duly signed and stamped by the Competent Contractor & Engineer.  The preparation of drawings should be in accordance with the requirements as specified in the relevant IS specifications or as required by Chief Electrical Inspector.

- All the circuits, equipments etc. should be numbered, names written, precautions, feeding points etc. as required should be neatly written with DUCO Make paint.  The same should truly reflect in the drawings for site checking.

- Wherever excavation of cable is underground / cable laying works is involved, it should be strictly executed as per IS: 2309 with all minute details.

CONTRACTOR                                          ACCEPTING AUTHORITY

LIST OF SAFETY PRECAUTIONS TO BE OBSRVED BY THE CONTRACTOR

The Contractor shal take all necessary Safety precautions and arrange for appropriate appliance as per direction of BHEL to its authorized officials to prevent loss of human lives, injuries to personnel engaged and damage to property.

The Contractor shall provide to the work force and ensure the use of the following personnel Protective Equipment as found necessary and as directed by the authorized BHEL Officials.

- Safety Helmets conforming to IS: 2925, 1984

- Safety Belts conforming to IS: 3521, 1983

- Safety shoes conforming to IS: 14544, 1998

- Eye & Face protection devices conforming to IS: 1179, 1967

- Hand & body protection devices conforming to IS:2573-1975; IS: 6994-1973 and IS: 8520-1978, IS: 578-1985 and IS: 6694.

The contractor shall not use any hand lamp energized by electric power with supply voltage of more than 24Volts (DC)

All portable electric tools, used by the Contractor shall have safe plugging system to sources of Power and be appropriately earthed.

All tools, tackles, lifting appliances, scaffolds, cradles, safety nets, ladders, equipment etc. sued by the contractor shall be safe design and construction.  The authorized BHEL officials shall have the right to ban the use of any item, if such use is considered to be dangerous by the concerned BHEL officials.

If the Contractor fails to take appropriate safety precautions or to provide necessary safety devices and equipment or to carryout instructions issued by the authorized BHEL officials, BHEL shall have the right to take corrective steps at the risk and cost of the contractor.

The contractor shall take necessary fire safety precautions as per directions of the authorized BHEL official.

In case of a fatal or disabling injury accident to any person due to lapses by the Contractor, BHEL shall have the right to impose appropriate financial penalty on the sub-contractor and recover the same from payments due to the contractor  for suitably compensating the victim or his/her dependents.  Before imposing the penalty, appropriate enquiry shall be held by BHEL.

In case of any damage to property due to lapses by the Contractor , BHEL shall have the right to recover the cost of such damages from the payments due to the contractor after holding an appropriate enquiry.

In case of any delay in the completion of a job due to mishaps attributable to lapses by the Contractor, BHEL shall have the right to recover cost of such delay from the payments due to the Contractor after notifying the contractor suitably.

If the Contractor fails to improve the standards of safety in its operation  to the satisfaction of BHEL after being given reasonable opportunity to do so.  BHEL shall have the right to terminate the contract and get the job completed at the risk and cost of sub-contractor.

If the Contractor succeeds in carrying out the job in time without any fatal or disabling injury accident and without any damage to property, BHEL shall favorably consider to reward the contractor suitably for the performance.

CONTRACTOR                                          ACCEPTING AUTHORITY

COMPLIANCE OF TIDINESS AT THE SITE OF WORK

1.            a)	During erection work, every day contractor has to follow sorting of the things at work place and throw away unwanted things as directed by site engineer  on daily basis.

- Arrange the things in such a way that they are retrieved quickly.

- Work place shall be maintained clean and neat on  daily basis.

2.	After completion of work, the area should be cleaned by duly removing scrap/balance materials and shifted to scrap yard/stores as directed by Site Engineer.

CONTRACTOR                                          ACCEPTING AUTHORITY

Guidelines and statutory payments for submitting tenders for

Elec./Mech./ Civil Works as per existing instructions.

Daily wage rate  is exclusive of Weekly off, Holiday and Leave Wage.

Wage  rates as on date

U S W  : Rs.117.10                 per day  Inclusive of weekly off.

S S W  :  Rs.132.90                     “                         "

S  W    :  Rs.150.65                     “                         "

- Leaves and Holidays

+   11  days  paid  holidays  /  per  year

+   18   paid  leaves / per  year.

- P F and  E S I  contributions  wages

PF @  13.61 %  and  ESI  @  4.75  %  of  basic  wages should be contributed by the contractor on above daily wages.

CONTRACTOR                                                      ISSUING/ACCEPTING AUTHORITY

PRICE BID

BHARAT HEAVY ELECTRICALS LIMITED

RAMACHANDRAPURAM :: HYDERABAD-32

--------------------------------

PROJECTS(E&C)

TENDER SCHEDULE FOR THE WORK OF " ESTABLISHMENT OF NEW STEAM TURBINE TEST FACILITIES AT 01 SHOP.

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

1.  Shifting,Erection, testing & commng. of

BHEL free issued MCC of size: 4.5 x  1.0

x 2.5 Mtrs. (1 panel - 4 cubicles) on the  3   No.

cable  trench  as per  site  requirement.

The  MCC  compartments are to  be  neatly

assembled, pre-wired as necessary as  per

drawing,  tightening of screws, nuts etc.

The  MCC  to be erected on to  the  cable

trench  by  welding BHEL free  issued  MS

materials and positioning and  alignmnet.

The  job  includes double  earthing  with

suitable GI flat of 50 x 6 MM.(Approx.wt:

4.0 Tons). The following tests are to  be

carried out & report to be submitted. All

testing eqpt/kits,instruments &  consuma-

bles are in Contractor's scope:

i) Insulation Resistance test with 500V /

1000 V Megger  ii) Terminal check

iii)operational check     iv)Functional

check   v)Protective check(Tripping)  and

(f) Earth continuity.

2. Shifting,  erection, testing &  commng.of

DCDB  Distribution  board  of  BHEL  free  1   No.

issued of size (3.0 x1.0 x2.5   Mtrs)

on the cable trench as per site  require-

ment. The job includes pre-wiring as  per

drawing, tightening of screws, nuts  etc.

The DCDB to be erected onth cable trench

by  welding BHEL free  issued  MS

channel,  positioning  and  aligning  the

same.  Double earthing of GI flat of size

: 50x6 MM.

…2

CONTRACTOR					ACCEPTING AUTHORITY

::2::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

3. Shifting,  erection, testing &  commng.of

MAXDNA PANEL   of  BHEL  free              1   No.

issued of size (2.5 x1.0 x2.5   Mtrs)

on the cable trench as per site  require-

ment. The job includes pre-wiring as  per

drawing, tightening of screws, nuts  etc.

The  Panel to  be erected  on  the  cable

trench  by  welding BHEL free  issued  MS

channel,  positioning  and  aligning  the

same.  Double earthing of GI flat of size

: 50x6 MM.

4. Shifitng,erection,  testing  &  commng.of

P.L.C.   panel  of 1 No. of BHEL           1   No.

free issue of size: 1.5Lx1.2Bx1.0 H Mtrs.

on  the  cable  trench as  per  the  site

requirement. The job includes  pre-wiring

as   per   the   drawing/as    necessary.

Tightening  of screws/nuts etc.  The  ACP

is  to be erected on the cable trench  by

welding  BHEL  free issued  MS  channels.

The  job  includes double  earthing  with

50x6 MM GI flat

5.  Shifting,Erection, testing & commng. of

BHEL free issued Control Desk of 7        1  No.

Section size:  7x 1.0x 1.5  on the

cable  trench  as per  site  requirement.

The  Control desk compartments are to  be

neatly  assembled, pre-wired as necessary

as  per drawing,  tightening  of  screws,

nuts etc.  The Control desk to be erected

on  to  the  cable  trench  as  per  site

engineer  instructions  by  welding  BHEL

free issued MS materials and  positioning

and  alignmnet.  The job includes  double

earthing with suitable GI flat of 50 x  6

MM.(Approx.wt: 4.0 Tons).

…..3

CONTRACTOR				ACCEPTING AUTHORITY

::3::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

6. Shifting  & Laying of PVC  insulated  and

sheathed Al. armoured cable 660 V  grade,

IS:  1554-Part  I.  The cable has  to  be

laid from power lighting switch boards to

various ICTP switches.  Along the cable 2

runs  of  No.10G  GI  wire  with   copper

earthing clamps and llugs, cable  glands,

PVC  ferrules etc. Above ground level  at

FDB  and at starter the cables are to  be

mechanically protected by drawing through

steel  conduit pipe and  neatly  clamped.

The  cable has to be partly laid  in  the

existing cable trenches/structures as per

site engineer instructions.

a. 3 1/2 C x 300 Sq.mm cable.                100  RM

b. 3 1/2 C x 120 Sq.mm cable                 800  RM

c. 3 1/2 C x 95 Sq.mm cable                  750  RM

d. 3 1/2 C x 35 Sq.mm cable                   50  RM

e. 3 1/2 C x 25 Sq.mm cable                  300  RM

f. 3 1/2 C x 16 Sq.mm cable                  150  RM

7. Supply  & execution of cable  end  joints

for item No.6  above with suitable  cable

sockets/tinned   copper   lugs   suitably

crimped and connected as per site  requi-

rements.   Testing & commissioning.   End

joints suitable to:

a. 3 1/2 C x 300 Sq.mm cable.                 4  Jts

b. 3 1/2 C x 120 Sq.mm cable                 16  Jts

….4

CONTRACTOR				ACCEPTING AUTHORITY

::4::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

c. 3 1/2 C x 95 Sq.mm cable                  12  Jts

d. 3 1/2 C x 35 Sq.mm cable                   4  Jts

e. 3 1/2 C x 25 Sq.mm cable                  10  Jts

f. 3 1/2 C x 16 Sq.mm cable                  10  Jts

8. Laying of BHEL given insulated and shield

Al.armoured  cable 660 V grade IS:  1554-

Part-I  includes cable end termination  /

joints  by  providing  cable  glands   by

making   suitable   holes   with   double

earthing.

a. 4 C x 10 Sq.mm cable                      2200  RM

9. Shifting,laying & fixing of the following

BHEL  free  issued  cable  on steel trays

slotted  angles  or  in  pipes  as may be

required by site  conditions from control

room to field junction boxes,  instrument

location points etc. All the cables  must

be  group  wise  run  by  fixing suitable

clamps/conduit saddles  (to  be  supplied

by  the  contractor  at every 2 ft.), All

the  cables are to be provided with cable

indications  marks/numbers  at  regular 5

Mtrs.Interval  all along  the  length.The

job  includes  supply  &  end connections

with tinned  copper lugs, neatly  crimped

PVC  ferrules  for indication at both the

ends, PVC sleeves, PVC/nylon threads, PVC

tape,cable glands etc. as per site  engi-

neers instructions.

A. CONTROL CABLES: Copper armoured cable

a) 2C x 2.5 Sq.mm                             600  RM

b) 4 C x 2.5 Sq.mm                            600  RM

….5

CONTRACTOR					ACCEPTING AUTHORITY

::5::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

c) 6 C x 2.5 Sq.mm                           1500  RM

d) 8 C x 2.5 Sq.mm                           1000  RM

e) 12 C x 2.5 Sq.mm                           100  RM

f) 16 C x 2.5 Sq.mm                           500  RM

B. SHIELD CABLES : Copper Conductor

a) 2 C x 1.5 Sq.mm                           1000  RM

b) 3 C x 1.5 Sq.mm Sq.mm                      500  RM

c) 4 C x 1.5 Sq.mm                            600  RM

d) 10 Pair x 1.5 Sq.mm                        600  RM

e) 8 Pair x 1.5 Sq.mm                         200  RM

f) 16 pair x 1.5 Sq.mm                        300  RM

10.Double   earthing   of    switches/eqpt./

machine  tools  with BHEL free  issue  GI

flat by suitably clamping/welding arrnage

ments as per site engineer's instructions

a) Size of GI flat 50 x 6 mm                 200  R.M.

b).Supply and laying of 8 SWG GI earth wire  500   RM

for eqpt./switches etc.

….6

CONTRACTOR					ACCEPTING AUTHORITY

::6::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

11.Supply  of  materials &  construction  of

earth pit of following specification and

as per sketch enclosed:

Tinned copper plate of dimension 2' x  2'

x 14" thick, should be fastened with a GI

pipe  of  size  2"  OD  and  length  8'6"   2  No.

flattened  at one end for a length  of  1

ft.  properly rivetted  with  non-ferrous

fastners  at 3" apart and the  other  end

being threaded to facilitate mounting  of

the  funnel fixture.  The pipe should  be

drilled with the holes of 1/4" dia at  4"

apart  at  random tinned copper  flat  of

size  1"x 1/4" thick should  be  rivetted

with copper rivets overlapping the  earth

plate  firmly fastened.  The flat  should

be extended upwords upto the ground level

firmly fastened through a bracket  around

the GI pipe.  The bracket should be  fab-

ricated   out  of  non-ferrous   material

(copper)  and the fastening  bolts,  nuts

and  washers  should  also  of  the  same

materials.    The  entire   earth   plate

assembly  with  GI pipe and  copper  flat

should be positioned at a depth of 9  ft.

(nine feet) beneath the ground level over

surface  prepared with salt and  charcoal

and   further   extended   upwards   with

alternative layers.  The masionary struc-

ture / brick work with internal dimension

of  1'x1'x1' depth with provision  for  a

removal  cover/lid will house  the  water

collector funnel.  PVC pipe of 2" OD will

also  be  partitioned along with  the  GI

pipe extending from the lower surface  of

the brick work and upto the earth plate .

PVC  pipe  should also  be  drilled  with

holes of 1/4" dia at 4" apart at random.

NOTE:    The  masionary   structure/brick

work  construction should be carried  out

only  after  total settling down  of  the

earth  dug out from the pit.  The  cover/

lid should be distinctly marked (painted)

INSTRUMENTATION   EARTHING.   The   earth

resistance  when checked up shall have  a

reading of less 2 OHMS.

…7

CONTRACTOR				ACCEPTING AUTHORITY

::7::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

12.Supply  &  Construction  of  earth   pits

strictly  as per IS: 3043 which  includes   2  No.

brick  works,  cement  plastering   cover

plate, GI pipe, funnel, GI hardware,  end

connections etc. with GI clamps as  reqd.

Testing & commissioning.

13.Fixing of Instrumentation                  50 Nos.

14.Fabrication     of   cable    racks/other

structural fabrication works in the cable

trench   with   BHEL   free   issued   MS   5 Ton

materials.  The racks should be made  for

laying  of  cables  in 2 or  3  tiers  as

desired  by  site  engineer.

15.Dismantling   of  equipment  piping   and   5 Ton

valves

16.Laying  of Impulse lines-16 mm  dia  each   30 RM

length is 10 M.                            (each.length)

17.Supply  & fixing of Terminal Jn.box press   6  No.

and  insert type made out of 16 SWG  CRCA

sheet with 100 Nos. of 2.5 Sq.mm terminal

of  WAGO/ELMAX  make with  powder  coated

paint, gland plate etc.

18.Dismantling,  shifting  to  Scrap   yard/

store of following panel/fans/lights etc.    LUMPSUM

a) Control Desk panel - 1 No.

b) Startor various type - 20 Nos.

c) Junction boxes terminals - 520

d) Battery bank, shifting and re-erection

with battery charger - 1 Unit.

e) FBD's - 8 Nos.

f) Lights, fans - 40 Nos.

19.Disconnection, removing and shifting from

various sizes of power cables:           2000  RM

a) 3 1/2C x 300 Sq.mm  - 100RM

b) 3 1/2C x 120 Sq.mm  - 800RM

c) 3 1/2C x 95 Sq.mm   - 500RM

d) 3 1/2C x 35 Sq.mm   - 100RM

e) 3 1/2C x 25 Sq.mm   - 300RM

f) 3 1/2C x 16 Sq.mm   - 200RM

…8

CONTRACTOR				ACCEPTING AUTHORITY

::8::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

20. Disconnection, removing and shifting

various sizes of Signal, Control

cables..                                 2900  RM

a) 2 C x 2.5 Sq.mm  - 500 RM

b) 4 C x 2.5 Sq.mm  - 600 RM

c) 6 C x 2.5 Sq.mm  - 1000RM

d) 8 C x 2.5 Sq.mm  - 500RM

e) 12 C x 2.5 Sq.mm - 100RM

f) 16 C x 2.5 Sq.mm - 200RM

B.  Various type/size of signal cables       1700  RM

g) 2C x 1.5 Sq.mm   - 500 RM

h) 3C x 1.5 Sq.mm   - 200 RM

i) 4C x 1.5 Sq.mm   - 300 RM

j) 10 Pair x 1.5 Sq.mm - 300 RM

k) 8 Pair x 1.5 Sq.mm  - 200 RM

l) 16 Pair x 1.5 Sq.mm - 200 RM

21.Supply  & Installation of 2x40  W  switch

start Fl.luminaire,with vitreous enamelled  23  No.

reflector, Electronic ballast,rotary bipin

holders,  pre-wired  complete  unit  with

2xTLD 36W/TL 40 W tubes model:TKC  22/236

HF OF PHILIPS make, Bajaj: BJIE 236/240 W

EB. fixing according to site  conditions.

Testing and commissioning.

22.Supply & Installation of ceiling fans  56"  17   No.

(1400 mm) sweep, 220/240 V, complete unit

with regulator, 300 mm down rod,  canopy,

blades etc.Make: USHA/GEC/ORIENT/CROMPTON

GREAVES   New  delux  with  double   ball

bearing (WHITE) Confirming to IS:  374/79

Class-I.  Testing and Commissioning.  The

job  involves  with supply  of  concealed

ceiling  fan  hook of 16  G  sheet  steel

round/square as required 2 1/2" deep & 10

mm  dia fan hook having 1"  pipe  conduit

entry holes on all four sides.

…..9

CONTRACTOR				ACCEPTING AUTHORITY

::9::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

23.Supply & installation of Exhaust Fan  12"

dia  (305 mm), 50 W, 900 RPM, 1200  Cu.M/   3  No.

Hr.  Make: USHA / GEC complete unit  wall

mounting.  Testing & commissioning.( The

job involves making suitable holes in the

wall  and  masonary  work  inclusive   of

materials is in contractor's scope).

24.Supply  & erection of 150 W  Flood  light

luminaire complete unit with glass  cover  10  No.

and accessories etc. Type: MWF 230/AK/150

ASYM of Make: Philips MVC-GE.MF 1x150 CAI

with metal halide lamp. The luminaire  is

to   be   fixed   by   making    suitable

arrangements  as per site conditions  and

site engineer instructions.

25.Supply & Installation of bracket type air

circulator wall mounting/column  mounting

Heavy Duty with steel tubular support for  6  No.

mounting the air circulator fan.  The air

stream   adjusted   in   horizontal   and

vertical by tilting head arrangement wire

guard  impellers.  Max.air velocity at  a

distance  of  10 times  blade  sweep  250

m/min.conforming   to   IS:    2997-1964.

Complete  unit  of  GEC  Alsthom/Crompton

Greaves  make  18" 450 mm sweep  1  Phase

motor for 12000 Cu.m/Hr. of air  delivery

suitable for mounting on a steel  column/

RCC column/Wall.  The fan has to be fixed

with  12/8  mm dia. MS  fastners,  spring

washers, double nuts-4 Nos. of four sides

by  duly welding  of 6 mm thickx350 mm  x

350 mm plate welded on the steel  column/

RCC   column/in  wall   inserter   making

suitable   arrangement   as   per    site

requirement.   Painting  the   fabricated

plate,   angle,   channels   with    rust

preventive  redoxide  and  two  coat   of

synthetic  enemal  paint.   Necessary  MS

plate/anles/channels  only will be  given

by BHEL free of cost.  The air curculator

should  be double earthed with 8  SWG  GI

wire.

….9

CONTRACTOR				ACCEPTING AUTHORITY

::9::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

26.Supply  &  installation of  sockets  with

switch  control  15/5  A,  3  pin   flush

mounting on a steel box with decolam       13  No.

sheet  cover  of  4"  x  6",  230  V  and

earthing as per site conditions.  Testing

& commissioning.

27.Supply & installation ofconcealed/surface

steel conduit pipe wiring, 1.5 Sq.mm, 660

V grade PVC insulated COPPER cable run in  59   Pt.

16  G steel conduit pipe of suitable  dia

(as per for IS for wiring points) with 14

G  GI  wire for earth  continuity.   Each

light  should  be controlled  a  3  plate

ceiling  rose / connector.  Each  fitting

should be controlled by independent  MCB.

28.Supply & installation of concealed  steel

conduit  pipe  wiring with  2.5 Sq.mm PVC

insulated  and COPPER  cable run in  16 G

steel  conduit pipe of suitable  dia  (as   13  Pt.

per  IS for wiring points) with 14  G  GI

wire for earth continuity.  The wiring is

for  15/5 Amps sockets  (Independent  ckt

for   each   socket   from   power    MCB

Distribution  board).  Testing &  commng.

This  wiring  should not  be  mixed  with

lighting conduit wirin).

29.Supply  and installation of  PVC  conduit

pipe  of 1.5 mm thick 1" dia  with  nece-  200  RM

ssary  clamps,  couplings,  Jn.boxes   at

every  3.6 Mtrs.  The conduit to be  laid

inside  the  building at a height  of  9"

from  the  ground level for  drawing  the

telephone  cables  with a 14 G  GI  guide

wire drawn in.

30.Supply  & Installation of Junction  boxes

(Teak   wood  boxes  of  10"x8"x4"   deep

(inside) with decolam sheet cover of  2.5   4   No.

mm  thick  of plain colour  as  required.

Thickness  of wood 3/4" teak  wood.   The

…10

CONTRACTOR				ACCEPTING AUTHORITY

::10::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

decolam sheet cover should be fixed on to

box with counter sunk screws, cup washers

etc.  concealed in the walls as  junction

boxes  for the telephone cables  at  each

ends.

31.Instln.of BHEL free issued 2 Plate ceiling

rose  on a teak wood box  flush  mounting

decolam sheet cover size 6"x4 1/2"x2 1/2"   8   No.

deep,  thickness  3/4" teak  wood  double

varnished with a decolam sheet cover  2.5

mm thick with counter sunk screws and cup

washers  etc. for telephone  connections.

Testing & commissioning. The teak wood

box,decolam cover,counter sunk screws etc.

are to be supplied by the Contractor.

32.Supply & installation of MCB Distribution   4   No.

board with TPN 415 V, 12way consisting of   No.

(32Amps - 12 Nos. on each phase,  sheet

enclosed  dust & vermin  proof,  (KST1/4)

readymade  unit of STANDARD / KOPP   make

along with controlling ICTPN switch  fuse

unit 32 A HRC fuse units, reverse  entry

cable  box,  cable  glands,  PVC  marking

ferrules   etc.   fixed   on   a   neatly

fabricated steel frame and mounted on  to

….11

CONTRACTOR				ACCEPTING AUTHORITY

:11::

--------------------------------------------------------------------

Sl.       Description of item                Qty. Unit  Rate  Amount

No.                                                     each

Rs.

--------------------------------------------------------------------

walls    as   required    for    lighting

distribution.  The job includes  painting

of steel frames, end connections,  double

earthing,      labelling/writing      the

connection  chart  inside the  door  with

WHITE duco paint as required.  Testing  &

commng.

---------

Total:

---------

--------------------------------------------------------------------

NOTE:

1. Cable joints are to be carried out by

a qualified cable jointer and should be

carried in presence of site engineer.

2. These are urgent and most critical works.

The agency should deploy required manpower

of certificate holders and should be

supervised by a Diplamo holder.

3. The site supervisor should contact the

site engineer for taking day-to-day

instructions during morning and in 2nd

half every day.

CONTRACTOR                    ACCEPTING