## BOQ
| Haridwar 2A | ANNEXURE-"A"
Design, Engineering, Supply, installation, Testing and commissioning of the project "25MVA ,132/6.6 kV Transformer Circuit with associated equipments for 800 MW T/G Test facility" at BHEL, Haridwar.
SL | Description and Details of Equipment | Make | Unit | Qty.
A. | Equipments :-
1 | ISOLATOR :- 145KV, 600A, Tripple pole, Centre Post Rotating Horizontally Double Break ISOLATOR, suitable for 31.5 kA for 1 Sec., Electrically & manually Operated with One Manually operated Earth Switch with Support Insulator & Support Structure, complete with all accessories. Applicable Standadrs for Isolator IS:9921 (Part I to V) / IEC 1128, for Insulator IS:2544 with upto date ammendments. | GR Power, Elpro, S&S or other Standard make conforming to given IS. | No. | 1
2 | CURRENT TRANSFORMER :- 145KV, 150/1A (3 Cores), 31.5 kA for 1 Sec., CURRENT TRANSFORMER, Out door, oil cooled, hermatically sealed , Dead Tank, for Differential Protection, Over Current & Earth fault Protection and Metering purpose, with Support Structure. Applicable Standadrs for Current Transformer IS:2705, for Bushings IS:2099, for Insulating Oil IS:335 with upto date ammendments. | ABB, Areva & Siemens | Nos. | 3
3 | CIRCUIT BREAKER :- Supply of 145 KV, 2500 A, 31.5 KA for 1 Sec., SF6 CIRCUIT BREAKER with support insulators and structure, suitable for 110 V DC supply, rated Impulse withstand Voltage 650 kVp, rated operating duty O - 0.3 Sec.-CO - 3 Min - CO. Applicable Standadrs for SF-6 Circuit Breaker IEC 56 with upto date ammendments. | ABB, Areva & Siemens | No. | 1
4 | LIGHTENING ARRESTOR :- 120kV, 10KA Surge Arrestors/ Lightening Arresters with surge monitor (Metal Oxide Gapless LA) (1-ph). Insulated copper conductor of adequate length shall be provided for connecting LA base and surge counter. Applicable Standadrs for Lightening Arrester IS:3070 / IEC 99, for Insulator IS:2544 with upto date ammendments. | ABB, Areva & Siemens | No. | 3
5 | POWER TRANSFORMER :- 25 MVA, 132/6.6 KV, POWER TRANSFORMER with first filling of Transformer Oil with 10% extra Oil, Vector Group YNyn0, ONAF, 12.5% Reactance with OLTC with step size 1.25%, HT side Bushing suitable for ACSR Deer and LV cable box suitable for 12 Nos. of 1x630 Sq.mm XLPE Alluminium cable (one HT & one LT Bushing required as Spare). Applicable Standadrs for Transformer IS:2026, with upto date ammendments. | ABB, Areva & Siemens | No. | 1
6 | CONTROL PANEL :- Control relay & protection PANEL for 25 MVA Transformer with remote & local control on load tap changer panel having control switches, control cable incorporating indicating lamps, tape position indicator, oil & winding temp. indicator, control switch with discripency indicator, ammeter, voltmeter, Static protection relays for over current, earth fault and Differential, and auxiliaries & tripping Flag relays for PRV, Buchholze, oil & winding temp., oil level (alarm & tripping), Flag relays for all SF-6 Circuit Breaker control & protection, Power meter with accuracy Class 0.5, featuring KW, KVA, KVAR, KWH, KVAH, KVARh, Frequency, Voltage, Current, Power Factor, inputs available 110 VAC (from PT) and 110 VDC(Charger/Batter Bank) and any other control & protection for transformer & OLTC. Applicable Standadrs for Panel IS:3427, IEC 298, BS 5277, VDE 0670 with upto date ammendments. | ABB, Areva, Siemens and L&T | No. | 1
7 | REACTOR :-2500A, 6.6 KV,30 MVA, Air cooled REACTOR, 12.5% Reactance | ABB, Areva, Siemens or other Standard make conforming to relivant IS. | Nos. | 3
Contnued….2…
---- 2 ----
SL | Description and Details of Equipment | Make | Unit | Qty.
8 | INCOMER PANEL :- Incomer VCB, 6.6 KV,2500 A, 31.5 kA for 1 Sec., should have bus bar arrangement to accomodate 12 nos.cable (Heat shrinkable Type) end termination of 1X630 Sq.mm with Current Transformer (Qty.-3 Nos.) of 6.6KV, 3000/1A (3 Cores for Differential Protection, Over Current & Earth fault Protection and Metering purpose) fitted with Bus-Bars on each phase., Incorporating indicating lamps, control switch, ammeter, voltmeter, protection relay for over current & earth fault (static) and other auxiliary relays for anunciation & alarm purpose, Power meter with accuracy Class 0.5, featuring KW, KVA, KVAR, KWH, KVAH, KVARh, Frequency, Voltage, Current, Power Factor (for supply valtage 110 VAC and control voltage 110 VDC), metering instrument should be of Accuracy Class 1.0.Degree of protection not less than IP-54 fabricated out of CRCA Sheet Steel. Applicable Standadrs for Panel IS:3427, IEC 298, BS 5277, VDE 0670 with upto date ammendments. | ABB, Areva, Siemens and L&T | No. | 1
9 | OUTGOING PANEL :- Out going VCB 6.6kV, 2500A, 31.5 kA for 1 Sec. with copper bus bar to accomodate 9 nos. cable end termination (Heat Shrinkable Type) of 3X300 Sq.mm size with Current Transformer (Qty.-3 Nos.) of 6.6KV, 3000/1A (2 Cores for Differential Protection, Over Current & Earth fault Protection (PS Class) and 1core for Metering purpose (Accuracy class-2) fitted with Bus-Bars on each phase, with support structure. Incorporating indicating lamps, control switch, protection relay for over current & earth fault (static) and other auxiliary relays for anunciation & alarm purpose, Power meter with accuracy Class 0.5, featuring KW, KVA, KVAR, KWH, KVAH, KVARh, Frequency, Voltage, Current, Power Factor (for supply valtage 110 VAC and control voltage 110 VDC), metering instrument should be of Accuracy Class 1.0.Degree of protection not less than IP-54 fabricated out of CRCA Sheet Steel. Applicable Standadrs for Panel IS:3427, IEC 298, BS 5277, VDE 0670 with upto date ammendments. | ABB, Areva, Siemens and L&T | Nos. | 2
10 | P.T. PANEL :- Suitable for 6.6 kV/110V Drawout type PT, which shall be supplied with Voltage indicator and complete with all respect. Applicable Standadrs for Panel IS:3427, IEC 298, BS 5277, VDE 0670 with upto date ammendments. | ABB, Areva, Siemens and L&T | No. | 1
11 | LT POWER DISTRIBUTION PANEL :- Incomer ACB, 3 phase, 50 Hz +/- 5%, 415 Volt +/- 10%, 600A, 31.5 kA for 1 Sec. with 6 Nos. out going of 415 Volt, 100 Amp. each, complete with bus bar for three phase & neutral, switches, fuses, indications, voltmeter, ammeter should be of accuracy Class 1.0, eart switch. Complete with all accesories & fittings. Degree of protection not less than IP-54 fabricated out of CRCA Sheet Steel (2 mm thick), free standing & floor mounting. Shall be used for feeding LT power to main transformer OLTC, SF-6 Circuit breaker and all other auxiliary equipment and lighting etc. | ABB, Areva, Siemens and L&T | No. | 1
12 | XLPE CABLE :- 1X630 sq. mm, 6.6 KV (E) XLPE cable Alluminium Conductor, Non-magnetic round armouring, 12 Lengths of 250 RM each (from transformer to reactor and reactor to 6.6 KV Incomer Panel). Applicable Standadrs for cable IS:7098 (II) 1985 with upto date ammendments. | CCI, Uniflex, RPG, Torrents & Universal | RM | 3000
13 | XLPE CABLE :- 3X300 sq. mm, 6.6 KV (E) XLPE cable Alluminium Conductor, round steel armouring, 27 Lengths of 700 RM each (from 132 kV sub-station to Test bed). Applicable Standadrs for cable IS:7098 (II) 1985 with upto date ammendments. | CCI, Uniflex, RPG, Torrents & Universal | RM | 18900
14 | JOINTING KIT :- End termination joints (heat shrinkable type) suitable for 1X630 sq. mm. XLPE Cable | Rechem make | Nos. | 55
15 | JOINTING KIT :- Straight through joints (heat shrinkable type) suitable for 3X300 sq. mm. XLPE cables . | Rechem make | Nos. | 25
16 | JOINTING KIT :- End termination joints (heat shrinkable type) suitable for 3X300 sq. mm. XLPE cables | Rechem make | Nos. | 25
17 | CONTROL CABLES :- 1.1 KV grade, control cables with copper conductor PVC insulated with inner seathed and armoured. Applicable Standadrs for cable IS: 1544 (1/1988) with upto date ammendments. | CCI, Uniflex, RPG, Torrents & Universal | Lot | 1
Contnued….3…
---- 3 ----
SL | Description and Details of Equipment | Make | Unit | Qty.
B. | Other Items :-
i) | Gantry structure (Galvenised) as per IS: | Kamani, Richardson & Crudas or other Standard make | Lot | 1
ii) | Conductor (Deer). Applicable Standadrs for conductor IS:398 (1961) with upto date ammendments. |  | Lot | 1
iii) | Clamps connector as per IS: |  | Lot | 1
iv) | Earth mat with 40 mm MS round rods as per IS: |  | Lot | 1
v) | Earthing pits as per IS: |  | Lot | 1
vi) | Sheilding wire as per IS: |  | Lot | 1
vii) | Equipment earthing from GI Strip (50x6 mm) with earth mat X-axis & Y-axis as per IS: |  | No. | 1
viii) | Lighting mast as per IS: | Kamani, Richardson & Crudas or other Standard make | Lot | 1
ix) | Illumination (Luminaire of 1000 Watt metal halide with Lamp, control gears and photo cell etc.) for switch yard as per IS: | Philips, Crompton & Bajaj | Nos. | 4
NOTE :-
1. All the above items includes support structure & other accessories required to complete the work.
2. Power supply of 415 Volt AC, 110 Volts AC & 110 Volts DC are available.
3. Type test and routine test certificate (original and one copy), O&M manual (3 sets) for individual equipments shall be provided by the party.
4. All G.A. drawings for Isolators, Lighting arrestors, Current transformers, Potential transformers, Power transformers and HT Panels, Cotrol & relay panels wiring scheme are to be provided by the party.
5. Plan, sections, layout of switchyard & drawings of foundations for Transformer and other equipments etc., cable schedule, lighting layout, earthing layout, schematic diagram and as built drawings/documents are to be provided for approval from BHEL by the party well before the start of installation work.
6. Party has to arrange approval of drawings inspection for the above Project before commissioning of the system from Central Electrical Authorities/Inspectorate.
7. Detail designing of the project shall be done by the party and shall take the approval from BHEL.before start of work.
8. All the Control wiring shall be carriedout with 650 Volt grade standard copper wire, PVC insulation. For CT & PT circuit the wire size should be 2.5 Sq.mm. and other circuit shall be with 1.5 Sq.mm copper wire.
9. Tape off from the existing 132 KV line shall be done by the party.
10. Supply of consumables like nuts & bolts for foundations and other equipments, clamps, connectors, SF-6 gas or any other instruments/machines required for the erection, testing & commissioning of the above equipment shall be done by the party.
BHEL, Haridwar Scope of Work :
1. Excavation & levelling of site.
2. Preperation of Equipment foundations, cable trenches, oil soak pits etc., however the drawings shall be prepared & submitted by the party for approval from BHEL.
3. Electrical power & water supply will be provided free of charge for construction work.