## Sheet1
BHARAT HEAVY ELECTRICALS LIMITED
| Heavy Power Equipment Plant, Ramachandrapuram, |  | Enquiry No.: | M2/06/CG6P0701/KRP
| Hyderabad - 502 032. INDIA. |  | Due Date : | 06/09/2006
| Phone Nos. : 0091 - 040 - 2318 2581 |  | Supplier Qtn. No.:
| Fax Nos.: 0091 - 040 - 23021910 & 23021954 |  | Date :
E-mail : kollipara@bhelhyd.co.in
TENDER DOCUMENTS TO BE FILLED BY THE SUPPLIER FOR SUPPLY OF
DC WELDING GENERATOR [Total QTY : 1 Nos.]
NOTE:-
1. Vendor must submit complete information against clause no. 15.0 The offer meeting this clause would only be processed.
2. The "Offered' Column and where applicable, the "Deviations" & "Remarks" Column of this format shall be filled in by the Vendor and submitted along with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specifications / requirements shall be treated as non-compliance.
3. The offer and all documents enclosed with offer should be in English language only.
ADDRESS OF THE SUPPLIER :
TELEPHONE NOS.:
FAX NOS.:
E-MAIL ADDRESS :
SCOPE : SUPPLY & COMMISSIONING OF 320 AMPS DC WELDING GENERATOR COMPLYING WITH SPECIFICATION AS BELOW.
SL.NO. | DESCRIPTION FOR BHEL REQUIREMENT | SPECIFIED / TO BE CONFIRMED BY | OFFERED | DEVIATIONS | REMARKS
1.0 | MAIN PARAMETERS
| PURPOSE | For heavy metal deposit and X-ray quality joints welding using the electrode E 7018, E 309, E 318 etc.
2.0 | TECHNICAL PARAMETERS
2.1 | Output current | 35-320 Amps , at 60% duty cycle: 320 A minimum , at 100% duty cycle :250 A
2.2 | Open circuit voltage | 100 V
2.3 | Power | 13.5 Kw
2.4 | Starting | Star / Delta starter as per IS:13947(Part - IV)
2.5 | Speed ( Synchrounous ) | Vendor
2.6 | Recommended switch fuse rating | Vendor
2.7 | Over voltage, under voltage and single phase protection | Vendor
2.8 | Protection of machine | Vevdor
2.9 | Welding electrode range | 2 - 6.3 mm
2.10 | Insulation | Class F
2.11 | Machine cooling | Fan cooled
2.12 | Voltmeter Ammeter attachment | Vendor
2.13 | Remote control with 5 metres cable length | Vendor
2.14 | Inbuilt electronic power saver to facilitate machines shut down if idling for more than 5 mintues | Vendor
2.15 | Ease of mobility ( wheels & handles etc. ) | Vendor
2.16 | Enclosure | Vendor
2.17 | Power and earth cable minimum | 5 meters
2.18 | Welding holder and cable for 320 amps current carrying capacity | Vendor
3.0 | GENERAL :
3.1 | Weight of the full unit | Vendor
3.2 | Enclosure of the Motor | Vendor
3.3 | Input power supply cable | To be suitably protected
4.0 | ELECTRICAL :
4.1 | 415V + 10% / -10%, 50HZ +/-3 Hz, 3 Phase AC (3 wire system with out neutral) Power Supply will be provided by BHEL near the machine. All types of cables, connections, starter etc. required for connecting BHEL's power supply point to welding generator, shall be the resposibility of vendor. Requirement of grounding/earthing with required material details should be informed by vendor well in advance so that same could be made available. | Vendor
4.2 | All electrical & electronic control cabinets & panels should be dust and vermin proof | Vendor
4.3 | Motors shall conform to IEC or Indian Standards | Vendor
4.4 | Vendor should ensure the proper earthing for the machine and its peripherals. | Required
5.0 | SAFETY ARRANGEMENTS: | Vendor
1. Generator should have adequate and reliable safety features/ devices to avoid damage to the generator due to the malfunctioning or mistakes.
6.0 | ENVIRONMENTAL PERFORMANCE OF THE MACHINE : | Vendor
The generatorystem should conform to following factor related to environment :
If any safety / environmental protection enclosure is required it should be built in the machine by the vendor.
7 | SPARES:
7.1 | Itemised breakup of any other spares used on the generator in sufficient quantity as per recommendation of Vendor for 2 years of trouble free operation on three shifts continuous running basis should be offered by vendor. | Vendor
7.2 | All types of spares for total generator and accessories should be available for atleast ten years after supply of the of the generator is likely to become obsolete in this period, the vendor should inform BHEL sufficiently in advance and provide drawings of parts / details of spares & suppliers to enable BHEL to procure these in advance, if required | Vendor
7.3 | Vendor to confirm that complete list of spares for generator and accessories, along with specification / type / model, and name & address of the spare supplier shall be furnished along with documentation to be supplied with the generator | Vendor
8 | DOCUMENTATION : Five sets of following documents (Hard copies) in English language should be supplied along with the machine | Vendor
8.1 | Operating manuals of generator
8.2 | Detailed Maintenance manual of generator with all drawings of system.
9 | COMMISSIONING
9.1 | Supplier to take full responsibility for testing of generator with all supplied items. The supplier shall commission the machine at BHEL works and prove the perforamance. Service requirement like power, air shall be provided by BHEL at only one point to be indicated by supplier. | Vendor
9.2 | Charges, duration, terms & conditions for Commissioning should be furnished in detail separately by vendor along with offer. | Vendor
10 | AMBIENT CONDITIONS & THERMAL STABILITY :
10.1 | Total machine and all supplied items should work trouble free and efficiently under following operating conditions. Ambient Conditions: Temperature = 0 5 to 45 degree celsius Relative Humidity = 95% max. (Vendor to confirm that machine is suitable for above) | Vendor
10.2 | The generator and accessories, should be suitable for 24 hrs. continuous operation to its full capacity for 24 hour a day and 7 days a week throughout. Vendor to ensure and confirm the same. | Vendor
11 | ACCEPTANCE: (Tests/Activities to be Performed by Vendor) | Should be accepted & confirmed by Vendor
| Tests/Activities to be carried out at supplier’s works on the machine before dispatch : | IS : 2635 / Applicable Std.
Tests/Activities to be carried out at BHEL works while commissioning the machine :
11.1 | The machine should be tested for welding continuously for 8 hrs. If any break down occurs during this test, the test should be repeated for 8 hrs from that time.
11.2 | Demonstration of all features of the generator & accessories to the satisfaction of BHEL for efficient and effective use of the system.
12 | PACKING:
12.1 | Rigid packing for all items of complete system, all Accessories and other supplied items to avoid any damage/loss in transit. | Vendor
13 | GUARANTEE :
13.1 | 24 months from the date of acceptance of the generator | Vendor
14 | GENERAL :
14.1 | Model No. | vendor
14.2 | Total connected load (KVA): | vendor
14.3 | Floor area required (Length, Width, Height) for complete generator | vendor
14.4 | Total weight of the generator | Vendor
14.5 | Vendor to submit , along with offer, reference list of customers where similar generators have been supplied mentioning broad specifications of the supplied generators | Required
14.6 | Detailed catalogues , sketch/ photographs of the generator and accessories should be submitted with the offer. | Required
15 | REFERENCE LIST / QUALIFYING CONDITIONS :
15.1 | Only those vendors, who have supplied and commissioned at least one Welding generator of same cpacity or higher sizes for similar applications in the past five years and such generator is presently working satisfactorily for more than one year after commissioning, should quote.However,if such generator(s) has/had been supplied to BHEL, then such generator should be presently working satisfactorily for more than six months after its commissioning and acceptance in BHEL, should quote. The following information should be submitted by the vendor about the companies where similar generator have been supplied. This is required from all the vendors for qualification of their offer. | Vendor
1.Name of the customer/company where similar generator is installed.
2. Complete postal address of the customer.
3. Year of commissioning.
4. Application for which the machine is supplied.
5. Name and designation of the contact person of the customer.
6. Phone, FAX no. and email address of the contact person of the customer.
7. Performance certificate from the customers regarding satisfactory performance of system supplied to them