## Sheet1
Ref. No. HY/OP/CAPITAL/2006-07/008, Dated: 18/07/2006
| BHARAT HEAVY ELECTRICAL LIMITED |  |  | Enquiry No. :
| UNIT'S ADDRESS: |  |  | Due Date :
| UNIT'S PHONE NOS. |  |  | Supplier Qtn. No.:
| CONTACT PERSON'S NAME/DESIGN./PHONE NO./E-MAIL (FROM PURCHASE DEP'T.) |  |  | Date :
SPECIFICATION CUM COMPLIANCE CERTIFICATE FOR DATA ACQUISITION SYSTEM
NOTE:-
1. Vendor must submit complete information against clause no. 17.0 The offer meeting this clause would only be processed.
2. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specifications/requirements shall be treated as non-compliance.
3. The offer and all documents enclosed with offer should be in English language only.
ADDRESS OF THE SUPPLIER : |  |  |  | ADDRESS OF THE INDIAN AGENTS :
TELEPHONE NOS.: |  |  |  | TELEPHONE NOS.:
FAX NOS.: |  |  |  | FAX NOS.:
E-MAIL ADDRESS : |  |  |  | E-MAIL ADDRESS :
SCOPE: SUPPLY & COMMISSIONING OF DATA ACQUISITION SYSTEM WITH SPECIFICATION AS BELOW
Sl. NO | DESCRIPTION FOR BHEL REQUIREMENT | SPECIFIED BY | OFFERED | DEVIATIONS | REMARKS
1 | PURPOSE
1.1 | The system is required for automatic Logging, monitoring & measurement of field Test parameter acquired through field instruments during testing of Planetary gear box. | Confirm
2 | Technical Specification :
2.1 | The data acquisition system shall be latest design compatible to LAN based network system incorporating embedded program coding for easy software Installation through Ethernet of fiber optics communication & The system shall essentially consist of the following : | Confirm
| a) Main Controller with M 2.0 GHz P IV processor and Real time embedded Software.. | Confirm
| b) Local automation module with 16 bit ADC digital I/O & Triggering & 32 bit counters. | Confirm
| c) Base TX Ethernet Communication between main controller & local module. | Confirm
| d) Data Acquisition system capable of performing multi flexing, Signal conditioning, Switching, Amplification, filtering, Isolation with industries highest, bit ADC . | Confirm
| e) Separate real time DAS software package on windows XP ver : 2001 or higher, fully customized to cater the requirements for real time solutions through real time controller using embedded codes on Operating system for development of package . | Confirm
f) Accessories and Spares .
| g) Various instruments and sensors required for testing shall be connected to the Local Modules. The local modules shall be compact, light weight portable units capable of signal conditioning, excitation, multiplexing, digitizing switching, and communicating with the main controller. The main controller unit shall be Pentium--IV M 2.0 GHz with real time embedded software to support PC based LAN communication through Ethernet or fiber optics. The minimum PC requirement shall be PIV processor loaded with real time Date Acquisition module/Software to support Windows--XP or higher. | Confirm
2.2 | Main Controller unit & embedded system with the following features.
2.2.1 | Microprocessor | Intel Pentium -IV M 2.0 GHz real time embedded Software.
2.2.2 | Math Co- processor | Built in.
2.2.3 | On- chip cache Memory | 256 KB L2 Cache & 400 MHz Front side Bus.
2.2.4 | Chipset: | Intel 845 chipset with AGP 4X support .
2.2.5 | RAM | 512 MB dual channel DDR2 RAM standard expandable up to 2.0 GB.
2.2.6 | Clock Speed | 2.2 GHz or faster .
2.2.7 | Single channel PID loop & software development platform for real time application . | Confirm
2.2.8 | 10/100/1000 Base TX (Gigabit), Ethernet . | Confirm
2.2.9 | Integrated hard drive, GPIB, Serial, & other peripherals . | Confirm
2.3 | PC hardware & Software requirement
2.3.1 | Hard Disk | 120 GB & 10GB SCSI
2.3.2 | Key board | Suitable for Windows 2000/XP With high MTBF .
2.3.3 | Mouse | USB Mouse
2.3.4 | Interfaces
| 1 parallel, 4USB, 2 Serial. GPIB, Keyboard, pointing device, video (Monitor), 1RJ --45 jack, 1 Line - in, 1 Line --out, Head phone jack . | Confirm
2.3.5 | Processor | Pentium IV 2.0 GHz, 512 MB RAM,
2.3.6 | Monitor | 21" SVGA monitor color
2.3.7 | Video RAM | 32 MB or More .
2.3.8 | Video card | Video card with 32 MB RAM
2.3.9 | Expansion Slots | 5 PCI , 1 AGP PRO 4X
2.3.10 | Operating System | MS Windows XP/2000 (with original back -up on CD ROM)
2.3.11 | Software | Data acquisition developmental real time software module
2.3.12 | Network | In built port or network card with 300 m Ethernet cable
2.3.13 | Sound Card | Integrated 32 bit sound card
2.3.14 | Printer | Hewlett Packard make Scanner cum - color jet printer.
2.3.15 | Drives
| a) 3.5"(1.44 MB) diskette drive | Confirm
| b) Internal SCSI Plax writer 12x10x32 or greater CD- RW drive Compatible with INCD sw or equivalent with 2 blank pre formatted CR_RW disks (Compatible with Plax Writer INCD sw or equivalent and highest speed available . | Confirm
2.3.16 | Modules required for communicating with local modules . | Confirm
2.3.17 | Facility for connecting over to LAN | Confirm
2.3.18 | Real Time clock with battery backup . | Confirm
2.4 | Local Automation Modules :
2.4.1 | Main data acquisition unit shall be compact, ruggeidsed with rack mounted chassis for main controller and local modules for acquiring data from variety of field Instruments, I/O modules, and communication modules for hardware PC Interface. The various instruments and sensors shall be Terminated in the local module. Main controller shall be a real time processor with intelligent unit built on PXI platform (The PCI Extensions for Instrumentation). Each local modules shall essentially have the architecture where it includes instrumentation amplifier, low pass filters & multiplexer forming SIXI ( Signal conditioning extensions for Instrumentation) platform for data acquisition and control system. | Confirm
2.4.2 | The data acquisition unit/ system, which comprises of main controller & local module shall essentially have the following salient features ::
| a) Excitation DC power supply for the pressure transmitters, preamplifiers and other Instrument/devices . | Confirm
| b) Signal conditioning of the input signal as per the system requirement | Confirm
| c) Multiplexing, scanning better than 200 channels per seconds . | Confirm
| d) Digitizing 16 bit A/D conversion . | Confirm
| e) Communication interface with the main control unit . | Confirm
| f) Programming, parameter display and diagnostic facility through a detachable local monitor . | Confirm
| g) Operating condition of data acquisition unit : 5 tom 55 C, acoustic emissions below 32 db Shop floor environment . This modules/units shall be placed near rotating equipment They may be subjected to vibration and shock . | Confirm
| h) The terminal connectors shall be highly ruggedised Push fit (Wago) type as they may be subjected to frequent connection / disconnection . | Confirm
| i) The local module enclosure should be waterproof to be safeguarded it from water or oil spillage . | Confirm
| j) Capable of Capturing and processing live picture of the rotating equipment along with other process parameters . | Confirm
| k) Data update rate for total number of configured channels (100 maximum) shall not be more than 500 milliseconds | Confirm
2.5 | Instruments shall be connected to local module | Measuring channel Accuracy
2.5.1 | a) 4 wire resistance temperature detectors (Pt 100) . | +/- 0.01 deg C
2.5.2 | b) Thermocouples (all types) | +/- 0.02 deg C
2.5.3 | c) Pressure transmitter : two wire type , 4- 20 ma Provision for 3 wire and 4 wire pre transmitter with 4-20mA or 0-5 volts output with 24 volts DC excitation . | +/- 0.01%
2.5.4 | d) Turbine type Flow meters or speed sensors, 50 mv to 20 volts pulses input. Programmable threshold and hysterisis, adjustment . Provision for preamplifier Power supply (24 volts DC), speed / frequency measurement unto 10 KHz through event/ turn counters and totalizing . | +/- 1 pulse/min
2.5.5 | e) Analog inputs : 4-20mA, 0 to +_5 volts or 0 to +_ 10 volts process variable signals from vibration monitors and other control system | +/- 0.01%
2.6 | Local Module Configuration :
| List of Devices to be terminated in the local module | Number Of Channels Requirement
2.6.1 | Resistance Temperature Detectors | 20
2.6.2 | Thermocouples | 32
2.6.3 | Pressure Transmitter | 16
2.6.4 | Flow | 8
2.6.5 | Vibration (Analogue inputs) | 24
2.6.6 | Speed | 8
2.7 | Communication between Main control unit and Local modules :
2.7.1 | The Main controller and each of the Local modules shall be preferably mounted on the common unit with respective racks closely placed to establish reliable, uninterrupted ruggedised and fastest communication link between modules through Ethernet, fiber optic, Radio communication or equivalent . | Confirm
2.8 | Data acquisition and presentation software
2.8.1 | The soft ware shall cater to the requirements of data acquisition control, alarm, management communication, customized graphics and report generation. The real time package developed on windows that executes embedded codes on real time operating system shall be fully cater to customized requirement by using powerful and flexible development tools to build real time solution. The development features to be incorporated in customized software shall essentially include the following features . | Confirm
| a) Windows -XP/2000 based software development module | Confirm
| b) software must cater to the requirement of analogue/digital/frequence/pulse/Dcvolts Ac voltage /current/KW type of inputs . | Confirm
| c) Real time graphics, bar graphs and trend , meter display & tables . | Confirm
| d) User programmable mimic displays settings & customized report formats . | Confirm
| e) Selectable Triggering -automatic, based on time, speed, other parameter or manual . | Confirm
| f) Selectable scanning rate for each parameter & grouped . | Confirm
| g) Selectable data storage modes- delta speed, deal time, event based or manual . | Confirm
| h) In manual data storage mode, a set of readings shall be logged at the press of a key/click of mouse button and displayed in the required format., facilities shall be provided to print/store the displayed data as per the operator's choice. Point no. shall be automatically incremented by I for each set of stored readings, Auto & manual settings for scan fixed duration logging monitoring , editable post acquisition data edit facility, format, x-y plots of selectable parameters, time base trends and plots for speed, flow, pressure, temp. etc. | Confirm
| i) Scaling in engineering units & selectable gain/offset setting for each channel in Y=mX+ C form. | Confirm
| j) Selectable alarm and danger set points, real time alarm display, annunciation, print out, acknowledge/reset facilities . Alarm status screen at the click of mouse or press of a key. | Confirm
| k) User programmable channel configuration screen. | Confirm
| l) For MRT, Channel configuration facilities shall be provided for running one to Six Machines, at a time with separate storage file for each machine. | Confirm
| m) Provision for display/print, list of selected channels in a customized format. | Confirm
| n) Provision for a run-time plot ( X vs Y) screen for minimum four plot windows. X vs Y - Selectable from any of the configured channels. Provision to print any of the plot screen at operator's choice. | Confirm
| o) Post acquisition data editing facility. | Confirm
| p) Data shall be stored in a database format (ODEC), easily accessible through Micro soft-Access or any other DATABASE software. | Confirm
| q) After testing, data shall be retrieved and printed in the specific format. | Confirm
| r) Pass word administration for security. | Confirm
| s) Provision for software modifications for future improvement. | Confirm
| t) Animation facility like coloring, horizontal /vertical /angled movement, scaling for 3 D effects, rotation with real time data display . Display screen of test set-up MRT-Other test on operator's choice. | Confirm
2.9 | Vibration & acoustic measurement and analysis modules: Unlike other measurements and acquisition of process parameters, Vibration & sound measurement forms an important part of data acquisition system for Planetary gear box. Therefore separate local modules to support signals from ICP accelerometer and microphones would be required. Using latest diagnostic software tools, it is possible to carry out different analysis based to real time data acquired through data acquisition controllers for vibration & sound measurement it frequency and octave bands. Therefore main data Acquisition unit shall essentially include the basic hard ware for PCI extension of Input signals (PXI) configuration, analysis & diagnostic software shall be follows. | Confirm
2.1 | PXI Hard ware modules :
2.10.1 | It shall be essentially a eight (8) channel dynamic signal acquisition module for making high accuracy frequency domain measurements incorporating integrated electronic piezoelectric (IEPE) signal conditioning for accelerometers and microphones. Modules shall facilitate digitization of input signal over bandwidth from DC to 50 KHZ & synchronization with PXI trigger bus when used with other software tool kits. Module shall essentially have following salient features. | Confirm
| a) 8 Simultaneously sampled analog inputs | Confirm
| b) ± 10 V Range DC AC wave form 25mv to 5 V | Confirm
| c) Signal conditioning : Through software programmable AC/DC coupling IEPE/ICP source, Sensor calibration reading information using Transducer electronics Data sheet. (TEDS). | Confirm
| d) ICP Bias source : 4m A 24 V compliance (on/off) software programmable | Confirm
| e) Bandwidth | 50 KHZ Alias free
| f) Sampling eate | 102 4KS/s max sampling rate.
| g) Frequency Range | 0.16 Hz to Khz
| Resolution | 0.01 Hz
| h) Spectral lines Resolution | 64 to 25600 line for high resolution.
| i) FFT Windowing | Henning, Blackman Harries, Flat Top Exponential functions
| j) Averaging | Linear, Exponential, peak hold & Time Synchronous
| k) 2 Independent Tach inputs for RPM measurement. | Confirm
| l) 3D plot & display of spectrum single, dual harmonic | Confirm
| m) display functions : includes Time, spectrum, power spectrum, PSD, FRF, Transfer function, cross spectrum, (Magnitude, phase,real,imaginary,Nyquist ) Coherence, fractional Octave, third Octave | Confirm
| n) Signal connectivity : BNC, or any other type of signal termination in line with standard practice | Confirm
| o) High pass filter | 0.1 Hz & 1 Hz software programmable
| p) Alias Rejection | 75 db min.
2.11 | Sound & Vibration software package for Octave Analysis, FFT,FRF,THD,TMD
2.11.1 | This soft ware shall be developmental and offer the following measurement and analysis | Confirm
| a) Audio measurement and Fractional octave analysis | Confirm
| b) Swept sine analysis and sound level measurements | Confirm
| c) FFT analysis and Frequency analysis and Transfer functions | Confirm
| d) Frequency Response measurements & Transient Analysis | Confirm
| e) 3D plot & display of spectrum single, dual harmonic | Confirm
| f) display functions : includes Time, spectrum, power spectrum, PSD, FRF, Transfer function, cross spectrum, (Magnitude, phase,real,imaginary,Nyquist ) Coherence. | Confirm
| g) Measurement, display and analysis of vibration in narrow and wide frequency bands | Confirm
| i) Narrow band | 0.5 Hz to 200 Hz 800 Lin es Resolution
| ii) Wide band | 0.5 HZ to 1Khz > 1600 Lines resolution
| h) Software shall provide an easy to use foundation with more than 50 example for sound and Vibration application. | Confirm
| i) Software shall support and facilitate comprehensive sound & vibration measurement. | Confirm
| j) Audio measurements such as THD, TMD,SNR,SINAD & swept sine. | Confirm
| k) Fractional Octave analysis with weighting for audio spectrum | Confirm
| l) Software for simplified analysis set up | Confirm
| m) Frequency measurements including base band FFT& Frequency response function | Confirm
| n) Sound level with weighting and vibration level with Integration measurements | Confirm
| o) Audio, Vibration, Spectrum, and Frequency analyzer. | Confirm
2.12 | NETWORKING:
2.12.1 | Machine control should have necessary hardware and software for interfacing with gigabit Ethernet Local Area Network with 100 MB/sec through UTP cables for data transfer. This network to be connected to wide area network/Internet. The networking should have following capabilities. | Confirm
| a) The system / equipment shall appear as a node in the Entire Network. (Network Neighborhood) | Confirm
| b) The program transfer shall be by simple copy and paste method provided sharing access is allowed between any PC and the Data acquisition system across the network. | Confirm
3 | Testing
3.1 | The Data Acquisition System shall be tested in accordance with standard practices using signal generators and calibrators for simulation of measurement parameters. | Confirm
3.2 | Additional tests, if any shall be specified in the enquiry & vendor to include these tests in the offer | Specify
3.3 | All the above tests should be demonstrated to BHEL engineers during pre-acceptance at Suppliers works and during Erection & Commissioning at BHEL Works. | Confirm
4 | AMBIENT CONDITIONS & THERMAL STABILITY :
4.1 | Total equipment should work trouble free and efficiently under following operating conditions. Ambient Conditions: Temperature = 5 to 45 degree Celsius Relative Humidity = 95% max. (Confirm that machine is suitable for above and details of provisions on the machine for the same should be furnished) | Confirm
4.2 | Weather conditions are tropical, Atmosphere may be dust laden during some part of the year. Equipment shall be kept in the normal shop floor condition. Max. temperature variation is 25 deg Celsius in 24 hours. | Confirm
4.3 | Thermal Stability of the complete equipment keeping in view specified Ambient Conditions and accuracy requirements of BHEL and trouble free operation of the equipment should be ensured by vendor. (Confirm that machine is suitable for above and details of provisions on the machine for the same should be furnished) | Confirm
4.4 | The equipment including attachments & accessories should be suitable for 24 hrs. continuous operation to its full capacity for 24 hour a day and 7 days a week throughout. Vendor to ensure and confirm the same. | Confirm
4.5 | If any safety / environmental protection enclosure is required it should be built in the machine by the vendor. | Confirm
5 | ELECTRICAL :
5.1 | 415V + 10% & -15%, 50HZ +/-3%, 3 Phase AC (3 wire system with out neutral) Power Supply Voltage will be provided by BHEL at a single point near the system, as per layout recommended by Vendor. All types of cables, connections, circuit breakers etc. required for connecting BHEL's power supply point to different parts of the machine/control cabinets, shall be the responsibility of vendor. Requirement of grounding/earthing with required material details is to be informed by vendor well in advance so that it be ready at the time of commissioning the system. | Confirm
5.2 | Tropicalization: All electrical / electronic equipment shall be tropicalized | Confirm
5.3 | All electrical & electronic control cabinets & panels should be dust and vermin proof | Confirm
5.4 | All electrical components in the cabinets should be mounted on DIN Rail | Confirm
5.5 | All electrical and electronic panels including operator's panel should be provided with fluorescent lamps for sufficient illumination and power receptacles of 220Volts, 5/15 Amp AC. All adapters/receptacles should have compatibility with Indian equivalents. | Confirm
5.6 | Vendor should ensure the proper earthing for the machine and its peripherals. | Required
5.7 | In-cycle hour counter with reset facility. | Required
6 | SAFETY ARRANGEMENTS:
6.1 | Following safety features in addition to other standard safety features should be provided on the machine:
| 1. System / Equipment should have adequate and reliable safety interlocks / devices to avoid damage to the equipment and the operator due to the malfunctioning or mistakes. System / Equipment functions should be continuously monitored and alarm / warning indications through lights / Alarm No. with massages (On display panels) should be available. | Confirm
| 2. A detailed list of all alarms / indications provided on the equipment should be submitted by the supplier. | Required
7 | SPARES:
7.1 | Itemized breakup of electrical and electronic spares used on the equipment in sufficient quantity as per recommendation of Vendor for 3 years of trouble free operation on three shifts continuous running basis should be offered by vendor. The list to include the following in addition to recommended spares (Unit price of each item of spare should be offered) | Specify
7.2 | Electrical /Electronic Spares: All types of Relays, Contactors, Proximity Switches, Push Buttons, Indicating Lamps, Semiconductor Fuses, Special Fuses, Circuit Breakers, Main Power Switch, Encoders, Operator panel with display unit , Power module & Control cards for main drives as well as feed drives. | Specify
7.3 | All types of spares for total machine and accessories should be available for at least ten years after supply of the equipment. If the equipment or control is likely to become obsolete in this period, the vendor should inform BHEL sufficiently in advance and provide drawings of parts / Details of spares and suppliers to enable BHEL to procure them in advance if required. | Confirm
7.4 | Vendor to confirm that complete list of spares for the system and accessories, along with specification / type / model, and name & address of the spare supplier shall be furnished along with documentation to be supplied with the equipment. | Confirm
8 | DOCUMENTATION : Five sets of following documents (Hard copies) in English language should be supplied along with the machine | Confirm
8.1 | Operating and maintenance manuals of the Equipment
8.2 | Test reports of all the tests to be carried out on the Data Acquisition System shall be furnished .
8.3 | Detailed Maintenance manual of the equipment with all drawings of assemblies/sub-assemblies/parts including Electrical/Electronic circuit diagrams. All Assembly / Sub Assembly Drawings shall be supplied with part list also.
8.4 | Catalogues, O&M Manuals of all bought out items including drawings, wherever applicable.
8.5 | One additional set of all the above documentation on CD ROM, wherever possible.
9 | PROVE OUT OF BHEL COMPONENTS :
9.1 | Complete prove out of the system / equipment shall be done at BHEL works to the specified design accuracy after commissioning. Job for the prove out of the system / equipment shall be provided by BHEL. Vendor should submit the procedure, schemes etc. in advance for the prove out. Vendor shall be fully responsible for proving out the equipment as per requirements specified by BHEL to the full satisfaction of BHEL. Clarifications, if any required by vendor, regarding accuracy requirements of the prove out components, whether specified or not, should be discussed and cleared by vendor during initial technical discussions. Vendor shall be responsible for any deviation in prove out component due to malfunctioning of the equipment during prove out. The cost of such deviations / rejection, if any, shall be refunded by the vendor to BHEL. | Confirm
10 | Data to be furnished with in 15 Days of Letter of Indent / P.O :
10.1 | Vendor shall submit the preliminary layout drawing for getting BHEL’s approval within 15 days from the date of Letter of Intent (LOI) / P.O. which ever is earlier. Complete system details and Final Layout drawings shall be submitted by the supplier within one month after getting BHEL’s approval. The layout should consist of all requirements pertaining to complete system / equipment including space requirement for any other accessories. | Confirm
11 | COMMISSIONING OF THE EQUIPMENT
11.1 | Supplier to take full responsibility for carrying out the commissioning, start up, testing of the equipment and it’s controls etc. Service requirement like power & air shall be provided by BHEL at only one point to be indicated by supplier in their layout drawings. Other requirements like crane and helping personnel shall also be provided by BHEL. Details of these requirements should be informed by vendor in advance. | Confirm
11.2 | Successful proving of the equipment for BHEL components by the supplier shall be considered as part of commissioning. All tests, as mentioned at clause 13 (Machine Acceptance) shall form part of the commissioning activity. | Confirm
11.3 | Schedule, Charges, duration, terms & conditions for E&C should be furnished in detail separately by vendor along with offer. | Specify
12 | TRAINING
12.1 | BHEL Persons should be trained at supplier's Works for mutually agreed period in the area of (a) Operation of the system / equipment & other supplied accessories. (b) Electrical and Electronic maintenance of the equipment & other supplied accessories. | Confirm
12.2 | Vendor to quote for training on man / week basis | Specify
13 | MACHINE ACCEPTANCE: (Tests/Activities should be Performed by Vendor) | Confirm
13.1 | Tests/Activities should be carried out at supplier’s works on the machine before dispatch : | Confirm
13.1.1 | The Data Acquisition system shall be tested as per clause No. 3.0 | Confirm
13.1.2 | Demonstration of all features of the system / equipment, control system & accessories | Confirm
13.1.3 | The equipment should be tested for continuous running of 48 hrs. If any break down occurs during this test, the test should be repeated for 48 hrs from that time. | Confirm
13.2 | Tests/Activities should be carried out at BHEL works while commissioning the machine : | Confirm
13.2.1 | The Data Acquisition system shall be tested as per clause No. 3.0 | Confirm
13.2.2 | Demonstration of all features of the system / equipment, control system & accessories to the satisfaction of BHEL for efficient and effective use of the equipment. | Confirm
13.2.3 | The machine should be tested for continuous running of 48 hrs. If any break down occurs during this test, the test should be repeated for 48 hrs from that time. | Confirm
13.2.4 | Prove out of the system / equipment with BHEL components. | Confirm
13.2.5 | Training of BHEL personnel in operation of complete equipment & accessories etc by the supplier's experts / engineers during their stay at BHEL works | Confirm
14 | PACKING:
14.1 | Sea worthy & rigid packing for all items of complete equipment, all accessories and other supplied items to avoid any damage/loss in transit. | Confirm
15 | GUARANTEE :
15.1 | 24 months from the date of acceptance of the equipment. | Confirm
16 | GENERAL :
16.1 | System / Equipment Model | Specify
16.2 | Total connected load (KVA): | Specify
16.3 | Floor area required (Length, Width, Height) for complete machine & accessories | Specify
16.4 | Total weight of the equipment | Specify
16.5 | Weight of heaviest part of equipment | Specify
16.6 | Weight of the heaviest assembly and Sub-assembly of the equipment | Specify
16.7 | Dimensions of largest part of the equipment | Specify
17 | REFERENCE LIST / QUALIFYING CONDITIONS :
| Only those vendors, who have manufactured, supplied and commissioned atleast two numbers of the quoted model of data acquistion system of same or higher capacity (Processor, Embedded software, Operating system, Ethernet Communication etc.) for similar applications in the past ten years and such equipment is working satisfactorily for more than one year of operation with out any problem after commissioning should quote. However, if such equipment(s) has/had been supplied to BHEL, then such equipment should be presently working satisfactory for more than six months after its commissioning and acceptance in BHEL, should quote. The following information should be submitted by the vendor about the companies where similar equipments have been supplied. This is required from all the vendors for qualification of their offer. | Confirm
| 1. Name of the customer / company where similar equipment is installed. | Specify
| 2. Complete postal address of the customer. | Specify
| 3. Month & Year of commissioning. | Specify
| 4. Broad Specifications of the equipment. | Specify
| 5. Application for which the machine is supplied with details of accuracies achieved on the job. | Specify
| 6. Name and designation of the contact person of the customer. | Specify
| 7. Phone, FAX no. and email address of the contact person of the customer. | Specify
| 8. Performance certificate from the customers regarding satisfactory performance of machine supplied to them | Confirm
| 9. BHEL reserves the right to verify the information provided by vendor. In case the information provided by vendor is found to be false/incorrect, the offer shall be rejected. | Confirm
18 | Delivery | 12 Months
N.T. Mahender K. Bhaskara Rao
Sr. Manager / Testing (51 Shop) DGM / Testing (51 Shop)