BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

BHARAT HEAVY ELECTRICALS LIMITED – HARDWAR

Electrical Machines Test-bed

SPECIFICATION

for

AUXILARY COOLING WATER SYSTEM

FOR 800 / 1000 MW TG

CONTENTS

| SLNO | DESCRIPTION |
| --- | --- |
| 01 | INTRODUCTION |
| 02 | SCOPE OF WORK |
| 03 | SCOPE OF SUPPLIES & SERVICES |
| 04 | TECHNICAL SPECIFICATION |
| 05 | DRAWINGS/DATA SHEET/ DOCUMENTS |
| 06 | GUARANTTEE |
| 07 | PROJECT SCHEDULE |
| 08 | GENERAL TERMS & CONDITIONS |
| 09 | REFERENCE DRAWINGS / SKETCHES |

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### 1.0	INTRODUCTION

Turbo-generators and Motors are tested in fully assembled condition at Test-bed, Block-1 as per IEC and IS Standards.  The existing Oil & Water Pump-house is capable of meeting the requirement of cooling water to test Turbo-generator upto 500 MW only.

Maximum capacity of existing water services 1800 cu m/hr. Stand-by Pump capacity is 900 cu m/hr.  Cooling tower is rated for uninterrupted cooling of warm water by 7ºC at consumption of 1800 cu m/hr.  Inlet temperature of cold water is maintained below 36ºC in the summer.  Pump section consists of 6 Nos. Pumps, each rated for 900 cu m/hr,                  Head 32 MWC Speed 1450 RPM. Three pumps (two active + one standby) are used for cold water pumping.

1.1	PURPOSE

A new Cooling Water Service System has been envisaged to test Turbo-generator up to 800 MW / 1000 MW.  It is proposed to provide Vertical Turbine Pumps for pumping cold water from cold water sump up to the various cooler inlets and return water from the coolers to the cooling tower along with necessary control & Instrumentation, Measurement & protection and Mimic panels to test 800/1000 MW Turbo-generator.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### 2.0	SCOPE OF WORK

  - General

The scope of work under this Bid Enquiry would include setting up of new cooling water service system on Turnkey basis as per battery limits shown in the Drawings/and detailed in the Specifications herewith.

  - Engineering Services

The scope of engineering services shall include, but not limited to the following:

- Detailed engineering for all Civil, Structural, Hydro-Mech and Electrical works for cooling water service system with pumps, piping, valves, controls & accessories.

- Calculations for Total Head requirement.

- Calculations for Cold Water sump capacity/sizing.

- Calculation of cooling tower sizing

- Architectural & Structural designs and layout for construction of Pump house, Cold Water Sump, Electrical Sub Station Building and associated Structures/Units.

- Detailed Engineering for Electrical works Single Line diagrams and Layout arrangement for all Electrical equipments, lighting etc.

- Erection & Commissioning of the Plant and proving of the system by Trial Runs.

- Training of Purchasers’ (BHEL, HEEP) personnel at site during commissioning of the Plant.

i)   Any other item as per requirement on the basis of Turnkey project

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### 2.3	Plant & Equipment

The equipment to be provided is detailed in the Clause 3 in the following sheets.

Along with above, all the Hydro-Mech-Elect equipments required for the Job shall be provided.  Any item not specifically written in the specifications but required for completing the works shall be deemed to be included in the scope of supply by the Contractor.

2.4	Civil & Structural Works

a) Complete civil work including design and construction required for completion of the project such as Construction of Cold Water Sump, Pump house, Electrical Sub Station building, Cooling Towers, Trenches, Supports and other associated structures as required for the Cooling Water Service System.

b) All civil work shall be carried out as per latest technical 	specifications.

2.5        Scope of Civil Work

Engineering, civil work including building construction, awarding & execution of works contract for civil work and E&C of equipment (This shall include procurement of misc. items required for civil work) for following:

- Cooling Tower

- Cold well sump

- Pump house building to accommodate water-pump sets, valves, pipings, local control & instrumentation panels for all the Electricals with proper ventilation and illumination

- Foundation for motor and pump sets, pipe supports, main header valve chamber etc.

- Electrical building to accommodate 11 KV/415 volts, Transformer and 415 volts MCC panel which will include the Incomer, outgoing feeders for pump-motor, cooling tower motor, Valve-motors, control supply etc.

- Required cable trenches for laying of cable within /outside the buildings shall be included in the civil work.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

- Any other item as per requirement on the basis of Turnkey project

  - Scope of Electrical  Work

- Engineering, procurement, awarding & execution of  works contract, E&C of equipment ( This shall include procurement of misc. items required for erection & commissioning ) , supervision of erection & commissioning and proving of All Electricals which includes 11 KV/415 volts Transformer and 415 volts MCC panel i.e. Incomer, outgoing feeders for pump-motor, cooling tower  motor, Valve-motors , control supply etc

- Preparation of cable schedule and its layout scheme

- Fan & Lighting work of buildings

- Any other item as per requirement on the basis of Turn-key project

2.7	Scope of Motor- Pump sets, Piping Work & their accessories

- Engineering, procurement, awarding & execution of works contract, E&C (This shall include procurement of misc. items required for erection & commissioning), supervision of erection & commissioning and proving of motor-pump-sets, piping work & all the accessories as per drawings.

- Layout  drawings for motor- pump sets

- Layout drawings for piping to connect cooling tower, cold well sump, pump-house building, and 800/1000 MW test bed.

- Layout for all the accessories like valves, supports etc

- Any other item as per requirement on the basis of Turnkey project

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

2.8	Scope of Erection, Commissioning & Proving

- Competent staff to be deputed full time during execution of the Project staring from beginning of the project till its proving.

- Awarding & execution of the works contract (This shall include procurement of misc. items required for erection & commissioning).

- Supervision of Erection & commissioning of all equipments supplied by supplier.

- To train the purchaser's (BHEL, HEEP) personnel at site during commissioning of the equipment.

- First trial testing shall be performed during testing of 800/1000 MW TG.

- Any other item as per requirement on the basis of Turnkey project

2.9	Reference Drawings

(i)  ACW System	 		1-139-01012

(Only Part-I covering cooling tower & pump House)

(ii) Proposed location of New Pump House and piping routing upto 	  	     basement for Auxiliaries TGE-2466

(iii) MCC Single Line Diagram for Pumps& Electrics for 800 MW Test 	      Bed in Block-1   TGE-2467

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### SCOPE OF SUPPLY & SERVICES

| SL.NO. | EQUIPMENT | QUANTITY |
| --- | --- | --- |
| 1 | Vertical Turbine Pumps with Accessories Capacity 1000 m3 /hr at 50 MWC ( Refer clause 2.2 b)as per Technical Specifications | 4 Sets |
| 2 | Vertical Solid Shaft Squirrel Cage Induction Motors 200 KW 1500 rpm (Syn.) for above Pumps as per Technical Specifications | 4 Nos. |
| 3 | 450 mm dia Cast Iron Double Flanged Butterfly Valves PN 1.0 for Pump delivery line with Electrical Actuator as per Technical Specifications | 4 Nos. |
| 3a | 450 mm dia Cast Iron Double Flanged Butterfly Valves PN 1.0 for Pump delivery line Manually operated as per Technical Specifications | 1 No. |
| 4 | 450 mm dia Cast Iron Double Flanged Non Return Valves PN 1.0 for Pump delivery line as per Technical Specifications | 4 Nos. |
| 5 | 600 mm dia Cast Iron Double Flanged Butterfly Valves PN 1.0 with Electrical Actuator for Pipeline System as per Technical Specifications | 7 Nos. |
| 6 | 200 mm dia Cast Iron Sluice Valves PN 1.0 for Cooling Towers with Hand-wheel (2 Valves per CT cell) as per Technical Specifications | 12 Nos. |
| 7 | Self Cleaning Strainers capacity 2000 cu.m/hr | 2 Nos. |
| 8 | FRP Induced Draft Cooling Tower with 6 Cells as per Technical Specifications. | 1 Set |
| 9 9.1 9.2 9.3 9.4 9.5 | Instrumentation: Flow meter Electromagnetic On-line type suitable for flow rate of 2000 m3/hr as per Technical Specifications Capacitance/Ultrasonic type Level Measurement System for Cold Water Sump with High/Low alarms Pressure gauges/Pressure Transmitters (Pressure gauges at each Pump delivery and PG&PT at Common outlet) One Pressure gauge & PT on the Common Return Line Electronic Tempt. measurement system for Cold Water Sump with High/Low Alarms Signal & Control Cables with accessories from field instruments to control panel including Cable Trays and conduits as required | 1 No. 1 Set 1 Set 1 Set 1 Lot |
| 10 | Control Panel for Remote Control/Operation with Indications including for Level, Flow, Tempt, Pressure complete with accessories | 1 Set |
| 11 | EOT Crane 5.0 T capacity with gantry rails and accessories/controls as per Technical Specifications | 1 Set |
| 12 | 1.5T Air Conditioner in Control Room with Wiring/ Controls | 1 Set |
| 13 | 450 mm dia. Exhaust Fans with Accessories 900 RPM | 6 Nos. |
| 14 | Portable Dewatering Pump set Submersible type capacity 10 m3/hr each Total Head 15 mts with flexible pipe and submersible cable | 4 Sets |
| 15 | 11 KV/415V 1000 KVA ONAN Dyn.11 Indoor Dry type Transformers as per Technical Specifications | 1 No. |
| 16 | Power cum Motor Control Centre (Main LV Switchboard) comprising of Incomer feeders Bus coupler & Outgoing feeders with protections relays, metering & indications as per Technical Specifications and Single Line Diagram | 1 Set |
| 17 | Sub Distribution Board comprising of Incomer & Outgoing Feeders with metering & indications for Lighting & Small power requirements as per Technical Specifications and Single Line Diagram | 1 Set |
| 18 | Capacitor Bank with APFC Panel for improvement of System Power factor to 0.98 with protections, metering & indications | 1 Set |
| 19 | 11 KV grade 3C x 70 sq. mm Aluminium Conductor XLPE insulated Armoured Cables | 1200 mts |
| 20 | 1.1 KV grade 6 (3½C x 300 sq.mm) Aluminium Conductor PVC insulated Armoured Cables | 1500 m |
| 21 | Bus duct with Copper Bus bars for Inter-connections between LV of 1000 KVA Transformer & Incomer from LT Power Distribution | 1 Lot |
| 22 22.1 22.2 22.3 22.4 | 1.1 KV Grade PVC insulated armoured Cables for: Inter-connection between Main Pump Motors & PMCC size 3C x 150 Sq. mm (Copper Conductor) Inter-connection between PMCC & Cooling Tower Motors Size 3C x 10 Sq. mm (Copper Conductor) Inter-connection between PMCC & APFC Panel Size 3C x 300 Sq. mm ( 2 runs) (Aluminium Conductor) Inter-connections between PMCC & Sub Distribution Board (SDB) 3C x 240 Sq. mm (Aluminium Conductor) | 1 Lot 1 Lot 1 Lot 1 Lot |
| 23 23.1 23.2 23.3 23.4 23.5 | 1.1 KV Grade Copper Conductor PVC Insulated Cables for: Inter-Connections Between SDB & Valve Actuator Motors Size 3 C x 4 Sq. Mm Inter-Connections Between SDB & Exhaust Fans Size 3C x 4 Sq. Mm Inter-Connections Between SDB & EOT Size 4C x 6 Sq. mm Inter-Connections Between SDB & Battery Charger Size 4C x 6 Sq. mm Inter-connections between SDB & Lighting DB Size 4C x 6 Sq. mm | 1 Lot 1 Lot 1 Lot 1 Lot 1 Lot |
| 24 | 1.1 KV Grade Copper Conductor PVC Insulated armoured Control Cables | 1 Lot |
| 25 | 100 AH 24V DC Lead Acid Batteries including Battery Stand, Couplers/Connectors and accessories as per Technical Specifications | 1 Set |
| 26 | Battery Charger for 100 AH 24V DC Batteries including metering & indication as per Technical Specifications | 1 Set |
| 27 | Industrial Luminaries in CRCA Sheet Steel Housing with Reflector for 2 x 36W and 1 x 36 W FL for the entire Building complete with accessories Control-gear, Conduits, Wiring and Switches with Spare plugs | 1 Lot |
| 28 | GI Earth Strips & earth pits ( 02 for Transformer neutral and 02 for Equipment body) for earthing of all Electricals as per IE Rules | 1 Lot |
| 29 | Safety equipment comprising First Aid Box, Shock Treatment Chart, Rubber Mats etc. | 1 Lot |
| 30 | 900 cu meter/hour, 32 MWC Motor-Pump set for existing system to be quoted as an optional | 2 Nos. |
| 31 | Spare-parts for 2 years normal maintenance (List to be furnished) | 1 Lot |

The Scope of Supply/Works for Cabling would include necessary Termination Kits for 11 KV Cables; Lugs, Glands & other accessories for LV Cables.

For underground/buried cables; sand & bricks shall be provided for protection.

For Cables to be carried in the Trenches ladder type Cable Trays and supports shall be provided.

The trenches shall be provided with chequered plate covers.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### 4.0	TECHNICAL SPECIFICATIONS:

  - SITE CONDITIONS

    - Environmental Conditions

    - Maximum Ambient temperature:	 45-50 deg C

    - Reference temperature for	  :	 50 deg C

Electricals design

    - Altitude				  :	< 300 mts above Mean Sea Level

    - Max Temperature of outlet  water from test bed :42-460 C (assumed)

    - Temperature of inlet water to the test bed: less than 10 0C from the test      						        bed outlet temperature.

    - Cooling Tower to be designed with dry bulb and wet bulb temperature of Haridwar in consideration

    - Contactor shall take care of environmental regulation as per guidelines by State Pollution Control Board and Central Pollution Control Board.

    - Contractor shall take care of safety requirements also

    - Water quality at inlet to the system:

BODs	at 27ºC		:	1 mg/L

COD	at 27ºC		:	4 mg/L

Total suspended solids	:	17 mg/L

    - Power Supply

Supply System			:	11000 Volts 3 Phase 50  C/s AC

Voltage Variation			:	(±) 10%

Frequency Variation			:	(±) 5%

Combined Voltage & Frequency	:	(±) 10%

Variation

4.1.4	Site location & space requirement for new cooling water service plant

Contactor shall examine & decide in consultation with BHEL the exact location of site for its optimum use in testing of 800/1000 MW TG as per

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

space requirements for new cooling water service plant keeping in view of the following:

    - The water head & flow requirements are met for testing of 1000 MW TG at new location situated approximately at 150 meters away from New Pump House.

    - Conformance with National And International Standards

    - Supplier shall take care of loading requirements of civil structures equipments etc and submit the layout drawing.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### TECHNICAL DETAILS/SPECIFICATIONS

4.2.1	PUMPS

| Make | Mather & Platt/equivalent |
| --- | --- |
| Quantity | 4 Nos. (2W + 2 SB) |
| Type | Vertical Turbine |
| Total Bowl Assembly Head | 50 MWC ( refer clause 2.2 b) |
| Rated Output | 1000 cu.m / Hr. (each pump) |
| Liquid handled | Cold clear Water |
| Bowl Efficiency | 88% |
| Power absorbed | 154.73 KW plus transmission losses |
| Recommended drive | 200 KW |
| Column length | To suit Cold Water Sump depth |
| Lubrication | Self Water |
| Speed (Nom.) | 1480 RPM |
| Material Construction |  |
| Bowl | C I FG 260 |
| Impeller | SS CF 8 M |
| Pump Sleeve | SS CF 8 M |
| Pump/Head/line shaft | SS AISI 410 |
| Line Shaft bearing | THORDON |
| Discharge Head | CI FG 260 |
| Column pipes | MS fabricated |
| Motor Stool | MS fabricated |
| Packing | Graphite Asbestos |
| Shaft Sealing | Gland packing |

4.2.2	MOTORS

| Make | Crompton/ABB/Kirloskar/Alstom |
| --- | --- |
| Type | Squirrel Cage Induction Solid Shaft |
| Type of Mounting | Vertical Flange mounted |
| Motor Output | 200 KW |
| Quantity | 4 Nos. |
| Supply Voltage | 415V (±) 10% |
| Supply Frequency | 50 Hz (±) 5% |
| Combined Voltage & Frequency Variation | (±) 10% |
| Duty | Continuous S1 |
| Type of Enclosure | TEFC |
| Degree of Protection | IP-55 |
| Syn. Speed | 1500 RPM |
| Full load Current (Nom.) | 325 A |
| Insulation Class/Temp. rise allowed | Class F/Class B with reference Tempt as 50ºC |

    - VALVES

| Cold well Pump | Delivery line Butterfly Valve | 450 mm, PN-1.0 rated, C I Body & disc with SS trims, Motor operated as per BS:5155/IS:13095 |
| --- | --- | --- |
| Cold well Pump | Non return valve single door swing check type on pump delivery line | 450 mm, PN-1.0 rated, C I Body & disc with SS trims, Motor operated as per IS:5312 Part-1 |
| Valve Chambers | Butterfly valves | 600 mm PN-1.0 rated, C I Body & disc with SS trims, Motor operated as per BS:5155/IS:13095 |
| Cooling tower inlet to cells | Gate valve/Sluice valve | 200 mm PN-1.0 rated, C I Body & disc with SS trims, Manually operated as per IS:14846 |

    - COOLING TOWERS

| Type of Cooling Tower | Induced Draft |
| --- | --- |
| Overall Dimensions (L*W*W) mm | 4000*12000*4550 2 Nos. |
| Height of Air Inlet mm | 800 |
| Material of Louvers | FRP |
| Material of Tower Structure | RIGID PVC |
| Type | Honey Comb |
| Colour | Transparent Blue/Black |
| Cooling Tower No. of Cells | 6 |
| Auxiliary Equipments |  |
| 1. Fan type | Axial Flow |
| No. of Fan | 6 |
| Dia of Fan | 2440 |
| Fan RPM | 470 |
| No. of Blades/Fan | 6 |
| Material of Blades | FRP |
| Material of Hud | Cast Aluminium |
| Fan Shaft | SS 304 |
| Type of Balancing | Dynamic |
| 2. Motor |  |
| No of Motor | 6 |
| Motor HP | 15 |
| Seed (Nom.) | 1440 RPM |
| Drive | Reduction Gear Box |
| Make (Motor) | Hindustan or other reputed |
| Make (Gear Box) | MM Gears/Deekay or other reputed |
| 3. Distribution Piping |  |
| Type | Fixed Nozzle |
| Material | PVC, Non-clog |
| 4. Design Performance |  |
| Spray Loss Max. % | 0.1 |
| Evaporation Loss Max. % | 0.59 |
| 5. Inlet Pipe | “10” NB |
| Outlet Pipe | “10” NB |
| 6. Hardware |  |
| Material of Bolt, Nut and Washer | SS |
| Weight of Tower without Water-KG | 2000/Tower) |
| Weight of Tower with Water-KG | 3600/Tower) App. Reference Values |
| 7. Contact Surface Area | 30000/Tower) |

    - TRANSFORMER

    - One No. 1000 KVA 11 KV/415V 3 Phase 50 Hz Dry type Power Transformer shall be provided.

    - Indoor installation for Connections with 11 KV XLPE Cables on        HV and Bus ducting for LV

    - Impedance 5%

    - ONAN Cooling

    - Vector Group Dyn.11

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

    - LV Neutral solidly earthed

    - Design Ambient Temp 50ºC

    - Double Wound with Copper windings

    - Windings Temp Rise measured by resistance method 45ºC

    - Full capacity Off-load type Tap Changer on HV Side for Dry type Tr. with Pad locking facility for (+) 5% to (-) 10% range; Tap Set 2½%

    - Rated Voltage HV 12 KV (HV Side) and 1100V (LV Side).  Nominal system voltage 11 KV (HV) & 415V (LV)

    - One Minute Power Frequency withstand voltage (day & wet)                          28 KV (HV) & 3 KV (LV) rms values

    - 1.2/50 micro second full wave impulse withstand voltage 75 KV (Peak)

    - Minimum creepage distance 372 mm (HV) and 34 mm (LV)

    - Governing Standards IS:2026, IEC 60076, 60214 and 60296

    - Accessories – all standard accessories like WTI and Tripping

For door opening

- Wheels – Bidirectional, plain

    - 415V POWER CUM MOTOR CONTROL CENTRE

    - 415V PMCC Panels shall be of single front, non-draw out, freestanding, floor mounting type.  This shall be compartmentalized design and made of CRCS sheets.

    - Totally enclosed, dust & vermin proof enclosure with IP-52 degree of protection.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

    - It shall have copper bus bars.

    - The Sheet Steel thickness shall be min. 2.0 mm for front/base/side and 3.16 mm for load bearing pads.

    - This Panel shall have two 415V, 1600A, 50 KA (1 sec) TPN bus sections coupled by a 415V, 1600A, 50 KA (1 sec) bus coupler, with Manual transfer interlock.

    - The Incomer shall have 1600 Amp ACB (motorized and fully withdraw able) and have Voltmeter, Ammeter with CTs, Selector Switches and Indicating lamps etc.

    - The Outgoing Pump Motor Feeders shall be provided with 415V,    630A MCCB Star/Delta Motor Starter modules with necessary protection and indications.

    - The Outgoing Cooling Tower Motor Feeders shall be provided with 415V, 63A SFU’s & Star/Delta Starter shall have necessary protection and Indication.

    - Suitable terminals for terminating 1600 Amp, 3 Phase, 4 W supply shall be provided in the MCC.

    - BATTERIES & BATTERY CHARGER

    - 24V/100 AH Battery Lead Acid type, low maintenance type.

    - Positive plates either of Plant or Tubular type.

    - Negative plates box type

    - Containers transparent made of toughened glass or plastic provided with Acid Level Indicator.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

    - Rated on 2 Hour basis; maximum recharge time of 8 hours.

    - Shall conform to IEC Standards

    - Electrolyte Sulphuric Acid

    - Battery Racks shall be provided

    - Porcelain insulators, Rubber pads & Set of inter-cell, inter tier and inter-bank connectors provided as required for complete installation.

    - Accessories for testing & maintenance:

- DC Voltmeter					:	 (One)

- Hydrometer					:	 (One)

- Filler hole thermometer with Plug & Cap	:	 (One)

- Pocket Thermometers				:	(Three)

- Acid Resisting Funnels				:	(Three)

- Acid Resisting Jugs of adequate capacity	:	(Two)

- Rubber Aprons					:	(Two)

- Rubber Gloves					:	(Four)

- Cell Lifting Straps

    - Float cum Boost type Battery Charger shall be provided comprising of Silicon controlled Rectifiers connected in a full wave bridge circuit with ripple control devices and transient suppression network.  The Rectifier shall consist of two branches, one for Supplying the battery and other for Feeding external loads.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

    - The 415V AC Input to Battery Charger shall be through suitably rated MCCB.  On output side, a 2 pole MCCB of suitable rating shall be provided.

    - Battery Charger shall be suitable for float charging.  The battery under normal conditions and boost charging the battery when it has discharged during service conditions.  The changeover from float to boost mode and vice-versa shall be automatic.

    - Battery charger shall be designed for Voltage regulation of 1% and ripple content in the rectified DC supply of less than 2%.  Boost charging time not to exceed 8 Hours.  DC Output voltage during float charging stabilized within ± 1%.  Voltage regulation by constant voltage regulator having fast response SCR Control.  Ripple Content within 1% of DC Output nominal voltage with battery disconnected.

    - Battery Charger equipment complete with all accessories housed in a free standing Sheet Steel cubicle.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

    - INSTRUMENTATION:

- Level Measurement:

Consisting of level transducer, level transmitter digital level indicator to indicate the water level in the Cold Water Sump.

  - Overall Accuracy of System ± 0.5% of full scale

  - Type Ultrasonic/Capacitance

  - Level Transmitter Microprocessor based with backlet/LCD display with 4-20 mA output

  - High/Low Level Alarms Contacts shall be provided

- Pressure Measurement:

Besides Pressure gauges on the individual pump delivery branches; electronic type pressure measurement system shall be provided on the common manifold/header of Pumps.

The Pressure transmitter shall have accuracy of ± 0.25% and of capacitive type.  The range shall be 0-60 mwc and output signal 4-20 mA for indication in LCD type.

On each of the Pump delivery-line common manifold & return line,        a pressure gauge of 150 mm dial shall be provided.  Accuracy ± 1% of full scale; Range 0-60 mwc.  Pressure gauge shall be equipped with shatter proof glass.  The Body shall be in Die cast Aluminium; Sensor & other wetted parts in SS; Dial of Aluminium with white background & black writing.

- Flow Measurement:

The Flow meter shall be provided in the Common manifold.                      The Flow meter shall be In-line full bore electromagnetic type.                     The Overall accuracy shall be ± 1%.  Range 0-2000 m3/hr. The materials for Electrode: SS 316, Coil Housing SS 316; Liner Hard Rubber.  Flow Transmitter, microprocessor based with 4-20 mA output, type of display 4 digit of segment backlit LCD/LCD with flow rate in cu.m/hour.  Totaliser shall be provided with 8 digit of segment backlit LED/LCD

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

4.2.10	 CONTROL PANEL:

The Instrument Control Panel shall be provided separately in the Control Room.  Control Panel shall be free standing floor mounting pattern;      made out of Cold Rolled Steel Sheets in minimum 2 mm thickness; incorporating:

- Flow indicator/Integrator

- Level Indicator

- Pressure Indicator

- Tempt Indicator

- Start/Stop Control & Indication of Main Cold Water Pumps

- Start/Stop Control & Indication of Cooling Tower Motors

- Start/Stop Control & Indication of Pump delivery B.F. Valves

- Start/Stop Control & Indication of CT fan motors

- Annunciation Alarm for abnormal conditions for Water Level, Water Pressure & Water Tempt.

4.2.11 CAPACITORS:

Capacitors shall be provided for improvement of Power factor at all working loads to min. 0.98 lagging.  LV Capacitors with APFC Relay and a Panel shall be provided for connection to PMCC bus as shown in SLD.

Capacitors shall comply with IEC 60871, IS 13585, IS 13925.  The rating of the Capacitors shall be suitable to achieve the above referred improvement.  Estimated Rating 300 KVAr.  However the rating as per actual requirement depending upon uncorrected PF of Motors to be provided.

- Type of Insulation		:	APP/MD

    - Rated Voltage			:	415V

    - Supply System			:	50 Hz 3 Ph AC

    - Capacitor Bank Connection	:	Delta

    - Mounting & Location		:	Floor mounted Indoor

    - Design/Reference Tempt	:	50ºC

    - Arrangement			:        Automatic power factor connection

    - Type of Switching		:	Automatic

    - Degree of Protection of Enclosure:	IP-52

    - Type of APFC Relay		:	Microprocessor based automatic 							Power factor corrections

relay (max setting 0.99)

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

APFC Relay shall automatically Switch ON/OFF the Capacitor banks to attain value of PF close to the set value.  A minimum power factor of 0.98 at any and all time shall be maintained.  Switching shall follow first in first out method to ensure uniform use of all Capacitor Banks.

The cubicle shall be fabricated out of 2 mm thick cold rolled sheets.  The Panel shall consist of the following:

- Isolating MCCB

- Contactors with overload element

- Relays responsive to current/voltage/KVAR/PF for automatic Switching

- Sequencing devices, timers & auxiliary relays for automatic Sequential  Switching of Capacitor units/banks

- Auto/Manual Selector Switch

- APFC Relay

- Indicating lamps

4.2.12 EOT CRANE:

    - Capacity		:	5 MT (SWL)

    - Class		:	II/IS:3177

    - Lift		:	6 mts

    - Span		:	5.5 mts

    - Bay Length	:	15 mts

    - Electrically operated bridge type with down shop conductor, rails and other accessories.

    - Pendant type push button station sheet steel enclosed consisting of Push Buttons & Indicating Lamps for Start/Stop, Long Travel (Right/Left), Cross Travel (To/Fro) Hook (Hoist/Lower) and Supply ‘ON’ indication.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

    - Pendant controls shall be supported independently of electrical cable and shall be earthed separately.  Automatic reset type Limit Switches shall be provided to prevent Over travel for –

- UP/DOWN motions of Hook

- Long Travel motion

- Cross Travel motion

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

    - 900 cu meter/hour Motor –Pump Set

Split casing, single stage, horizontal shaft, centrifugal pump suitable 	for Circulation of clear water in Electrical machines for cooling 	purpose.

PUMP

- Discharge rate - 900 m3/hr

- Total head - 32 mts.

- Suction x Delivery-300x250 mm

- Efficiency- 87%

- Temp. – 75 0 C

- RPM - 1450

- BKW – 90.15 KW

- Motor – 150hp/110Kw

- DOR – CW from DE, suction on right and delivery on left side*

- Compliance with standard safety norms.

* Direction of rotation of Pump and Suction/Delivery as viewed from DE

Material of Construction

1.  Casing-CI IS 210 GR FG 200

2.  Impeller	- Bronze IS 318

3.  Shaft- C-40 IS 157

4.   Shaft Sleeve- CI IS 210 GR FG 200

5.   Casing Wear ring- Bronze IS 318

6.   Stuffing Box Bush- CI IS 210 GR 200

MOTOR

1.  Make- Alstom/ Crompton

2.  Specification – 110 KW TEFC, Squirrel Cage Induction Motor

3.  Supply- 	3 phase, 415 volts, 50 Hz

4.  Insulation- Class F

5.  Enclosure- Conforming to protection IP-55

6.  Operating altitude- upto 1000mts.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### ENGINEERING CONSIDERATIONS

    - Cooling Tower for uninterrupted cooling of warm water by 10ºC at consumption rate of 2000 m3/hr maintaining cold water temperature below 36ºC when ambient is in the range of 45-50ºC.

    - Max. Pressure drop in TG Coolers will be approx 8 MWC (Meter Water Column).  Location of inlet to the Hydrogen cooler top is 6 meter from ground level.

  - PIPE WORK

- Piping upto & including 150 NB shall be carbon steel (ERW IS:1239)

- Piping 200 NB and above shall be carbon steel (IS:2062) rolled and welded conforming to IS:3589.

- All pressure tappings and root valves shall be NB 15

- All Pipelines to be supplied shall be of minimum working pressure 10 kg/cm2, test pressure 15 kg/cm2.  Test certificate for pressure test to be furnished.

- Thickness of the Pipelines shall be as per table below:

| NB | OD | Thickness | NB |  | OD | Thickness |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | 21.8 | 3.2 | 150 |  | 166.5 | 5.4 |  |
| 25 | 34.2 | 4.0 | 200 |  | 219.1 | 6.0 |  |
| 40 | 48.8 | 4.0 | 250 |  | 273.0 | 6.0 |  |
| 50 | 60.8 | 4.5 | 300 |  | 323.9 | 6.0 |  |
| 65 | 76.6 | 4.5 | 350 |  | 355.6 | 6.0 |  |
| 80 | 89.5 | 4.8 | 400 |  | 406.4 | 6.0 |  |
| 100 | 115.0 | 5.4 | 450 |  | 457.0 | 6.0 |  |
| 125 | 140.8 | 5.4 |  |  |  |  |  |
|  |  |  | 500 | 508 |  |  | 7.0 |
|  |  |  | 600 | 610.0 |  |  | 7.0 |

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

- Buried piping shall be protected as per IS:10221

- Surface cleaning by wire brush

- Apply one coat of Coal tar/Primer/Enamel confirming to AWWA C-203/ IS 10221

- Apply one layer of Tape comprising Coal tar. Application of Tape shall conform to AWWA C-203/IS 10221 (Appendix – B) with minimum thickness of tape as 4 mm ± 10%.

- External surface of the over ground piping shall be protected by

- Surface cleaning by wire brush

- Application of one coat of Red lead primer followed by adequate no of finish coats of synthetic enamel to achieve total dry film thickness of 125 microns

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### DRAWINGS/DATA SHEETS/DOCUMENTS

Following Engineering data and documents shall be prepared by Contractor for the Cooling Water System of Test-bed, Block-I to complete the entire project, which includes Engineering, Civil work, Supply, Erection, Installation & Commissioning and providing on full load condition of Cooling Water System on Turnkey basis.

5.1	Detailed Civil Structure drawing/layout drawing and certified dimensioned drawing with civil assignment for

    - Cooling Tower

    - Cold Well Sump

    - Pump House

    - Electrical Building for 11 KV/433 Volts Transformer, MCC Panel etc

5.2	Detailed Layout drawing and certified dimensioned drawing with civil assignment for

    - Water Pump sets

    - Valves

    - Piping Scheme etc

5.3	Detailed Single-line diagram of Cooling Water System with Specification of major components

5.4	Layout/Schematic/Control drawing of Electricals as per following:

    - Single-line diagram of Mains Supply 11 KV Transformer

    - Single line diagram of MCC Panel (Power Scheme)

    - Annunciation& Protection Panel

    - Control Schemes of Motor Pump set, Fan Motor and Valves Motor etc

    - Cable Schedule for all above

    - Layout drawing of all Electrical of MCC Panel including Incomer transformer 11 KV/415 Volts

    - Layout diagram for control & instrumentation panel

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

5.5	List of vendors with details addresses (postal addresses, e-mail, fax number & telephone number etc) for approval for all bought out items & spares.

5.6	Operation & Maintenance manual with catalog and test certificates of equipments

5.7	Approved Scheme of cooling water system for 800/1000 MW TG for our approval

5.8	5 Sets of each of above documents shall be furnished by the Contractor

5.9	All catalogues & technical details given by Vendor shall be furnished.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

### GUARANTEE

- Guarantee for healthy functioning of the Cooling Water System for 800/1000 MW TG Project shall be provided for a period of              24 months after commissioning & providing of complete system.     In this period, Supplier to provide all the necessary services (including deputation of Supplier expert) & spares free of cost for any kind of trouble-shooting during operation of the offered system.

- Supplier shall furnish test and guarantee certificates of all bought out items to HEEP, BHEL.

- During guarantee period, as and when there is requirement of Contractors’ experts against any irregularities reported in the system, persons shall reach HEEP Work place within 3 days.  Contractor shall organize for the Vendor’s visit, if needed, during their stay at HEEP.

- Contractor shall pay at least 8 visits for a minimum 1 week period free of cost for their services (including deputation of experts) as and when required during guarantee period.

7.0	PROJECT SCHEDULE

Project completion schedule to be furnished by Contractor along with the offer and shall be got approved by HEEP.  The Project is to be completed by December, 2007.

BHARAT HEAVY ELECTRICALS LIMITED – HARIDWAR

TURNKEY PROJECT ON AUXILIARY COOLING WATER

## SYSTEM FOR 800 / 1000 MW TG

# ________SPECIFICATION NO. : HEEP/TEST-BED/800/CWS,REV.01_____

8.0	GENERAL TERMS & CONDITIONS

  - Before quote, Supplier along with other Tenderer is requested to visit the site, understand the technical requirements in detail, site conditions, space availability and other requirements.  Contractor is required to ensure complete understanding of technical requirements and site conditions.

  - Contractor shall complete the entire job for the cooling water system of Test-bed, Block-I, as per this specification on turnkey basis.

  - Contractor shall obtain approval for scheme for complete cooling water system to test 800/1000 MW TG.

  - Supplier shall obtain final approval for each item before issue of                Purchase order/awarding of works contract by them.

  - Any material/or component not foreseen till the stage (completion & approval of Technical Specifications by BHEL for Cooling Water System 800/1000 MW TG), but which are necessary for the implementation, satisfactory & trouble free operation of the system and its accessories     shall be responsibility of the Contractor to fulfill them as per Project schedule without any extra cost.

  - Contractor shall train Testing staff at site during commissioning of the Project.  Contractor shall arrange training of testing staff at Contractor works for operation & maintenance aspects of water pump, cooling tower and accessories.

  - Contractor shall carry out inspection of all bought out items at manufacturers’ works as well as on receipt at HEEP, HARIDWAR.

  - Contractor shall quote for comprehensive Annual Maintenance Contract (AMC) for complete Auxiliary Cooling Water System for three years.