Technical Bid

SEALED  TENDER BOX IS AVAILABLE IN THE OFFICE OF AGM (TA)

FOR DROPPING TENDERS AFTER FILLING

B H A R A T   H E A V Y   E L E C T R I C A L S   L I M I T E D

RAMACHANDRAPURAM : : HYDERABAD 502 032

Township Administration Department

TELEGRAM : BHARATELEC,  TELEPHONE NO: 23184286 & 23183585

FAX NO: 040 – 23021925

TENDER NOTICE NO: HY/TA/OT-03/2006-2007 DATED: 29.08.2006

Part-B,  Item No. -  3

1.	Name of work				:  	Addition & Alterations to Electrical

points in General hospital, Bore 									wells, NRSP & STDP etc.

2.	Earnest Money Deposit			:   	Rs. 10,000/-

3.	Time of Completion				:   	6  months

4.	Maintenance period				:   	6 Months

5.	Last date of receipt of tenders		:   	23.09.2006

6.	Date & time of opening of tenders	:   	23.09.2006 at 13.15 hrs

(Technical Bids)

7.	Cost of tender document including S.T	:   	250/-

Name, Address & Phone No:

-------------------------------------------------------

-------------------------------------------------------

-------------------------------------------------------

-------------------------------------------------------

‘Signature of Tenderer’

TECHNICAL CUM COMMERCAL BID (TOBE FILLED IN BY TENDERERS)

1.	Name of the Contractor / Firm		:

2.	Address & Phone No			:

3.	Name of work				:

4.	Tender Notice No & Date, Item No	:

5.	Details of DD / Cash paid

a.	DD or Cash receipt  amount & No

for EMD					:

b.	DD for cost of tender documents 		:

(tobe enclosed along with this bid

when down loaded) from web

6.	Particulars of experience / credentials

a.	Whether all details as per pre-		:

qualification requirements enclosed

b.	Whether financial turnover details	:

enclosed

7.	P.F.Code No (proof of having Code No 	:

to be enclosed)

8.	ESI Code No (proof of having Code No.	:

to be enclosed)

9.	PAN No with proof  (in case not 		:

available, proof of having applied

with 	acknowledgement from concerned

authorities to be enclosed)

10.	APGST / VAT No with proof (in case 	:

not available proof of having applied with

acknowledgement from concerned

authorities to be enclosed).

11.	Labour licence (Central / State 		:

Government if available or to be furnished

at the time of commencement of work

12.	Latest Phone Nos / Cell No.		:

contd - Note

N O T E:-

1.	The  above  documents  should  be  given  along  with  the  tender as otherwise,

contractor’s bills can not be processed and payments may be held up.

2.	Techno  commercial  bids  will  be  opened  on  the  same  day  of  receipt.  After

scrutiny  incase  the  agency  has  not  fulfilled  all  the  above  conditions   with

documentary  proof,  the   bid  is  liable  to be  rejected  and  their  price bid will

not be opened.

3.	In case of a firm, the tender  shall be in the name of  the firm, and for individual

these  can  be  in  the  name  individual.  In case of sole proprietorship of a firm

he should  submit a notarized affidavit to that effect.  For partnership firms, the

deed of partnership and power of attorney are to be submitted.

4.	Though some  of  above  documents  are available with BHEL for those agencies

who  are presently working with BHEL, they also should submit one copy of the

same.

5.	All the columns shall be filled with proper information.

6.	BHEL  reserves the right to reject or cancel the tender at any stage of the tender

process without assigning any reasons there of.

7.	A  tender  may  be  rejected  while  scrutiny  of  technical  bids  in  case  there is

unsatisfactory past performance in the execution of an earlier contract.

‘Signature of Tenderer’

Tender Notice No: HY/TA/OT-03/2006-2007 Dated: 29.08.2006

PRE QUALIFICATION

I.	The  following  conditions are to be satisfied by the tenderers, with documentary

proof  to be enclosed  with  technical  bid.  In  case the agency fails to do so it is

liable for rejection.

1.	Registration  as  contractor  in  suitable  class or reputed contractor.

2. 	Average Annual financial turnover during the last 3 years, ending 31st March of the previous financial year, should be atleast 30% of the estimated cost.

3.	Experience of having successfully completed similar / civil works during last 7 years ending last day of months previous to the one in which applications are invited should be either of the following.

a.	Three similar / civil works completed works costing not less than the amount equal to 40% of the estimated cost or

b.	Two similar / civil works completed works costing not less than amount equal to 50% of the estimated cost or

c.	One similar / civil works completed work costing not less than the amount equal to 80% of the estimated cost.

NB :	Similar Work is defined as experience in relevant civil/electrical works as the case may be for the respective items.

- ESI code no. with proof of allotment

- P.F.Code no. with proof of allotment.

- APGST no. / VAT no. with proof of allotment or may be submitted before

commencement of work.

- PAN number with proof.

- Proof of Labour Licences to be submitted or to be submitted before commencement

of   work.

II.(1)	Tenders  must  be  submitted  in  sealed  covers  addressed  to  AGM/TA BHEL,

Ramachandrapuram,   Hyderabad  502 032.     Tenderer   shall   write   tender

Notice  No,  and  name  of  work  and  address  of  the tenderer  on each  sealed

cover.   In  case  the   agency fails to comply any of the above, the tender will be

liable for rejection.

(2)	The agency is responsible for  all  the statutory requirements & documentations

for  ESI  /  PF /  Labour  Licences  etc  as  per  prevailing  Government  Rules /

Labour Rules.  Any amount payable by BHEL on account of these  requirements

shall be recovered from contractors bills / deposits.

III.	NOTES:-

1.	Period of contract  shall be as mentioned above.

2.	Tenders are on two – part bid method (techno commercial bid and price bid).

3.	Tender  documents  can be had through  BHEL web-site http://www.bhel.com.

Cost of document  shall  be  paid  in  the  shape  of  Demand  Draft or Bankers.

Cheque or Pay Order and separately enclosed to the technical bid.

Contd..

4.	The  requisitions  for  tender  documents  shall  be  addressed  to  Addl.General

Manager/TA,  Ramachandrapuram,  Hyderabad  502 032  along  with  Demand

Draft / Banker’s  Cheque  drawn  in favour  of “BHARAT HEAVY ELECTRICALS

LIMITED,  HYDERABAD’  or  payment  of  cash  in  BHEL  Cash Office (No other

Mode  of  payment  will  be  accepted).   Tender  documents shall be collected in

Person by the contractor or his  authorized representative.

5.	The  agencies  are  advised  to  visit  the  work  site  to understand the nature of

work  / quantum  or  work  in  its  true   perspective  to  avoid  any  mis - under

standing.

6.	 The tender documents may also be submitted through speed post  by post to reach within the stipulated date and time.

7.	Tender bid with out EMD  as stipulated are liable for rejection.

8	BHEL reserves the right to reject any or all tenders in part or in full without assigning any reasons.

9.	BHEL reserves the right to split the work into convenient parts and award them to different contractors.

10.	The conclusion of contract will be in the form prescribed by BHEL for the purpose.  A copy of the general conditions of contract applicable to the above works is available for perusal at the office of the AGM/TA If a copy of the same is required for record, the  same will be issued separately at Rs.25/- per set.

11.	A penalty of 0.5% of the gross  value of work will be levied for every weeks delay in work subject to a maximum penalty of 10% of the gross value of work.

12.	Those who are down-loading the tender documents from web-site must also pay cost of tender documents before last date of receipt.  The DD’s against Tender Cost / EMD are to be enclosed in technical bid cover.

13.      Separate Covers (ie)

Cover-A		-	for Technical Bid (sealed cover)

Cover-B		-	for Price Bid (sealed cover)

Cover-C		-	common cover for technical and price bid are

to be submitted, super scribing the name of work and NIT number on each over.

14.	The tenderers must sign on all the pages of tender documents including the detailed NIT, which forms 	part of tender.

15.	A tender may be rejected while scrutiny of technical bids in case there is unsatisfactory past performance in the execution of an earlier contract.

16.	In case more than one contractor quoted equal L-1 rates, further sealed quotations will be obtained only equal L1 parties  to decide L1 rate.  Under no circumstances revised rate should not be more than the original quoted rate.

‘Signature of Tendere’

BHARAT HEAVY ELECTRICALS LIMITED

Heavy Power Equipment Plant, Ramachandrapuram, Hyderabad 502 032

Grams  :  ‘BHARATELEC’ Phone : 23184286, 23183585.

TOWNSHIP ADMINISTRATION DEPARTMENT

TENDER NOTICE NO. HY/TA/OT-03/2006-2007 DATED: 29.08.2006.

Sealed tenders in two separate covers one  technical bid another  price bid are invited by the AGM/TA from contractors, experienced in similar works, registered or reputed contractors with Government of India, Public Sector, Government of Andhra Pradesh, Railways, Military Engineering Services or Bharat Heavy Electricals Limited, Ramachandrapuram, Hyderabad 502 032 for the following works so as to reach the office of Addl.General Manager/TA, Township Administration Department, Bharat Heavy Electricals Limited, Ramachandrapuram, Hyderabad 502 032 upto 13.00 hours on the dates specified.  The technical bids of tenders will be opened on the same day in the office of the Addl.General Manager/TA.

| Sl.No. | Name of Work | Approx. Estimate Amount (Rs. in Lakhs) | Earnest Money Deposit (Rs. in Lakhs) | Completion period |
| --- | --- | --- | --- | --- |
|  | Part-A Civil Works |  |  |  |
| 1 | Providing support services for maintenance of Horticulture works in Type-V quarters, Nursery, Sunderavanam etc | 19.00 | 1.00 | 12 months |
| 2 | Providing support services for maintenance of sweeping of open areas in NH-I, V, VI & CISF | 16.41 | 1.00 | 12 months |
| 3 | Providing support services for maintenance of STDP, NRSP, Internal Drainage Lines | 12.47 | 1.00 | 12 months |
| 4 | Providing support services for maintenance of buildings | 11.10 | 1.00 | 12 months |
| 5 | Providing support services for maintenance of Fencing, Play Fields etc | 5.56 | 0.25 | 12 months |
| 6 | Providing support services for maintenance of water works and swimming pool. | 6.18 | 0.25 | 12 months |
| 7 | Providing support services for OPD in general hospital | 2.10 | 0.10 | 12 months |
| 8 | Providing support services for HRDC Hostel-1 and 2 | 2.63 | 0.10 | 12 months |
| 9 | Providing lawns in General Hospital Premises | 1.10 | 0.10 | 2 months |
| 10 | Zero waste management solutions in BHEL township. | 16.74 | 1.00 | 12 months |
|  | Part-B Electrical Works |  |  |  |
| 1 | Support services for Electrical maintenance of residential buildings. | 11.37 | 1.00 | 12 months |
| 2 | Support services for Electrical maintenance of non-residential buildings. | 7.53 | 0.25 | 12 months |
| 3 | Addition & Alterations to Electrical Points in General Hospital, Bore Wells, NRSP & STDP etc | 1.95 | 0.10 | 6 months |

Last date for receipt and opening of tenders is 23.09.2006  for all items except Part-A Item No.10 which is on 30.09.2006.   Tender cost for all items Rs. 500/- except Part-A Item No. 7, 8, 9 Part-B Item 3  Rs. 250/-.

Sale of tender documents (9.00 to 16.00 hrs) from 07.09.2006 to 21.09.2006 for all items and Part-A Item No.9 from 15.09.06 to 28.09.06.  Tenderers have to submit Registration, ESI Code, PF Code,  PAN No., APGST / VAT No (Tin No. for above Rs.5.00 lakhs works) Experience Certificate,  Labour Licence and  Other terms and conditions are as shown in the Techno Commercial Bid and full information may be had from web site http//www.bhel.com or in  the office of undersigned.

(G.Raghavulu),

Addl.General Manager/TA

Issued to:________________________

________________________

________________________

________________________

BHARAT HEAVY ELECTRICALS LIMITED

## RAMACHANDRAPURAM :: HYDERABAD–32

TOWNSHIP ADMINISTRATION

### TENDER DOCUMENTS (TECHNICAL BID)

Name of the work :  Additional & Alterations  for Electrical points in general hospital, Borewells, NRSP & STDP etc.

Tender Notice No. HY/TA/OT-03/2006-07  	Part-B  Item No. 3

#### INDEX

- Tender Notice

- Directions to Parties for Tendering.

- Tender for the work.

- Tenderer’s and Contractor’s Certificate.

- Contractor’s obligation

- General terms and conditions.

a) General terms and conditions (Part-2)

6.	Schedule – B  :---  Issue of stores to the contractor.

7. 	Schedule – C  :---	Services : Viz.,

Water and Electricity to the site of Contractor.

8.	Special Conditions

9.	Special Conditions (Safety)

- Drawings (if any)

SIG OF TENDERER				                       ISSUING OFFICER

Address:

BHARAT  HEAVY  ELECTRICALS   LIMITED

RAMACHANDHRAPURAM : : HYDERABAD-32

TENDER  NOTICE

###### No.  HY/TA/OT-03/2006-07,    	Date: 29.08.2006,  Part-B  Item No: 3

1.	Sealed  Tenders  will  be  received  by  the  Addl..General Manager  (TA), Bharat  Heavy Electricals Limited, Ramachandrapuram, Hyderabad-32  at his office up to 13.00 hours  on 23.09.2006 for  the  work of “Additional & Alterations  for Electrical points in general hospital, Borewells, NRSP & STDP etc.” at Ramachandrapuram, Hyderabad-502 032.A.P., Tenders (Technical bid) will be opened by the Senior Engineer (Civil),  Bharat Heavy Electricals  Limited, Ramachandrapuram, Hyderabad-32. on the same day at 13.15 hours in Township Administration office. The tenderers or their agents are expected to be present at the time of opening of the tenders. The tender receiving officer will, on opening such tender, attest over writings or corrections, if any, therein  in the presence of the tenderer’s who may be present at the time.  The tender should be in the form of obtainable from the Office of the Addl.General Manager (TA).  The Andhra Pradesh Detailed Standard specification  and other documents relating to the contract such as additional specifications, proforma for Bank  Guarantees, descriptive specifications sheets regarding materials etc., can be seen at any time between 09.00 A.M to 16.00 Noon in the office of the Addl.General Manager (TA). Tender forms and other particulars regarding the proposed work can be obtained on any working day from 09.00 to 16.00 hours upto 21.09.06 on payments of the prescribe sum of  Rs.  250.00  per set as non-refundable.

2.      Tenders   must  be  submitted  in  sealed   covers   and   should  be   addressed

to  the  	Addl.General Manager (TA),  Bharat  Heavy  Electricals  Limited,  	Ramachandrapuram,  Hyderabad – 32, the name of the tenderer and the

name of the 	work being displayed on the cover.

Contd.….2

:: 2 ::

If the tender is made by a individual, it shall be signed with his name and his full  address shall be given, If it is made by firm, it shall be signed with the co-partnership name by a member of the firm, who shall also sign his own name and the name and address of each member of the firm shall be given. If the tender is made by a corporation, it shall be signed by a duly authorized officer who shall produce with his tender, satisfactory evidence of his authorization. Such tendering corporation may be required before the agreement is executed, to furnish evidence of it’s corporate existence.

3.	Each  tenderer  must  pay  as  Earnest  Money,   a  sum  of  Rs.10,000/-   (Rupees  Ten thousand  only)  and  enclose  with his  tender the  receipt  endorsed  accordingly.  The  earnest 	Money prescribed for this work may be  offered  in  any of  the  following forms duly   pledged   to   the   Sr.  Accounts Officer (CASH), B.H.E.L.,  Ramachandrapuram, Hyderabad-32.

- a)	 Cash Receipt from B.H.E.L., Cash Office

- b)	 Bankers cheque, Demand Draft.

The Earnest Money will be refunded to the unsuccessful tenderer  after  the  intimation of  rejection of the  tender is  sent.  The Earnest  Money  will be retained in the case of the  successful  tenderer  and  get  converted  as  a  part of security Deposit for the due performance  of  the  contract and  in  either case  will  not  carry any interest. It will be dealt with as provided in the conditions attached to the tender.

When a tender is to be accepted, the tender whose tender is under consideration, shall attend the Office of Addl.General Manager (TA) upon  written information to him.  He shall forth with upon intimation being given to him by the Addl.General manager (TA) of acceptance of his tender, complete the execution of the agreement by signing all documents connected  there with, Failure to do so shall entail forfeiture  of the Earnest Money Deposit.

#### Contd.…..3

:: 3 ::

4.	EMD by the Tenderer will be forfeited as per Tender Document if.

- After opening the tender, the bidder revokes his tender within the validity period or increase his quoted rates.

- The tenderer does not commence the work within the period as per LOI/Contract.

EMD  shall not carry any interest.

If only a part of the work as shown in the tender is awarded, the amount of Earnest money will be forfeited with regard to the estimated cost of the work so awarded.

5.	Tenderers shall  peruse  carefully  the   instructions  laid  in  General Conditions of the  contract   and   all  other  relevant  documents  before   tendering   for  the  work.   The   approximate   quantity   of  work   to   be   executed   under  each  class  is  given  in   Schedule – “A”.  The quantities are given with a view to enable the tenderer to quote his over all rate to each clause of work in the tender form and for a uniform  comparison  of  tenders.   It  shall  be  definitely  understood  that  the  Bharat  Heavy  Electricals Limited, does not accept any  responsibility for correctness or completeness by commissions, deductions or additions at the discretion of accepting authority.

- The  Addl. General Manager (TA) reserves the right to reject any tender or part            thereof or all the tenders with out assigning any reasons thereof.

7.	 Tenders not submitted in proper form or in due time will be rejected.

8.	 The   offer  shall  be  valid  for  a  period  of  90 days  from  the date of

opening of the  tender.

Contd…4

:: 4 ::

9a.	 Security   Deposit  should  be  collected  from  the  successful  tenderer.   The

rate  of  Security  Deposit will be as below:

Upto Rs. 10 lakhs			        		10%

Above Rs. 10 lakhs upto Rs. 50 lakhs       	Rs. 1 lakh + 7.5% of the

amount exceeding

Rs. 10 lakhs

Above Rs. 50 lakhs                                     	Rs. 4 lakhs + 5% of the amount

Exceeding  Rs. 50 lakhs

If the work is awarded, the agency has to pay 50% of SD in advance on contract

value  before commencement of work after adjusting of EMD amount.

9b.	 Security Deposit may be furnished in any one of the following forms.

- Cash (as permissible under the Income Tax Act)

- Pay Order, Demand Draft in favour of BHEL.

- Local cheques of scheduled banks, subject to realization.

- Securities available from Post such as National savings Certificates, Kisan Vikas Patras etc.

- Bank Guarantee from schedules Banks / Public Financial Institutions as defined in the Companies Act subject to a maximum of 50% of the total security deposit value.  The balance 50% has to be remitted either by cash or in the other form of security.  The Bank Guarantee format should have the approval of BHEL.

- Fixed Deposit Receipt issued by scheduled Banks / Public Financial Institutions as defined in the companies Act.  The FDR should be in the name of the contractor, A/C BHEL, duly discharged on the back.

- Security Deposit can also be recovered at the rate 10% from the running bills.  However in such cases at least 50% of the Security Deposit should be deposited  before start of the work and the balance 50% will be recovered from the running bills.

- EMD of the successfully tender shall be converted and adjusted against the security deposit.

NOTE:  Acceptance of  Security Deposit against sl. No. (iv) and (vi) above will be adjusted to hypothecation or endorsement on the documents in favour of BHEL.  However, BHEL will not be liable or responsible in any manner for the collection of interest or renewal of the documents or in any other matter connected therewith.

9c.	 Security  Deposit  shall  not  be refundable to the contractor except in accordance  with the terms of the contract.

The  Security  Deposit  will  be  released  along  with  final  bill or after getting the final I.R. clearance certificate.

SIGNATURE OF TENDERER                                       ACCEPTING AUTHORITY

DIRECTIONS TO PARTIES FOR TENDERING

- A list of materials, proposed to be supplied by the Bharat Heavy Electricals Limited, Ramachandrapuram, Hyderabad – 502 032, and the places where and the prices at which they are proposed to be supplied is given in Schedule-B.  TENDERER MUST ACCEPT THESE MATERIALS AT THE SPECIFIED PRICES AND QUOTE FOR FINISHED WORK ACCORDINGLY.  Not with standing any subsequent change in the market value for those materials the charges to the party executing the work will remain as originally entered in the Agreement.  If at any time subsequent to the execution of this agreement, materials of B.H.E.L., other than those specified in the agreement are required by B.H.E.L., to be used on the work they will be charged at issue rate of BHEL.  The contractor will be informed in writing of this and he should intimate in writing the rate which he demands for finished work in view of the fact that he is to use materials of B.H.E.L, and at the issue rate.  No cartage or incidental charges will be borne by B.H.E.L., in connection with the supply of materials referred to in this paragraph.  If at any time, B.H.E.L., supplies materials other than those specified in the agreement at the request of the contractor for use on work, they will be charged at the market value prevailing at the time of supply or issue rate plus 12 ½% whichever is greater.

- Subsidiary items such as water for work, clearing and marking out site, hire of tools and plants should be separately entered.  If such items are not so entered, it will be assumed that the rates quoted, in the schedule include provision for them also.

- The tenderer shall examine closely, the Andhara Pradesh Standard specifications kept in Sr.Engineer, Civil’s Office and also the relevant clauses of the standard preliminary specification before submitting his tender unit rates which shall be for finished work in situ. The contractor should purchase a book of Andhra Pradesh Standards Specifications for his references.  He shall also carefully study the drawings and additional specifications and all the documents which form part of the agreement to be entered into by the accepted tenderer.

Contd.…2

:: 2 ::

- Each tenderer must quote the PAN no. with proof of allotment by the Income Tax Authority.   In the case of proprietary firm, it will be necessary to quote the  aforementioned for the proprietor or proprietors and for each of the partners as the case may be.

- Every tenderer is expected, before quoting his rates to inspect the site of the proposed work. He should also inspect the quarries, and satisfy himself about the quality and availability of materials.  The best class of materials shall be used on the work.  In every case, the materials must comply with the relevant standards specifications.  Samples of materials as called for in the Standard Specifications, or in this tender  or as required by the  Engineer-in-charge  having jurisdiction for the time being over the work, herein-after called Addl.General Manager(TA), shall have the due approval before the supply to site of work is begun.  Attention of the contractor is  directed to standard preliminary specification regarding payment of seigniorage,  tools etc,.

- Time shall be considered as the essence of the contract.  The rate of progress as mutually agreed to is required to be maintained.  Date of commencement of this programme will be the date on which the site (or premises) is handed over to the contractor.

- The tenderer should quote specific rates for each item in the schedule and the rates should be in rupees and paise or as directed in the Schedule-A.  The units and rates should be written both in words and figures.  The schedule accompanying the tender shall be written legibly and free from  erasures, over writings or corrections of figures.  Corrections where unavoidable should be made by crossing out, initialing, dating and rewriting.  No alterations which is made by the tenderer in the tender form, the conditions of agreement, the drawings or specifications accompanying the same will be recognized and if any such alterations are made, the tender will be void.

SIGNATURE OF  TENDERER     		               ACCEPTING AUTHORITY

TENDER FOR THE  WORK

I/We_____________________________________________do hereby tender to execute works of the under mentioned description and in accordance with the conditions noted below in consideration of payment being made for the quantity of work executed at the respective rates specified in the following schedule.

I / We hereby distinctly and expressly declare and acknowledge that before the submission of my / our tender I / We carefully followed the instructions in the tender notice and have read the  Andhra Pradesh Standard specification and the clauses of the preliminary specifications and that I /We have made such examination of the contract documents and of the specifications etc., and of the location where the said work is to be done and such investigation of the work required to be done and in regard to the material required to be furnished as to enable me/us thoroughly to understand the intention of same and the requirements, covenants, agreements, stipulations  and restrictions contained in the contract and in the said specifications and distinctly agree that I /We will not hereafter make any claim or demand upon the Bharat Heavy Electricals Limited based  upon or arising out of the said requirements, covenants, agreements, stipulations, restrictions and conditions.

Signature of  Tenderer

Address

TENDERER’S AND CONTRACTOR’S CERTIFICATE

1.	I hereby declare that I have perused in detail and examined closely the Andhra Pradesh Standard Specifications and it’s addenda volume and also BHEL General Conditions of contract. I agree to be bound by and comply with all specifications contained in Andhra Pradesh  Standard Specification and General Conditions of contract, for the various items of works specified in the      Schedule “A” and the work as a whole.

2.	I hereby declare that I shall pay the statutory minimum wages to my workers as applicable from time to time. I shall  also adhere to all the statutory obligations under Contract Labour (Regulation and Abolition) Act 1971 and Rules framed there under with subsequent revisions if any .

3.	The daily wage rate of labour applicable as on date from 01.04.2006 is as follows  as per Sr.Manager /HR(IRX) Ref. No. HR/IR/CL/06 Date : 15.06.2006

Unskilled worker		-	Rs. 117.10 / Per day

Semi Skilled Worker	-	Rs. 132.90 /Per day

Skilled Worker		-	Rs. 150.65 /Per day

4.		The Contract/Job Executing Officers are required to ensure that Contractor pays the ‘Daily Wages’ as shown above to their Labour after deducting Employee contribution towards PF & ESI at the rate of 12% and 4.75% respectively on the daily wages w.e.f 01.10.2005.  Contract Labour are also entitled for Holidays which are applicable to BHEL and 1 day Leave for every 20 days of working.

5.		Contractor shall pay 12% PF and 1.61% Administrative charges towards PF and 4.75% towards ESI as Employer’s contributions.  The contractor shall remit the above contributions along with Employee’s contribution to PF & ESI departments and file monthly returns by 20th of every following month.  Contractor shall also provide uniform, shoes and other personal protective Equipments (PPEs) wherever applicable to their Labour.

6.		Any increase in rate of DA/Wages hike shall not be reimbursed to the contractor.  Contractor shall anticipate such hike, and quote in the tenders.  It shall be noted that any increase of DA/Wages shall be absorbed by the contractor himself and BHEL will not reimburse the increase in DA/Wages.

Date _________________                           SIGNATURE OF  TENDERER

Annexure-C

CONTRACTOR’S OBLIGATIONS

  - CONTRACTUAL

- Contractor shall decide the number of employees to be deployed for execution of the work awarded to him and he or his authorized representative will be solely entitled to dictate such workers about the manner of carrying out the work as per the prescribed specifications and quality plan.

- Contractor shall supervise the work allotted to him and to be carried out by his employees.

- Contractor to ensure that the employees deployed in the premises of BHEL are physically and mentally fit and do not have any criminal record.  Such employees should possess requisite skill, proficiency, qualification, experience etc.

- Contractor to maintain appropriate records of his employees deployed to carry out the job (s).

- Contractor should issue appropriate appointment letters to his employees.

- Contractor to provide employment card / identity card with photograph duly verified and attested by the Contractor to his employees.  Contractor to indicate the name of the proprietory / partnership firm / company, place of work, contract number and duration of validity of card.

- Contractor will be responsible for the good conduct of his employees.  In case of any misconduct / misbehaviour by any employee, the contractor will replace such employee (s) immediately.

- Contractor will ensure that the job is executed through his employees on his rolls and under  no circumstances the contractor will deploy any casual employee to carry out the job nor shall sub-contract the job without prior written permission.

- Contractor will keep watch on his employees and he will be liable for any pilferage / loss to BHEL due to acts of omission and commission by his employees.  Similarly, liability for any compensation to outsiders on account of any act of omission and commission by the employees deployed by the contractor shall lie exclusively with him.

- Contractor to provide safety appliances and safety shoes to his employees.  The contractor shall be responsible and safety regulations as applicable.

- The contractor has to provide a distinct uniform different from BHEL employees.  The Uniform should have logo of the Contractors firm / company.  The uniform shall be kept in neat, tidy and wearable condition.  Wherever necessary, the Cap shall be integral part of the uniform.

- Contractor to ensure that all precautions are taken for safety of his employees and equipments.

Contd..2

::2::

- In the event of termination of contract for any reason whatsoever, the contractor shall withdraw all his employees from the establishment of BHEL.  In case contractor decides to terminate services of his employees, he should settle all terminal dues including retrenchment compensation.

- Contractor shall provide to his employees all tools, tackles and equipments and maintain the same to carry out the job under the contract at his cost and if necessary contractor may take insurance policy of his men, material, equipments and tools and tackles.

- Contractor shall provide safety appliances and maintain the same at his own cost which may be required under the statute or otherwise.

- Contractor shall provide material at his cost as mentioned in the contract to his employees for carrying out the job.

  - TOWARDS STATUTORY LIABILITY

- All statutory requirements under Minimum Wages Act 1948 Payment of Wages Act 1936 Workmen Compensation  Act 1923, EPF & MP Act 1952, Payment of Gratuity Act 1972 ESI Act, 1948,  the Contract Labour (R&A) Act 1970, Payment of Bonus Act 1965, Income Tax Act, Service Tax Act and all other applicable Acts shall be complied with by the contractor.

- Contractor shall comply with all statutory requirements, rules, regulations, notifications in relation to employment of his employees issued from time to time by the concerned authorities.

- Contractor shall ensure payment of statutory prescribed minimum wages as applicable from time to time in the presence of authorized representative of BHEL and maintain proper records of their timely  disbursement.  These records need to be preserved for a period of atleast 3 years and should be made available even after the contract is over for any verification by the statutory authorities / BHEL authorities.

- Contractor to provide PF pass book to his employees and ensure payment of PF, EDLI, pension dues under EPF & MP Act 1952 to the RPFC.

- Contractor shall ensure payment of ESI contribution under ESI Act 1948 and provide ESI membership No / Card of each employees.

- Contractor shall produce proof of deductions as well as remittances of PF, EDLI, Pension, ESI contribution, administrative charges etc., wherever applicable and shall maintain proper records.  Contractor to issue wage slips to his employees.

- Contractor shall furnish proper returns to the concerned statutory authorities and provide a copy of the same to BHEL.

- Contractor shall be solely responsible for non payment / delayed payment of wages / DA, contributions under EPF & MP Act, ESI Act etc.

Contd..3

::3::

- In case the contractor fails to make payment of wages to his employees or remittance of contribution to the concerned authorities, the security deposit / other dues / running bills under the contract can be utilized by BHEL to discharge the liability of the contractor.

- Contractor shall indemnify BHEL against all claims and losses under various Labour Laws, statutes or any civil or criminal law in connection with employees deployed by him.

- The liability for any compensation on account of injury sustained by an employee of the contractor will be exclusively that of the contractor.

- Contractor to obtain insurance cover for his employees / equipment, tools and tackles etc and take third party risk insurance coverage at his own cost.  BHEL shall not be responsible for any loss, damage pilferage of his property and / or his employees.

- Contractor should have independent code numbers / exemptions under EPF & MP Act 1952 and ESI Act 1948 and shall cover his employees under the said codes.

- Payment of bonus under the Payment of Bonus Act Payment of gratuity under the Gratuity Act, and retrenchment compensation under Act will be the sole responsibility of the contractor.

- Over and above the daily wage rate, payment shall be made  for leave with wages.

- Contractor shall observe Provisions of the Factories Act in respect of working hours, holidays, rest intervals, leave and over time to his employee.  No work shall be done on second / third shift, overtime, Sundays or on other declared holidays without written permission.

- In case a contractor employs women as employee he will discharge his obligation under law in respect of such women workers such prohibition of engaging them during night-hours, prohibition of employing them for more than 9 hours per day, provision of crèche facility, grant of maternity leave as per rules etc.

- Contractor shall be responsible for making payment of wages before expiry of 7 days from the last day of wage period and to ensure disbursement of wages in the presence of the authorities representative of contract operating division who shall record under his signature at the end of entries in the Register of wages.

- Contractor to obtain license under CL (R&A) Act 1970.

‘Signature of Tenderer’                                  		ACCEPTING AUTHORITY

GENERAL TERMS & CONDITIONS (Part-2)

- The contractor shall comply with the following general terms conditions and special instructions.

- The contractor shall fully comply with the following enactment’s:

- Contractor Labour (R&A) Act,  1971.

- Wage Rates not less than that notified by State Labour department from time to time.

- Payment of Wages Act.

- ESI Act,  1948.

- EPF Act,  1952.

- Workmen’s Compensation Act, 1923.

- The company’s instructions as issued from time to time in regard to working hours, wages, leave, holidays etc.

- The Contractor shall obtain license from the Assistant Labour Commissioner (Central), or appropriate Government if he engages 20 (Twenty) or more workmen only.

- The contractor shall produce the following Registers and forms before commencement of work, for verification by the Executing Officer of the company.

a.	Form XIII	-	Register of workmen employed by contractor (Rule 75).

- b.	Form XIV 	-	Employment card issued by contractor (Rule 76).

- c.	Form XVI	-	Muster Roll (Rule 78 (1) (a) (i)).

- d.	Form XVII	-	Register of Wages (Rule 78 (1) (a) (i)).

- e.	Form XVII	-	Register of wages - cum Muster Roll (in case of weekly

- payment).

- f.	Form XIX	-	Wage slip (Rule 78 (b)).

- g.	Form XX	-	Register of deduction for damages or loss (Rule 78 (1)

- (a) (ii)).

- h.	Form XXI	-	Register for fines  (Rule 78 (1) (a) (ii)).

- i.	Form XXII	-	Register of advances  (Rule 78 (1) (a) (ii)).

- j.	Form XXIII	-	Register of overtime (Rule 78 (1) (a) (iii)).

- k.	Form XXIV	-	Register to be sent by the contractor to licensing

- officer (Rule 82 ) (1).

The contractor shall maintain the above neatly, completely an legibly for inspection by various statutory authorities and the company officials even at short notice.

5.	The contractor shall observe

- (a) 	Weekly rest day.

- (b)	The company list of holidays.

- Contd….2

:: 2 ::

- Contractor shall obtain complete bio-data of the labour, employment certificate and Antecedent verification in the prescribed form for each labour and supervisor  engaged  by him and shall submit the same to the Personnel Department / IR section through the contract executing officers before commencement of the work.

- The Entry permits are to be issued to the Contract Labour by Assistant Commandant /   CISF (Plant), based on the requisition submitted by Contract Executing Officer and forwarded by  Dy.General manager / Personnel.

- Every contractor shall submit a notice regarding commencement and completion, of work in form – VI A&B [Rule 25 (VIII) & 81 (3)] to Personnel Department, IR section through his contract executing officer, for forwarding the same to State Labour Department.

- The contractor shall make himself of his representative available at the work spot everyday during execution of work, for effective supervision.

- The contractor shall attend to all inspections notified / conducted by the Personnel Department, Labour Department, P.F. authorities. Factory Inspectors ESI Inspectors, or any other such authorities under the act.

- Non – compliance of any provisions under the act/ rule/instructions / guidelines shall make the contractor liable for penal action including termination of contract.

- Contractor shall furnish in a separate letter his place of residence and postal address. The delivery at the above named place or posting in a Post box regularly maintained by the post and telegraph Department or sending letters registered for acknowledgement of any notice,  letter or other communication to the contractor. Change in address shall come into force at any time by an instrument executed by the contractor and delivered to the Company official who has signed the contract.

- The contractor must satisfy himself by personal study and examination of the drawings / specifications furnished and understand thoroughly the scope of proposed work in detail and all conditions affecting the work before entering into the contract. There shall not be at any time dispute / complaint of any misunderstanding with regard to scope  of work and interpretation of specifications or any misunderstanding with regard to nature or omission of the work to be done not shall any application for compensation in terms of time and money shall be accepted by company regarding the above.

- Contractor shall in his absence keep competent agent constantly on the works and any directions or explanations given by the “Contract Signing Officer” or his representative to such agent shall be held to have been given  to the contractor himself.

- Contractor on the advise of company official shall immediately remove any person employed by him, who may in the opinion of the company official is incompetent or misconducts himself and such persons shall not be again employed on the works without permission of the company official.

Contd.…3

:: 3 ::

- The contractor shall erect and maintain at his own cost temporary weather proof sheds at such places approved by the company for keeping  materials under cover.

- The contractor shall give all notices required by the acts regulations, bylaws, legal acts and pay all fees in connection therewith unless and otherwise arranged and decided in writing with the company. He shall also ensure that no attachments are made against materials or work forming part of or for the use of the contractor. In all such cases, contractor shall protect and indemnify the company against any claim or liability  arising from or based on the violation of any such laws, ordinances, regulations ,orders, decrees or attachments either by himself or by his employees,

- It shall be contractor’s sole responsibility to protect the public and his employees against accident from any cause and provide required safety equipments and shall indemnify, the company against any claims for damages for injury to the person or property resulting from any such accidents and shall, where the provisions of the workmen’s compensation act apply, take  steps to properly insure against any claims thereunder.

- In the event of any accident in respect of which compensation may become payable under the workmen’s compensation act. VIII of 1923 whether by the contractor or by the company as principle employer, it shall be lawful for the company to retain out of monies due and payable to the contractor such sum or sums of money as may, in the opinion of the company shall be final in regard to all matter arising  in this clause.

- No work shall be done on Sundays or on other declared holidays of the company without the written permission of the company officer incharge o f the work. The contractor shall comply with the provisions of the Factories Act Rules framed thereunder if the same are applicable.

- The contractor shall keep his work place clean and safe to avoid injuries to men and damage to finished products / equipments.

- On the occurrence of an accident, which results in the death of any of the workmen employed by the contractor or which is so serious as to be likely to result in the death of any such workmen, the contractor shall within 24 hours of the happening of such an accident  intimate in writing to the company official incharge of the work.

- The contractor shall indemnify the company against all losses or damages sustained by the company resulting directly or indirectly from his failure to give intimation in the manner aforesaid including the penalties or dues if any and become payable by the company, as a consequence of failure, the company to give notice under the workmen’s  compensation act or otherwise confirm to the provisions of the said act in regard to such accident.

Contd.…4

:: 4 : :

- The contractor shall ensure adherence to all statuary requirements applicable to BHARAT HEAVY ELECTRICALS LIMITED, RAMACHANDHRA PURAM, HYDERABASD-502032.

- The contractor shall ensure abidance by all the labour laws especially including contact labour (R & A ) Act, payment of wages Act, workmen’s compensation act, minimum wages Act ESI Act and Provident Fund Act as amended from time to time.

- The contractor shall comply with provident Fund Act either through PF code allotted to him are by the code provided by PF Department to work Centers in the FACTORY /TOWNSHIP CIVIL OF B.H.E.L. Ramachandrapuram,  Hyderabad –502032

- Not withstanding the clause, in case of any financial loss incurred by the company on account of contravention of the Provident Fund regulations or any regulations of rule touching the same by the contractor, the contractor shall submit an undertaking to indemnify the company to the extent of the loss incurred by the company.

- The contractor should engage only those labourers who shall be more than 18(eighteen) years of age.

- The contractor shall not resort to sub-contracting under any circumstances.  If found subcontracting at a later date, BHEL reserves the right to take whatever action it deems fit, including cancellation of the contract.

- The contractor shall provide the required safety  equipment to the labours engaged by him.

- Contractor shall issue “Employment Card” as per statute to all the labour and supervisors covered under the job work contract.

- The contractor shall be responsible to settle any grievances of the labour deployed by him.

- Whenever the term “CONTRACTOR” is used, it shall be understood to refer to the particular person, firm or corporation with whom an agreement has been made by the concerned company official for executing the work defined in the concerned agreement and for the purpose of instructions regarding compliance with contract conditions, it shall include the contractor’s authorised agents, who are entrusted with the work by contractor.

- The quantities mentioned in the agreement schedule are worked out from the relevant drawings in the company and may not be the actuals required for execution.

- The company does not expressly or by implication agree that the actual amount of the work to be done shall correspond there with, but reserves the right  to increase or decrease the quantity of any class or portion of the work as he deems necessary.

Contd.…5

:: 5 : :

- All the works shall be carried out in accordance with the directions and to the satisfaction of the company official in accordance with the drawings, specifications and instructions.  Supplementing or explaining the same as may from time to time shall be done by the company official.

- For all modifications, omissions or additions to the approved drawings and specifications, the company shall issue revised plans or written instructions and no modifications, omission or addition shall be made unless so authorized and directed by the company in writing at any time before completion of the work.

- The company shall have the privilege of ordering modifications, omissions, or additions at any time before completion of the work.

- All materials, articles, and workmanship shall be the best of their respective kinds for the class of work described in the contract specifications and schedule and materials to be obtained by the contractor shall be from sources approved by the company.

- Sample of materials shall be furnished by the contractor at his expense to the company when called for before execution of any work.

- The company shall have power to reject at any stage, any work which is considered to be defective in quality of materials or workmanship and  shall not be debarred from rejecting wrong material by reasons of having previously passed them in an unworked condition.  Any portion of the work or materials rejected or pronounced to be inferior or not in accordance with specifications shall be taken down and removed from the work site at the contractor’s expenses.

- The decision of the company shall be final and binding on the contractor on all technical questions which may arise in the contract with respect to material, workmanship, removal of improper work, interpretation of the working drawings, specifications, notes, procedures etc.

- The decision of the “Contract Signing Officer” or any officer deputed by him duly authorised on his behalf, in respect of the rate of progress and the quality of work or material shall be final.

- Contractor shall be deemed to have included in his tender price of all the plant.  Machinery and appliances required for the purpose of all operations connected to secure a satisfactory quality of work within the opinion of the company will ensure the completion of the work within the time specified.

- If at any time, during the progress of work or any part of it such methods or equipment appear to the company official to be insufficient or inappropriate for ensuring the quality of work required or rate of progress, he may order the contractor to increase their efficiency or to improve their quality of work and the contractor shall comply with such order and on failure of which the company may take such action as it deems it fit to improve the quality of work or the rate of progress required from the contractor and all such actions taken by the company shall be at the cost and risk  of the contractor.

Contd.…6

:: 6 ::

- It is open to the company to lend or supply to the contractor any tools, implement, material and machinery that are needed by the contractor, which in the opinion of the company is essential to improve the quality or progress of work.  The contractor shall pay such deposit or charges that may be fixed or determined by the company for any such articles or machinery lent or hired to the contractor.

- Any electric power required for contractors machinery for the purpose of work shall be supplied by the company at the written request of the contractor at one point subject to the observance of rules an regulations of Electric board / company and charges there on shall be recovered from the contractor.

- The contractor shall confirm to the regulations and laws of central / state govt. or any local authority and that of the company with whose system the machinery is supposed to be connected.

- All rubbish as it accumulates shall be removed from the site to the point of disposal as indicated from time to time by the company. If this is not adhered to, the company shall remove the scrap and recover the cost of these operations from the bills of the contractor.

- Any sum due from the contractor on account of tools and plants, stores, or any other items provided by the company shall be deducted from the respective bill due to him.

- In case of breach of any of the terms and conditions of the contract, a claim shall be lodged under the bank guarantee with the guarantor at the discretion of the competent authority of the company.  On successful completion of the contract to the satisfaction of the company, the bank guarantee shall be released after due claim period.

- In the event of any question or dispute  under this contract, the same shall be referred to a competent Authority in the company for sole arbitration and his decision shall be final and binding on the parties to the contract.

- In case of any suit or other legal proceeding arising under this contract, the courts at Sangareddy (Medak Dist.) A.P only shall have the Jurisdiction.

- The company reserves the right to enter into parallel agreement with one or more contractors at their direction.

- Disputes, grievances between the contractor and his labour, will have to be settled by the contractor only.

- The labour employed by the contractor, if found in abetting and fellow labour or contractors or any BHEL employee, the same shall be considered as an act of indicipline.  Such labourers shall be removed from the services of the contractor, on the advice of BHEL.  Further the contractor shall initiate every necessary action in accordance with the relevant Laws, Rules & Regulations and enactments of State and Central Government.

Contd.…7

:: 7 ::

- Wherever, BHEL/COMPANY standards are mentioned, copies of which are enclosed they shall by strictly followed.

- Nothing contained in the contract agreement and its conditions shall be deemed to preclude or render inoperative the service of any notice, letter or other communication upon the contractor personally.

- The decision of the “Contracting Signing Officer” shall be final and binding on the contractor on all technical questions which may arise touching the contract with respect to the quality of material, workmanship, removal of improper work, interpretation of the working drawings, specifications, notes, procedures etc.

- Special Instructions:

- If an individual makes the tender, it shall be signed with his full mane and his address shall be furnished.  If it is made by firm, it shall be signed with the co-partnership name by a member of the firm, who shall also sign his own name, also furnish the name and address of each member of the firm, if the tender is made by corporation, it shall be signed by a duly authorized officer who shall produce with the tender, satisfactory evidence of his authorization.  Such tendering corporation / firm is required to furnish evidence of its existence along with bid.

- The EMD will be refunded to the unsuccessful tenderers on application after rejection of the tender is intimated.  The earnest money will be retained in the case of the successful tenderers and either of the cases will not carry any interest.  If will be dealt with as provided in the conditions attached to the tender.

- Whenever a tender is to be accepted, the tenderer, whose tender is under consideration, shall attend the office of “Office Inviting the Tender” on the date fixed by written intimation to him.  He shall forthwith, upon intimation being given to him by the “Officer Inviting the Tender” [Ex. AGM (T.A)] for acceptance of his tender, complete the execution of the agreement by signing all documents connected therewith.  Failure to do so and not to commence the work within the time specified in the Letter of Intent shall entail forfeiture of the earnest money.

- Tenderers shall peruse carefully the instructions and directions to parties tendering and the conditions of the agreement and all other relevant documents before tendering the rates for the work.  The approximate quantity of work to be executed under each class is given in the schedule.  The quantities are given with a view to enable tenderer to quote his overall rate for each class of work in the tender form and for an uniform comparison of tenderers.  It shall be definitely understood that BHEL does not accept any responsibilities for the correctness or completeness of this schedule and that the schedule it liable to alterations by omission deductions, or additions at the discretion of accepting authority.

Contd.…8

:: 8 ::

- The tenderer shall keep the offer valid for a period of 90 days from the date of opening of tender.  It is being understood that the tender documents have been sold / issued to the tenderer and the tenderer is being permitted to tender in consideration of the stipulation on his part that after submitting the tender, he will not recall his offer or modify the terms and conditions   thereof  in a manner not acceptable to the “Officer Inviting the Tender” Should the tenderer fail to observe or comply with the foregoing stipulation, the EMD shall be forfeited.

- Tenderers have to quote their rates in the tender schedule legibly written in figures and words and those not submitted in proper form are liable for rejection.

- The submission of tender shall be strictly in accordance with the terms and conditions stipulated in this tender notice. No counter conditions will be acceptable or valid.

- The tenderers  must satisfy themselves by personal sturdy and examination of the drawings / specifications furnished and understand thoroughly the scope of proposed work in detail and all conditions affecting the work before entering into the contract.  There shall not be at any time after submission of the tender dispute/ complaint of any nature regarding the scope of work and interpretation of specifications or any misunderstanding with regard to nature or omission of the work to be done nor shall any application for compensation in terms of time and money shall be accepted by BHEL in regard to the above.

- Contractor shall be deemed to have included in his tender price of all the plant, machinery and appliance required for the purpose of all operations connected with the work embraced under the contract to secure a satisfactory quality of wok and rate of progress which in the opinion of the “Contract Signing Officer” will ensure the completion of the work within the time  specified.

- The contractor has to produce the bank guarantee in the prescribed proforma  valid for the contract period for a value calculated at the rates mentioned towards security deposit.  The claim period under the guarantee shall be valid for six months after expiry of  the contract.

- This is a time bound contract for period mentioned, and does not envisage any escalation of price.

- The rates quoted by the contractor shall be firm for the contract period.  There shall be no revision in contract rates due to increase in any statutory levies during the period of the contract and this increase shall be absorbed by the contractor himself in full.

SIG. OF THE TENDERER                           ACCEPTING AUTHORITY

Annexure-D

GENERAL TERMS & CONDITIONS

  - BHEL shall have privity of the contract with the contractor only and will give instructions to the contractor or his authorized representative.  BHEL will have nothing to do or be concerned with the employment of employees working for the contractor.  The relationship between BHEL and the contractor will be that of independent entities and nothing herein contained will amount to joint venture, partnership or an employer-employee relationship.

- The contractor shall maintain regular contact with the designated employee(s) of BHEL and will interact on matters relating to the work awarded under this contract.

- In case the contractor does not carry out the Contractual / Statutory obligations or the services rendered by him are found to be unsatisfactory, BHEL shall bring the same to his notice and he will be obliged to discharge the obligations and rectify the deficiency / anomaly within three days time failing which, BHEL reserves the right to terminate the contract without assigning any reason whatsoever.  In such an event, no damages will be payable for short closure of the contract.

- The contractor shall deposit an amount as per clause 9a,b,c of tender notice as security with BHEL.  This security deposit shall be liable to be returned to the contractor after termination of the contract or at the end of maintenance period subject to deduction on account of company dues, non-deposit of statutory dues etc.  No interest shall be payable on the security deposit.

- The decision of BHEL regarding interpretation of any of terms and conditions set forth in this agreement shall be final and binding on the contractor.

- Any matter arising out of or in connection with the agreement shall be under jurisdiction of Sangareddy Court, Medak District, A.P.

- Not with standing anything contained in this Agreement, the contract may be terminated by BHEL without assigning any reason there of by giving a notice of 30 days to the contractor.

- The contract will commence on ________________ date and will remain valid for a period of 6 months .  The parties reserve the right to extend the contract on mutually agreed terms and conditions.

- All disputes arising in connection with the contract shall be settled by mutual consultation.  If no agreement is reached the dispute shall be settled in accordance with the provisions of the Arbitration and Conciliation Act, 1996 and the rules made there under.  The dispute shall be referred for arbitration to any arbitrator to be appointed  by the Head of the Unit.  The award of the arbitrator shall be final and binding on both the Parties.  The venue of the Arbitration shall be Ramachandrapuram, Hyderabad in India.  The Award to be given by the Arbitration shall be a speaking award.  All questions, disputes, differences arising under, out of or in connection with this contract shall be to the exclusive jurisdiction of Sangareddy courts, Medak District, A.P.

SIG. OF  TENDERER		  	                 ACCEPTING AUTHORITY

N O T E:

(GENERAL CONDITIONS)

- The quantities shown above are approximate and liable for variation.

- All BHEL general conditions of the contract shall be applicable.

- The contractor shall affix his signature at the end of each page of this tender documents and put rubber stamp wherever he signs in the Contract agreement or bills for making payment.

- Any statutory increase in the labour wages during the period of execution shall be borne by the agency.  The agency shall quote the rates considering the possible labour escalation also.

- The rates quoted shall include all lifts, leads and other incidental charges mentioned in the General conditions of contract unless otherwise specified.

- The department reserves the right to split and award the work to more than one agency.

- The contractor should engage labours who should not be less than 18 (eighteen) years of age.

- All the bills of contractors will be cleared by Finance Department subject to production of "Clearance Certificate" by the contractors in respect of compliance of all statutory requirement, issued by IR section of Personal Department.

SIGNATURE OF  TENDERER					ISSUING OFFICER

SPECIAL CONDITIONS

- Time is the essence of contract and the specified time of completion is upto

6 months which will be reckoned from the date of commencement of work.

- These special conditions supplement the conditions to tenders and contracts and the General conditions of contract and from part of the contract documents.  Where these special conditions are at variance with the General conditions of contract, these special conditions shall prevail.

- All rates quoted shall be for finished work in situ inclusive of all leads, lifts and other incidental charges and those in general conditions.

- Before quoting his rates of the work, the tenderer shall inspect the site of work and the quarries from which various materials are to be brought and should satisfy himself about the nature and scope of work to be executed and quality of materials procurable from the quarries.  In every case the materials shall conform to the relevant APSS and shall be got approved by the engineer-in-charge before they are used on the work.  The Bharat Heavy Electricals Limited will not, however, after acceptance of a contract rate, pay extra charges for any other reasons, in case the contractor is found later on to have misjudged the nature and scope of the work and also the availability of materials.

- The  tenderer is not allowed to alter the specifications of the unit of work noted in the Schedule-A.  For the sake of uniformity in comparisons of tenders, the tenderers should not add any conditions of their own.  Tenders not complying with these conditions are liable to be rejected.

- The issues of materials are governed by the conditions specified in Scheduled-B.  The contractor himself shall supply all other materials and the rates for the relevant items are inclusive of all such supplies.

- The cement concrete work plain and reinforced shall be executed as per IS : 456 (latest).  A tentative sketch/drawing of work is available in the office, which is intended to give a general idea of the work to be executed and is liable for modifications during the actual execution based on the designs prepared and approved by the Competent authority.

- The rate quoted for Reinforced Cement Concrete items shall include smooth finishing of exposed faces.  The top surfaces of roof slab shall be laid to specified slope and mortar that comes to surface due to vibrations shall be trowelled so as to obtain smooth and even surface.

- The paint to be used shall be of standard make and shall be approved by the Engineer-in-charge before applying.

Contd…2.

// Page – 2 //

- The tenderer should specify the plant and machinery such as pan mixers, concrete mixers, vibrators, steel shuttering etc., that he possesses and is going to use them on the work.

- The Andhra Pradesh Standard Specification / I.S. Specifications, those in Schedule-A  shall be followed for all items of works.  Wherever there is difference between the A.P.S.S. and I.S. Specifications, the later shall prevail.

- The Addl.General Manager (T.A)  reserves the right to deviate either by addition or by deduction from the schedule of items of work given in the tender document after awarding the work.

- In case of any difference between agreement wording and detailed drawings the interpretation of the Addl.General Manager (T.A) shall be final and binding on the contractor.

- The final acceptance of work in all items is subject to proper behaviour after testing regardless of whether the items are paid for or not.

- All debris and surplus materials shall be cleared from  the site as and when directed by the Engineer-in-charge.  Any temporary structure / stores made by the contractor for the work shall be demolished and site cleared before payment of final  bill.

SIGNATURE OF  TENDERER			                   ACCEPTING AUTHORITY

## BHARAT HEAVY ELECTRICALS LIMITED

RAMACHANDHRAPURAM : : HYDERABAD – 32.

(SPECIAL CONDITIONS – SAFETY)

- The  following  are  a  few   safety  measures  suggested  while  carrying  the       work. However all the items of work should be carried out in safe working manner taking all precautions.

- Proper and necessary precautions shall have to be taken wherever the work involves breaking of reinforced  cement concrete slab and dismantling of brick work.  These items of work will have to be carried in the presence of the Engineer-in-charge.

- Proper and necessary scaffolding  is to be erected wherever dismantling of brick work is carried out  at height more than 1.80 M

- Reinforced   cement   concrete   slab   should   be   dismantled   parallel  to  the  main reinforcement, each piece not exceeding  300mm wide.  Under no  circumstances the supporting wall shall be cut or removed until the supporting slab is demolished.

- The  contractor  shall  keep  supply  all  safety  equipment  like  safety boots, goggles,  helmets and safety belts, to all the workers.

- The contractor shall keep a supervisor always at work site.

- Power shut  down shall be taken before commencement of the work wherever power cables are running.

- Proper and necessary scaffolding and ladders are to be used for carrying out all types  of  works.

SIGNATURE OF TENDERER     	              ISSUING/ACCEPTING AUTHORITY

Issued to:         ________________________

________________________

________________________

________________________

BHARAT HEAVY ELECTRICALS LIMITED

## RAMACHANDRAPURAM :: HYDERABAD–32

TOWNSHIP ADMINISTRATION

### TENDER DOCUMENTS  PRICE BID)

Name of the work :  Additional & Alterations  for Electrical points in general hospital, Borewells, NRSP & STDP etc..

Tender Notice No.HY/TA/OT-03/2006-07	Dt. 29.08.2006	Part-B Item No-3

#### INDEX

- Schedule ‘A’    : Schedule of rates and approximate quantities

SIGNATURE OF  TENDERER			ISSUING OFFICER

Address:

SPECIAL TERMS AND CONDITIONS

- All Decolam / Hylam top switch boards shall have a top of 3mm thick Decolam/Hylam sheet suitably fixed/screwed to MS boards/TW supporting plank ½" thick.  This form top half of the board.  The bottom half shall consist of a TW frame ¾" thick with a cover of 3/8" thick.  The top half of the board shall be fixed to the bottom half hinges at the end latches at the other end so that the top half can be got approved before bulk manufacturing.

- The switch boards shall be fixed as per the mark given by the Engineer-in-Charge.

- All the wires and cables should be of multi-standard and reputable make bearing ISI mark and should get approved by Engineer-in-Charge before use.

- All the earth terminals should be provided with suitable lugs.  A 25x3mm MS strip to be fixed to the bottom plank of the folding boards/MS boards for fixing the earth connections.

- All the terminal ends should be provided with suitable crimped lugs.

- The standard of wiring/rewiring in all respects should be superior quality and conform to ISI 732 and all accessories should be conform to relevant IS specification.

- All meters to be installed at the first stair case landing of the building and suitably numbered with white paint.

- Care should be taken to fix fuse wires of proper rating after approval of Engineer-in-Charge.

- All regulators switch boards shall be minimum 12"x10"x2" of MS sheet steel boxes.  Other switch boards shall be of 7"x4"x2", 6"x6"x2", 4"x4"x2" as per requirement.

- The top of MS junction boxes in ceiling shall be covered with teak wood round block of ¼" thickness to avoid leakage.

- All non-metallic conduit used shall conform to IS:2509 1973.  The conduit may be either threaded type or plain type as specified in IS:3419-1976.

- Bunching of cables shall be as per IS:732 (Part-11) 1983.

- The chase in the wall shall be neatly made and be of ample dimension to permit conduit to be fixed in the manner desired.  In case of building under construction chases shall be provided in walls ceiling etc.  at the time of their construction and shall be filled up neatly after erection of conduit and brought to the original finish with white wash/colour wash as the case may be.

- The conduit shall be fixed by means of staples saddles not more than 60cm apart, fixing of standard bends or elbows shall be avoided as far as practicable and all curves maintained by bending the conduit pipe itself.

Contd.2..

::2::

- Suitable inspection boxes shall be provided to permit periodical inspection and to facilitate removal of wires if necessary.

- All damages including cracks in any developed  in walls/ceilings etc. while making changes shall be made good by the contractor at his cost to the satisfaction of Engineer-in-Charge.

- The PVC conduit pipe used shall be of minimum size 25mm dia. 1.5mm thick.

- All the teak wood boards of  size 12"x10" and below should have single plank to cover and having teak wood back cover of size 3/8" thick with not more than two planks.

- All boards should have four gutties with four screws, round block to have two gutties with two screws.  The screws should not be fitted below any socket, switch or regulator.

- All the teak wood items such as reaper, round block, boards, gutties etc. must be replaced by new ones.

- Only best quality teak wood should be used for reaper, gutties boards etc. and shall be given two coats of varnish at site.

- All old servisable/unservicable switches, plug socket holders, shades, wires cables, GI wire (to be coiled and marked according to size specification) Sub-distribution boards, IC cut-out, brackets shades, TW boards should be properly accounted and returned to stores.

- All old switches, plug socket holders shades energy meters etc. should be properly cleaned and refixed in the quarters.

- The additional light points, plug sockets added by the residents shall be (in case they are required to be dismantled ) as it was previously and adjusted into spare circuits if any, leaving one circuits spare all in  the D.B.  In case spare capacity is not available in D.B. as specified above, the same shall be intimated to the Engineer-in-Charge and clearance obtained before handling over the installation.

- At the end of days work the working place should be cleaned off all dust, scrap material and supply to be restored at the end of days work.

- Separate neutral to be run from distribution board to each circuit.

- All wired/rewired quarters are to be meggered in the presence of the Engineer-in-Charge and results recorded.

- All the materials must be got approved by the Engineer-in-Charge before use.

Contd.3

::3::

I.  APPROVED BRAND OF MATERIALS

1.   TEAK WOOD GUTTIES             :	2.5cm (1") square on the inner end and 2cm (3/4") square

on  outer end  cemented with 6mm (1/4") of the surface.

Gutties should be of well seasoned teak wood.

2.   TEAK WOOD REAPER             : 	Straight minimum 12mm thick, well seasoned best

quality teak wood with two coats of varnish at site.

- SWITCH BOARDS FOLDING  :	Decolam top switch board shall have a top of 3mm thick

TYPE WITH DECOLAM TOP	Decolam sheet suitable fixed plank 12mm thick.  This

forms top half shall consist of a teak wood frame 20mm

(3/4")  thick with back cover of 10mm thick.  The top half

of the board shall  be fixed to the board shall be hinges at

one end and latches at the other end.

- TEAK WOOD FOLDING    : 	Well seasoned best quality teak wood should be

BOARDS				used with one end hinged 	and other end with a

latch.   All  teak wood  board  of  size 300x250mm

(12" x10") and below should have single plank cover

with not more than two planks.  All teak wood

boards of size 375x300mm (15"x12") and above may

have two plank top cover not more than three

planks.

5.   LINK CLIPS	             :	6mm width, 30 SWG brass tiger.

- WIRES 2.5 SQMM, 4 SQMM    :	Single core multistandard PVC insulated PVC

6 SQMM 10 SQMM.                   	Sheathed Aluminium conductor / copper cable

of Payal/Paragon /Radiant/Fincab/Minda

(Neon) ISI mark 1100V grade.

7.   SWITCHES SINGLE POLE/     :	Khosla/SSK/Leader/Anchor

DOUBLE POLE PORCELAIN

BASE TUMBLER TYPE.

8.   SWITCHES SINGLE POLE/      :	SSK/Cona/Leader/Ellora

DOUBLE POLE PIANO TYPE.

9.   PLUG SOCKETS 3PIN, 5A,       : 	Kosla/Leader/SSK

WITH PORCELAIN BASE.

10.  PLUG SOCKET FLUSH TYPE :	Anchor/Cona/Leader/SSK.

11.  LAMP HOLDER		       :	OK/SSK/Anchor

12.  CEILING ROSE		       :	SSK/Khosla/Anchor

contd..4

::4::

13.  EI SHADES		       :	16 SWG thick.

14.  GI PIPES		       : 	Kalinga brand/ khandelwal

15.  PVC PIPES		       :	Sudhakar 1.5/2mm wall thickness upto 40mm dia.

16. METALLIC CODUIT	        : 	I.T.C./Gupta/Bharat upto 40mm dia. 16

SWG and over 40mm dia.	 14 SWG.

17.  DISTRIBUTION BOARDS	:     Gem/KEW/SSK/BPC.

18.  DOUBLE POLE SWITCHES    :     SSK/Standard/Crompton/BPC/Simplex.

19.  TRIPLE POLE NEUTRAL	       : 	GEC/Standard/GemBPC/SSK

SWITCHES

20.  HUME PIPES		       :	Bharat pipes/ Indian hume pipes.

21.  WHITE HYLAM SHEET	:   3MM “HYLAM” printed sheet white colour formica.

22.  MCB BOARD		       :     Moraji Dormans

23.  FANS			       :     Ralli/Crompton/Orient/Bajaj

24.  TUBE LIGHT FITTINGS       : Bajaj/Crompton/Mysore lamps/Phillips.

NOTE :-

The brand indicated above are for cost estimation purpose only.  However the brands of material shall be individually got approved by Engineer-In-Charge before commencement of work.  All materials should be ISI specified.

II. CONDUIT WIRING

- Standards :- The following standards as amended upto date and rules shall be applicable for wiring :-

i.	IS	:	732	-	1963		Code of practice for Electrical wiring

installation (system  voltage not

exceeding 650V)

ii.		IS	:	1646	-	1964		Code of  practice  for  fire  safety  of

buildings (General) Electrical

installation.

iii.	IS	:	1953	-	1964		Rigid steel conduits for electrical

wiring.

Contd.5…

::5::

iv.	IS	:	2667	-	1964		Fittings for rigid steel conduit for

electrical   wiring.

v.	IS	:	3480	-	1966		Flexible steel conduit for electrical

Wiring.

vi.	IS	:	3837	-	1967		Accessories for rigid steel conduit for

electrical wiring.

vii.	IS	:	1554	-			PVC insulated cables.

viii.	IS	:	1087	-			5A, tumbler switches.

ix.	IS	:	2120	-			15A, tumbler switches.

x.	IS	:	1293	-			3 pin plugs and sockets.

- Indian Electricity act and rules are applicable as issued there under  upto date.

3.a. Rigid steel conduit :-  All conduit shall be of Heavy Gauge welded steel, black enameled and shall be of following gauges:-

Upto 	40mm dia	-	16 SWG

Over 	40mm dia	-	14 SWG

b. PVC conduit pipe shall be as per ISI Rules.

- Accessories :

Conduit fittings such as bends, elbows, reducers, chase nipples, split couplings, plugs etc.  shall be specifically designed and manufactured for their particular application.  All conduit fittings shall conform to IS:2667 – 1994 and IS: 3887 – 1996.

- All wires shall be PVC insulated with single core copper or aluminum standard conductors as specified and shall be 650/1100 volts grade.

- All wires shall be colour coded as follows wherever distribution is carried out :

Phase		Colour of wire

R		Red

Y		Yellow

B		Blue

N 		Black

- Installation :

The size of conduit shall be selected in accordance with the IS codes and the minimum size of the conduit shall be 25mm dia. Unless otherwise indicated size of the wire shall be not less than 2.5 sqmm aluminum or equivalent.

Contd.6…

::6::

- Separate conduits shall be used for

- Normal light and 5A, 3 pin sockets.

- Power outlets – 15A, 3 pin

- Emergency light

- Telephones

- Fire alarm

- Layout of conduits shall be generally as indicated in the drawings and the layout shall be supplemented   and complemented by contractor at site with the approval of Engineer-in-charge.

- Wiring for short extension to outlets in hung ceiling or to vibrating equipment, motors etc., shall be installed in flexible conduits.

- Conduits run on surface shall be supported on metal saddles which in turn are properly screwed to the wall or ceiling.  Saddles shall be at intervals of not more than 50cm., fixing screws shall be with round or cheese head and of rust proof material.  Exposed conduits shall be neatly run parallel or at right angles to the walls of the buildings.

- Conduits embedded into the walls shall be fixed by means of staples at not more than 50cm.,  intervals, chase in the walls shall neatly be made and refilled after laying the conduit and brought to the finish of the wall.

- Conduits buried in concrete structure shall be put in position and securely fastened to the reinforcement and got approved by the Engineer-in-charge before the concrete is poured.  Proper care shall be taken to ensure that the conduits are neither dislocated nor choked at the time of pouring the concrete.   Suitable fuse wires shall be drawn in all conduits before they are embedded.

14. Inspection boxes shall be provided for periodical inspection and to facilitate drawal and removal of cables.  Such inspection boxes shall  be flush with the  wall or ceiling in the case of recessed conduits. Inspection boxes shall be spaced at not more than 12 meters apart or  to 90 deg. Solid bends or equal or as directed at site.

15. Conduits shall be free from sharp edges and burrs and shall be free from grease oil. The entire system of conduits must be completely laid without break before the conductors are pulled in. Conduits shall terminate in junction boxes of not less than 32mm deep. Wherever required, deeper junction boxes shall be used.

16. A bare earth wire of not less than 14SWG  Aluminium shall be run in each conduit. The earth wire shall be clamped to the conduit with earth clamps on both sided of the conduit joint.

Wiring:

17. All final branch circuits for lighting and appliances, shall be single conductor and standard cables run inside conduits.

Contd.7

::7::

- The sizes of the branch circuit conductors shall be as shown in the schedule

19. Circuit wiring indicated in the drawings for the final branch circuits shall be kept in a separate conduit  up to the D. B No. other wiring shall be bunched in a separate conduit for each phase.

20. Looping system of wiring shall be used. Wires shall be jointed. Where joints are unavoidable they shall be made through approved mechanical connector.

21. Control switches shall be connected in the phase conductors only and shall be ' ON ' when knob is down. Switches shall be fixed in sheet steel boxes with cover plates as specified. Countersunk wood screws shall be used.

22. Outlets:

All outlets for fittings, switches etc., shall be boxes of suitable metal of either surface mounting or flush mounting system.  Wall  thickness shall not be less than 3.2mm (1/10")  with 3.2mm (1/8") thick perplex sheet in front giving a minimum clear depth of 75mm or above.

23. Power wiring shall be distinctly separate from light point wiring in conduits not less that 25mm and with wires not less than 4 Sqmm Aluminium or equivalent shall be used.

Testing:

24.  The entire installation shall be tested for:

a.  Insulation resistance.

b.  Earth continuity.

c.  Polarity of single pole switches.

d.  Test certificate shall be submitted in the Performa shown under Annexure  -

III.  BATTEN WIRING

1.  Fixing in wall and ceilings:

All PVC sheathed cables on brick walls, stone or plastered walls and ceilings shall be run on wall seasoned, perfectly straight and well varnished on four sides of teak wood or hard wood battens not less than 12 mm (1/2") thick and width batten. Prior to erection these shall be properly secured to the walls and ceilings by counter sunk wood screws on wooden gutties.

2.  Pluging wall : Plugs for ordinary walls or ceilings or ceilings shall be seasoned teak or hard wood of 7.5cm. length  by 2.5cm (1")square on the inner end and 2 cm. (3/4") square on outer end of the surface they shall be cemented into the wall to within 6mm (1/4") of the surface , the remainder being finished according to the nature of the surface with plaster or lime punning.

3.  Any damage to the walls, floors etc, during installation and erection must be repaired by the contractors to match the original  finish, at their own cost.

Contd..8

::8::

4.   Link clips : Only tinned brass clips shall be used. Link clips shall be arranged such that one single clip shall not  hold  more than 3 (three) single core cables. The clips shall be fixed on varnished wooden batten with the nails/pins and space at intervals of 10cm. Both in the case of horizontal and vertical runs. (For the wiring and run of mains exposed to heat and rain, clip specially made for outdoor use from durable metal resistant to weather and atmosphere corrosion shall be used.) Wiring exposed to weather, clips used shall be of out door  type.

5.  Passing through walls : There shall be one conduit for every twin core cable or two runs  of single core cable, and the conduit shall be neatly arranged so that the cables enter them are straight without bending.

6.  Buried cables : The PVC sheathed cables shall not be buried directly in plaster . They may be taken in teakwood channelling of ample capacity or cement chase or conduit pipe buried in the wall.

7.   Stripping of outer covering while cutting and stripping of the outer covering of the cables, care shall be taken that the sharp edge of the cutting instrument does not touch the rubber PVC sheathed insulation of conductors. The protective outer covering of the cables shall be stripped off near connecting terminals as far as practicable. Care shall be taken to avoid hammering on link clips with any metal instruments, after the cable are laid.

8.   Painting : If so required the tough rubber-sheathed wiring shall after erection be painted with one coat of oil-less paint or distamper of suitable colour over a coat of oil-less primer, and the PVC sheathed wining shall be painted with a synthetic enamel paint of quick drying type.

IV. Under Ground Cables

1.  All cables  joints should be in joint boxes and filling the compound shall be done as per IS specifications using the best quality materials . All cables, accessories and other materials shall conform to IS specifications. The joining of cables shall be carried out by a competent authorised cable jointer.

2.  Trench : Trenches should not be less than 45/60cm. wide and 75/90cm below ground level. Where the cables cross other service lines adequate protection should be taken to prevent accidental exposure and /or damage to the cables.

3.  Spacing between cables : Where more than one cable is laid in the same trench the space between the cables shall normally be 23cm. Apart leaving a clear distance of 15cm. from the cable and the trench walls.

Contd..9…

::9::

4.  Laying of cables: Before laying of the cables a layer of 5cm sand face is provided for purpose of cushioning. The cables after being uncoiled systematically and laid in the trench from the rollers should be drawn in straight lengths. After the cable is laid it is to be covered with another layer of sand of about 5cm. in depth and the top surface to be suitably embedded in concrete of 20cm x 20cm x 5cm. and spaced at  a distance of about 30M from centre and at every change in direction. While laying the cables, care should be taken to see that the paper insulated cables are bent straightened slowly and sharp bends avoided. The 20  diameters and for multicore cables 15 diameters and for armoured cables 12 diameters, the diameter being the overall diameter of the cable. Where the cables are required to cross roads this should normally be taken through sleeve pipes at least 10cm in diameter which may be either in stone wear, steel or spun reinforced concrete. Stems pipe shall be used (where it is not possible to obtain sufficient depth to withstand vibrations due to traffic). For crossing the road to give sufficient protection to the cable.

Cables laid inside the buildings should be properly protected and be carried either in ducts with suitable covers with slab or chequered plates or fixed to walls by clamps, brackets or cable trays.

5.	Testing the cables: High voltage test should be undertaken to ensure the damage has occurred during laying and weather the joints  are in order. Cables of 1.1 KV suitable for low and medium voltage should withstand for 15 minutes, 3000 volts D.C.  applied between the conductors and between each conductor and sheath.  In absence of pressure testing arrangement it is sufficient to test for 1 minute with 100 volts. If the test  results are found to be not satisfactory the contractors shall arrange for having this set right at their cost, including removal of rejected materials, relaying etc.

CONTRACTOR (S)								ISSUING OFFICER

|  | BHARAT HEAVY ELECTRICALS LIMITED |  |  |  |  | Tender Notice No. |
| --- | --- | --- | --- | --- | --- | --- |
|  | RAMACHANDRAPURAM :: HYDERABAD-32 |  |  |  |  | HY/TA/OT-03/2006-07 |
|  | (TOWNSHIP ADMINISTRATION) |  |  |  |  | Dated :29.08.2006 |
|  | SCHEDULE "A" (BILL OF QUANTITIES) |  |  |  |  | Part-B Item No.1 |
|  | NAME OF WORK :- Additional & Alterations for Electrical points in general hospital, Bore wells, NRSP & STDP etc. |  |  |  |  |  |
|  |  |  |  | Rate in |  |  |
| S.No | Description of Item | Qty. | Unit | Figures | Words | Amount |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) |
| 1 | Supply and wiring with 1.5 sq.m (22/3 mm) PVC insulated multistandard copper conductor cable run in concealed / surface in rigid PVC conduct pipe 25 mm dia / 1.5 mm thick (Sudhakar make) 14 SWG bare AL. conductor for earth continulty and supply and fixing of 5A 250V piano type switch for controlk of light point of Hylarm sheet of thickness 3 mm prefgerably white with suitable MS box. | 5 Nos | each |  |  |  |
| 2 | Supply and wiring with 1.5 sq.m (22/3 mm) PVC insulated muiltistandard copper conductor cable run in concealed / surface in rigid PVC conduit pipe 25 mm dia / 1.5 mm thick (sudhakar make) 14 SWG bare AL. Conductor for earth continuity and supply and fixing of 5A 250V piano type swith for control of light point on Hylarm sheet of thickness 3mm preferably white with suitable MS box with 5A, 250V ceiling rose on teakwood round block for ceiling fan point and tube light point. | 20 nos | each |  |  |  |
| 3 | Supply and wiring with 1.5 sq.m (22/3mm) PVC insulated multistandard copper conductor cable run in concealed / surface in rigid PVC conduit pipe 25 mm dia / 1.5mm thick (sudhakar make) 14 SWG bare AL conductor for earth continuity and supply and fixing of 2 nos. 5A, 250V two way turmbler / flush type switches for control from two sides on hylam sheet of thickness 3 mm preferably while with suitable MS box for stair case light points. | 1 nos | each |  |  |  |
|  | Signature of Tenderer |  |  |  | Issuing officer |  |

| 4 | Supply and wiring with 1.5 sq.m (22/.3mm) PVC insulated multistandard copper conductor cable run in concealed / surface in rigid PVC conduit pipe 25 mm dia / 1.5 mm thick (sudhakar make) 14 SWG bare AL conductor for earth continuity, supply and fixing of Buzzar / call bell point with 5A, 250V piano type bell push on Hylam sheet of thickness 3 mm preferably white with suitable MS box. | 5nos | each |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 5 | Supply and wiring with 2.5 sq.m (36/.3mm) PVC insulated single core copper conductor multistranded cable together run with 12 SWG bare copper conductor for earth continuity from distribution board to plug point including supply and fixing of 5/15 Amps socket and 15 Amps. 250V switch for control to be fixed on suitable switch board. | 10 nos | each |  |  |  |
| 6a | Supply and wiring with 4/6 sq.m PVC insulated Multistranded copper conductor cable together with 10 SWG bare AL. Conductor for earth contunuity run in concealed rigid PVC conduit pipe (sudhakar make) for run of mains, single phase two wires. | 50 mtrs | One Mtrs |  |  |  |
| b | Supply and wiring with 4/6 sq.m PVC insulated Multistranded copper conductor cable together with 10 SWG bare AL Conductor for earth continuity run in concealed rigid PVC conduit pipe (Sudhakar make) for run of mains for 3 phase (4 wires) of 4/6 sq.m | 50 mtrs | One Mtrs |  |  |  |
| c | Supply and wiring with 10 sq.m PVC insulated Multistranded copper conductor cable together with 10 SWG bare AL. Conductor for earth continuity run in concealed rigid PVC conduit pipe (sudhakar make) for run of mains, single phase two wires. | 10 mtrs | One Mtrs |  |  |  |
| d | Supply and wiring with 15 sq.mm PVC insulated Multistranded copper conductor cable together with 10 SWG bare AL. Conductor for earth continuity run in concealed rigid PVC conduit pipe (sudhakar make) for run of mains, single phase two wires. | 10 mtrs | One Mtrs |  |  |  |
| 7 | Supply and fixing of porcelian base rewireable fuse units. |  |  |  |  |  |
| a | 32A, 250V fuse | 2 nos | each |  |  |  |
| b | 32A, 415V fuse | 6 nos | each |  |  |  |
| c | 63A, 415V fuse | 6 nos | each |  |  |  |
|  | Signature of tenderer |  |  |  | Issuing officer |  |

| 8 | Supply and fixing of 6A-32 Amps, 240V MCB single phase similar to MDS load contract / Load master | 6 nos | each |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 9 | Supply and fixing of BC brass Batten / Slant holder on a teak wood round block | 2 nos | each |  |  |  |
| 10 | Supply and fixing of 5A, 250V ceiling rose | 6 nos | each |  |  |  |
| 11 | Supply and fixing of No.8 SWG bare copper wire. | 6 kgs | One kg |  |  |  |
| 12 | Supply, cutting and fixing of Hylam sheet 3 mm thick for switches and plugs on existing / new MS box with screws and cup washers of suitable size. | 1 Sq.M | One Sqm |  |  |  |
| 13 | Supply and fixing of ceiling fan hooks 10 mm rod in 'S' shape to the ceiling rod including chipping the ceiling with necessary masonry works. | 5 nos | each |  |  |  |
| 14 | Supply of fixing of tubular type heating element suitable for 50 Ltrs. Water heaters threaded type/non-threaded type as per sanmples given : |  |  |  |  |  |
| a | 1000 Watts element | 1 nos | each |  |  |  |
| B | 1500 Watts element | 8 nos | each |  |  |  |
| C | 2000 Wats element | 8 nos | each |  |  |  |
| 15a | Supply and fixing of tubular type heating element 3000 Watts with thermostat provision | 2 nos | each |  |  |  |
| b | Supply and fixing of kettle element 1.25" dia BPC size with cheknut and hylan washers 2 kilo watts. |  | each |  |  |  |
| 16 | Supply and fixing of crimping lugs of following sizes : | 5 nos | each |  |  |  |
| a | lug size 2.5 Sq.mm to 10 Sq.mm | 5 nos | each |  |  |  |
| b | lug size 16 Sq.mm | 10 nos | each |  |  |  |
| c | lug size 25 Sq.mm | 10 nos | each |  |  |  |
| d | lug size 35 Sq.mm | 10 nos | each |  |  |  |

| e | lug size 50 Sq.mm | 10 nos | each |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| f | lug size 70 Sq.mm | 10 nos | each |  |  |  |
| 17a | Supply and fixing of best quality 5A, 250V, 3 pin plug top | 6 nos | each |  |  |  |
| b | Supply and fixing of best quality 15A, 250V, 3 pin plug top | 6 nos | each |  |  |  |
| 18 | Supply and fixing of tubelight fitting side holder/starter basse/side holder base. | 12 nos | each |  |  |  |
| 19 | Supply and fixing of tubelight fitting with Roter looking type holders. | 12 nos | each |  |  |  |
| 20 | Supply and fixing Decolam Boards |  |  |  |  |  |
| a | Board size 4" x 4" | 1 nos | each |  |  |  |
| b | Board size 7" x 4" | 1 nos | each |  |  |  |
| c | Board size 8" x 10" | 1 nos | each |  |  |  |
| d | Board size 10" x 12" | 1 nos | each |  |  |  |
| 21a | Supply and fixing of buzzer to be fixed on 7"/4" Teakwood board. | 2 nos | each |  |  |  |
| b | Suppy and fixing of call bell on a suitable Teakwood board. | 2 nos | each |  |  |  |
| 22 | Suppy and fixing of piano switch 5A, 250V of reputable make. | 6 nos | each |  |  |  |
| 23 | Supply and fixing of BC night lamps 15 W, 250 V. | 6 nos | each |  |  |  |
| 24 | Supply and fixing of TL starter 20W-40W-65W-80W,250V. | 10 nos | each |  |  |  |
| 25 | Supply and fixing of 4' 36/40 W tube light make Bajaj/philips. | 6 nos | each |  |  |  |
|  | Signature of Tenderer |  |  |  | Issuing Officer |  |

| 26 | Supply and fixing of 4' 36/40 W tube light make Bajaj/philips. | 4 nos | each |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 27 | Supply and fixing of 40 watts copper ballast choke make philips/bajaj. | 6 nos | each |  |  |  |
| 28 | Supply and fixing of 65/80 watts copper ballast choke make philips/bajaj. | 3 nos | each |  |  |  |
| 29 | Supply and fixing of ermegency lamp dry cell 6 Volts 10 AH rechargable maintenance free battert. | 12 nos | each |  |  |  |
| 30 | Servicing of storage type water heaters, work involves cleaning of chocked tubes inside the tank, replacement of gaskets, elements, thermostat including dismanting and refixing back. | 6 nos | each |  |  |  |
| 31 | Removal of MS rod from ceiling and fixing of 4'/5' tube light fitting to down rods with suitable MS clamps to provide ceiling rose on Teakwood round block. (The work inlcudes dismantaling of fittings removal of existing gutties, clamos, bolts & nuts. | 6 fittings | each fittings |  |  |  |
| 32 | Supply and fixing of box type flourescent tube light fitting (5) 1 x 80W switch start, stove enamelled complete with all acessories inclusive of starter, ballast, PF correction capacitor lamp holder, together with tube lamp similar to BJR-180 Crompton /Philips & Glolite. | 1 nos | each |  |  |  |
| 33 | Supply and fixing of 32A. 250V MS sheet steel DP main switch with rewirable porcelain fuse each 3 units for controlling incomming supply of reputable make. | 1 nos | each |  |  |  |
| 34 | Supply and fixing of 3 pahse 32A, 415V TPN main switch. | 1 nos | each |  |  |  |
| 35 | Supply and fixing of 63A ICTPN switch for controlling incomming supply. | 1 nos | each |  |  |  |
|  | Signature of Tenderer |  |  |  | Issuing Officer |  |

| 36 | Supply, fabrication & fixing of MS sheet cupboards with single/double shutter and mechanical looking arangements. The cupboards shall be given 2 coats oif red oxide paint and finished with necessary general purpose quick drying oil paint of suitable shade as directed | 125 kgs | each |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 37 | Supply and fixing in wall of angle iron frame of suitable size for mounting main switch and DB IC cut-outs and meter etc., The frame shall be semi-flush mounted and shall be fixed with 1/1.6mm thick MS sheet on top and all four sides. All accessories should be mounted on top sheet and hinged to the frame at one and fixed with screws on the other end. The frame shall be gisven two coats of red-oxid4e paint and finished with admiral grey paint. | 75 kgs | each |  |  |  |
| 38 | Supply and fixing of Air break contactor 3TA11 11-0 Amps, rated current 22 Amps 1NO+1NC 11KW, 15HP, 415V. (Seimens make) | 1 nos | each |  |  |  |
| 39 | Supply and fixing os pare coils AC 50 cycles suitable for 3TA 76/3TA67/3TA11 standard 415 V. | 2 nos | each |  |  |  |
| 40 | Laying of PVC insulated PVC sheathed Armoured cables Aluminium & connecting the same to the switches (cable will be supplied departmentally) |  | each |  |  |  |
| a | 2.5 sq.mm to 6 sq.mm cable | 20 Mtrs | One Mtrs |  |  |  |
| b | 10 sq.mm to 35 sq.mm cable | 200 Mtrs | One Mtrs |  |  |  |
| c | 50 sq.mm to 95 sq.mm cable | 50 Mtrs | One Mtrs |  |  |  |
| 41 | Earth work excavation of cable trenches of size 0.6mm width and 0.9 m deep in all soils requiring blasting and also refilling the treches with excavated soils. | 200 Cu.m | One Mtrs |  |  |  |
| 42 | Supply and spreading of sand cushin 10cm thick all aorund the cablke and lying of rough shahabad sone of size 300x300x30mm over the cable. | 200 Mtrs | One Mtrs |  |  |  |
|  | Signature of tenderer |  |  |  | Issuing officer |  |

| 43 | Providing Earth plt as per IS:3043 | 6 nos | each |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 44 | Supply and fixing 12 way Amps. 600 V Bakelite with brass terminal connectors. | 20 nos | each |  |  |  |
| 45 | Supply and fixing of voltmeter 0 to 500V 22" dia. Round flush type. | 1 nos | each |  |  |  |
| 46 | Supply and fixing of Ammter 0 to 30 Amps. 22" dia round flush type. | 6 nos | each |  |  |  |
| 47 | Supply and fixing of timer switch type TSQ-100 make Larsen & Turbo ltd. | 6 nos | each |  |  |  |
| 48 | Supply & errection of street light fitting including street light bracket G1 peipe 32mm dia and length 1.5 Mtrs. The street light fittings shall be similar to Bajaj make model No. BJSLA 240 including all standard accessories and 2 Nos. 4' flourscent tubes and shall be fixed with MS falt clamps and with 15 A rewriable porcelain fuse unit | 1 nos | each |  |  |  |
| 49 | Supply and wiring as item no.1 and with 2/3 pin flush mounted multipurpose plug socket and 5A 250V piano type switch for contr9ol to be fixed on common switch board. | 5 nos | each |  |  |  |
| 50 | Supply and fixing of 6-32 Amps MCB distribution board with sheet steel encloser three phasse 6 way similar to MDS load contact including 63/100 Amps Isolator 415V. | 3 nos | each |  |  |  |
| 51 | Supply and fixing of MDS legrand single dia. A/c box (for General Hospital are conditioners). | 50 nos | each |  |  |  |
| 52 | Supply and fixing of sheet steel distribution board 16 a 240 V 8 way single phase.16, 240V. | 4 nos | each |  |  |  |
|  | Signature of tenderer |  |  |  | Issuing officer |  |

|  | Conditions |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | A penality of 0.50% of the gross value of work will be levied for every week's delay of work subject to a maximum penality of 10% of the gross value of work. |  |  |  |  |  |  |  |
| 2 | If the contractor has not quoted the % age clearly, it is considered as a incomplete tender and tender cannot be accepted. |  |  |  |  |  |  |  |
| 3 | All BHEL general conditions of contract and special conditions enclosed to this document are applicable to this work. |  |  |  |  |  |  |  |
| 4 | In case there is any difference in the quoted % age between figures and words, the resultant higher tender value will be taken for evaluation of tender priority and while awarding lower tender value will be taken and this should be binding on the contractor |  |  |  |  |  |  |  |
| 5 | The department reserves the right to cancel the work without assinging any reasons therefor. |  |  |  |  |  |  |  |
| 6 | The agency shall provide approved uniform two pairs per year, and one pair shoes, cap and identity badges to all of his workers while they are working for the purpose. |  |  |  |  |  |  |  |
| 7 | The scope of agency is to provide all the tools, PPES and the required chemicals, detergents, brooms, brushes, sponges, cloth, equipments for the full operations for completion as specified and as directed by the Engr-in-charge. |  |  |  |  |  |  |  |
| 8 | The billing is done as per the units specified and completion to the satisfaction of Engr-in-charge. Proportionate recovery will be made for work not done. |  |  |  |  |  |  |  |
| 9 | The quantities indicated are approximate and liable for variation. The tenderer has to accept the variations in quantities. |  |  |  |  |  |  |  |
| 10 | Conditional offers are not acceptable. |  |  |  |  |  |  |  |
| 11 | The work force employed shall have license from Govt. of AP/Tech, Educational Board / AP Electrical License Board. |  |  |  |  |  |  |  |
|  | SIGNATURE OF TENDERER |  |  |  | ISSUING OFFICER |  |  |  |