## Sheet1
Internal Electrical Power Distribution (Part B - A7, A8 & A9 ) of 800 / 1000 MW T/G Test Facility.
Package - 1
SECTION-1 (SCOPE) : Design, Supply, Erection, Testing and Commissioning of the following - ANNEXURE-1 (Sheet 1/5)
Sl.No. | Item Description | Make | Unit | Qty | Unit Ex- | Total Ex- | Total Freight | Unit Tax
1 | VACUUME SWITCH GEAR PANEL (Marked as P-1 in SLD Drg. No.TGE-2386,Rev-01) : 6.6 kV, 31.5 kA for 1 Sec., SINGLE COPPER BUS INDOOR VCB SWITCHGEAR PANEL : Following VCBs of Incoming and Out Going feeders of different capacity shall be provided with suitable CTs for Protection & Metering, incorporating indicating lamps, control switch, protective relays for over current & earth fault (static Relays) and other auxiliary relays for anunciation & alarm purpose (suitable for supply voltage 110 VAC from PT and control voltage 110 VDC from battary bank). Degree of protection shall be of IP-54. Panel shall be fabricated of CRCA Sheet Steel. Applicable Standadrs for Panel IS:3427, IEC 298, BS 5277, VDE 0670 with upto date ammendments. | ABB, SIEMENS, AREVA AND L&T | SET | 1 | 0 | 0 | 0 | 0
(a) INCOMER FEEDER : One Incomer of 2500A with PT (6.6KV/110 Volt) and suitable bus-chamber for termination of 9 Nos. XLPE Cable of Size 3x300 Sq.mm. and Power meter with accuracy of Class 0.5, featuring KW, KVA, KVAR, KWH, KVAH, KVARh, Frequency, Voltage, Current, Power Factor.
(b) OUT GOING FEEDERS (TOTAL FOUR) : with suitable indications and Digital Ammeters
(b-1) One No. 2500A with suitable bus-chamber for termination of 6 Nos. XLPE Al.Cable of Size 3x300 Sq.mm.
(b-2) One No. 2000A with suitable bus-chamber for termination of 12 Nos. XLPE Al.Cable of Size 1x630 Sq.mm.
(b-3) Two Nos. 600A with suitable bus-chamber for termination of 2 Nos. XLPE Al. Cable of Size 3x300 Sq.mm.
2 | VACUUME SWITCH GEAR PANEL FOR CORE LOSS TEST(Marked as 3 in SLD Drg. No.TGE-2386 , Rev.01) : 600 A, 6.6 KV, 31.5 kA for 1 Sec., with one PT (6.6KV/110 Volt) and suitable CTs for Protection & Metering, incorporating indicating lamps, control switch, protective relay for over current & earth fault (static Relay), under voltage relay and other auxiliary relays for anunciation & alarm purpose.Degree of protection shall be of IP-54, Panel shall be fabricated of CRCA Sheet Steel. Applicable Standadrs for Panel IS:3427, IEC 298, BS 5277, VDE 0670 with upto date ammendments. Seperate bus chamber shall be provided to terminate 2 Nos. XLPE cables of size 3x300 Sq.mm at Incoming side and 2 Nos. XLPE cables of size 3x300 Sq.mm at outgoing side . (This switchgear panel has to be installed at different location). | ABB, SIEMENS, AREVA AND L&T | Nos. | 1 | 0 | 0 | 0 | 0
3 | HT XLPE CABLE : 6.6 KV (E), Aluminium Conductor, 3X300 Sq.mm XLPE Cable with round Steel Armouring AS PER IS 7098 PART -2 1985 with upto date Ammendments. (Required Lengths : 4 Nos. Drum each of single length of 350 meter, 2 Nos. Drum each of single length of 400 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour) (from P1 Panel to different locations) | CCI, UNIFLEX, RPG, TORRENT, UNIVERSAL | Meter | 2200 | 0 | 0 | 0 | 0
4 | LT POWER CABLE : 1.1 KV (UE), PVC Insulated, Copper Conductor 1x630 Sq.mm Cable with round Aluminium Armouring as per IS 1544 (1/ 1988) with upto date Ammendments. Cable shall be laid in trifoil formation fixed with non magnetic clamps on cable racks. (Required Lenght : 8 Nos. Drum each of single length of 200 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour) (from 8.6 MVA, 6.6 KV/ 881 Volt Transformer to Rectifier Unit and to Exciter of T/G) | --do-- | Meter | 1600
Contd…..2….
---- 2 ----
ANNEXURE-1 (Sheet 2/5)
Sl.No. | Item Description | Make | Unit | Qty
5 | HT XLPE CABLE : 6.6 KV (UE), Aluminium Conductor, 3X300 Sq.mm XLPE Cable with round Aluminium Armouring AS PER IS 7098 PART -2 1985 with upto date Ammendments. (Required Lengths : 14 Nos. Drum each of single length of 350 meter, 8 Nos. Drum each of single length of 300 meter and 6 Nos. Drum each of single length of 200 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour) (P2A & P2B Panel to Motors at 03 Locations) | --do-- | Meter | 8500
6 | HT XLPE CABLE : 6.6 KV (E), Aluminium Conductor, 1X630 Sq.mm XLPE Cable with round Aluminium Armouring AS PER IS 7098 PART -2 1985 with upto date Ammendments. Cable shall be laid in trifoil formation fixed with non magnetic clamps on cable racks. (Required Lengths : 9 Nos. Drum each of single length of 200 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending orde in white colour) (P1 Panel to Old Test Bed through Reactor) | --do-- | Meter | 1800
7 | LT POWER CABLE : 1.1 KV (E), PVC Insulated Aluminium Conductor, 3X300 Sq mm Cable with round steel Armouring as per IS 1544 (1/ 1988) with upto date Ammendments. (Required Lengths : 1 No. Drum of single length of 450 meter, 1 No. Drum of single length of 350 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour) (from VFD to Brushless Eciter of Drive Motor at three different locations) | --do-- | Meter | 800
8 | LT POWER CABLE : 1.1 KV (E), PVC Insulated Aluminium Conductor, 3.5X300 Sq mm Cable with round steel Armouring as per IS 1544 (1/ 1988) with upto date Ammendments. (Required Lengths : 2 Nos. Drum each of single length of 450 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour) (from 3 MVA transformer Sub-Station to LT Panel in Machine Hall) | --do-- | Meter | 900
9 | LT POWER CABLE : 1.1 KV (E), PVC Insulated Aluminium Conductor size 3.5x50 Sq.mm Cable with round steel Armouring as per IS 1544 (1/ 1988) with upto date Ammendments. (Required Lengths : 1 No. Drum of single length of 200 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour) (from AC supply to Battery Charger) | --do-- | Meter | 200
10 | JOINTING KIT :HEAT SHRINKABLE END TERMINATION KIT SUITABLE FOR 6.6 KV, 3x300 SQ MM CABLE. | RAYCHEM | Nos. | 250 | 0 | 0 | 0 | 0
11 | JOINTING KIT :HEAT SHRINKABLE END TERMINATION KIT SUITABLE FOR 6.6 KV, 1x630 SQ MM CABLE. | RAYCHEM | Nos. | 90
12 | L.T. DISTRIBUTION PANEL : | ABB, SIEMENS, AREVA AND L&T | SET | 1
(a) ONE INCOMER (800A) Air Circuit Breaker, Draw Out type Electrically & Mechanically operated with Over Current & Earth Fault Protection (Micro Processor Based) with suitable CTs incorporating indicating lamps, control switch with Voltmeter and Ammeter (with selector switch). Degree of protection shall be of IP-54. Panel shall be fabricated of CRCA Sheet Steel. Applicable Standadrs for Panel IS:3427, IEC 298, BS 5277, VDE 0670 with upto date ammendments.
(b) OUT GOING FEEDERS (TOTAL FOUR) :
(b-1) Two Nos. 3 phase, Switch fuse unit of 250A.with HRC fuses
(b-2) Three Nos. 3 phase, Switch fuse unit of 100A.with HRC fuses.
Contd…..3….
---- 3 ----
ANNEXURE-1 (Sheet 3/5)
Sl.No. | Item Description | Make | Unit | Qty
13 | 110 Volt D.C. SUPPLY : |  |  |  | 0 | #VALUE! | #VALUE! | 0
13.1 | D.C. Distribution Board : 110 V, 300A, having capacity of Out going Feeders controlled with 2-pole MCBs for 60 Amp. - 3 Nos., 30 Amp. - 3 Nos., 20 Amp. - 3 Nos. | ANY REPUTED MAKE | No. | 1
13.2 | Batteries : High Performance Plante Lead Acid Stationery Cells (Transperent plastic mould boxes), 2.0 Volt Unit, 300 AH, with plante positive plates & negative plate, Lids, Vent plugs, buffers, Porvic separaters, inter cell connectros, fastners, along with Electrolite, support structure, insulators, electrolite of specific gravity 1.2 in seperate containers and other accessories required including erection & commissioning of the 110 Volt Battrey Bank. Dry & uncharged. As per IS:1652/1991 with upto date ammendments. | EXIDE PLANTE OR OTHER REPUTED MAKE | No. | 60
13.3 | Battery Charger : Battery Charger with boost and trickle charging arrangement and suitable for 110 Volt, 300 AH Battery Bank, along with Ammeter & Voltmeter with selector switch, indication Lamps, Fuses and other required accessories complete in all respect. | --do-- | No. | 1
14 | UPS (Uninterrupted Power Supply) : Double Conversion Online UPS for continuous use, of rated capacity of 4KVA, 240 Volt AC, Maximum Backup time - 01 Hr., with Exide Make batteries with stand and other accessories required for commissionimng. | Luminous, Su-kam, Microtek etc. | No. | 1
14.1 | Input : Nominal Input Voltage: 230 V 50 Hz +/-5 Hz, Input Connection: Hard Wire 5-Wire (3Phase + Neutral + Ground), Input Voltage Range: 160-280 V.
14.2 | Output : Output Power Capacity: 4 KVA, Output Voltage : 240 V AC single phase configurable, Output Voltage Distortion: < 3 %, Output Frequency: 50 Hz +/- 0.1 Hz, Output Connection: Hardwire 3-Wire (1 Phase + Neutral + Ground), Efficiency at full load: 90%, Bypass: Automatic as well as Manual. UPS should ensure continuous power supply in the event of electronic failure / overload / scheduled maintenance, Overload Capacity: 105% - Infinite, 125% - 1 minute, 150% - 30 seconds.
14.3 | Batteries : Sealed Maintenance Free Lead-Acid with leak proof suspended Electrolyte, typical 3-6 years lifetime, Recharge Time: 90% charging within 3 hours, Battery Cabinet: Batteries should be in proper separate enclosure.
14.4 | UPS Status Display : LED display for load and battery bar graph, On-Battery, Replace-Battery, Overload and Bypass Indicators, Audible Alarm: Continuous Alarm when on Battery, Low Battery Alarm, Overload Alarm.
14.5 | Conformance : C-tick, EN 50091-1, EN 50091-2, EN 55022 Class A, EN 60950, EN 61000-3-2, GOST, PCBC, VDE
15 | 24 Volt D.C. SUPPLY :
15.1 | D.C. Distribution Board : 24 V, 100A, having capacity of Out going Feeders controlled with 2-pole MCBs for 50 Amp. -2 Nos. | ANY REPUTED MAKE | No. | 1
15.2 | Batteries : High Performance Plante Lead Acid Stationery Cells (Transperent plastic mould boxes), 2.0 Volt Unit, 300 AH, with plante positive plates & negative plate, Lids, Vent plugs, buffers, Porvic separaters, inter cell connectros, fastners, along with Electrolite, support structure, insulators, electrolite of specific gravity 1.2 in seperate containers, and other accessories required including erection & commissioning of the 24 Volt Battery Bank. Dry & uncharged. As per IS:1652/1991 with upto date ammendments. | EXIDE PLANTE OR OTHER REPUTED MAKE | No. | 12
Contd…..4….
---- 4 ----
ANNEXURE-1 (Sheet 4/5)
Sl.No. | Item Description | Make | Unit | Qty
15.3 | Battery Charger : Battery Charger with boost and trickle charging arrangement and suitable for 24 Volt, 300 AH Battery Bank, along with Ammeter & Voltmeter with selector switch, indication Lamps, Fuses and other required accessories. | --do-- | No. | 1
16 | D.C. ISOLATORS (Marked as 5 in SLD Drg. No.TGE-2386 , Rev.01) : D.C. DOUBLE POLE ISOLATORS suitable to withstand continuous current of 5000 A, 881 Volt DC. Both the Isolators shall be placed side by side with same facing and shall have a common incoming bus for termination of 5 Nos. copper cables of size 1x630 Sq.mm. on +ve Bus and 5 Nos. copper cables of size 1x630 Sq.mm. on -ve Bus. Both the Isolators should have outgoing terminals seperately for termination of 5 Nos. copper cables of size 1x630 Sq.mm. on +ve and 5 Nos. copper cables of size 1x630 Sq.mm. on -ve from each Isolator (Same power shall be transmitted to two different places from either of the Isolators at a time).these Isolators shall be mounted on suitable foundations as per foundation drawing given by you. | ANY REPUTED MAKE | No. | 2
17 | COPPER BUS BAR ARRANGEMENT FOR FIELD EXCITATION OF TURBO-GENERATOR (Marked as 6 in SLD Drg. No.TGE-2386 , Rev.01): Copper Bus of 5000 A, 881 Volt, having provision for connection of 5 Nos. copper cables of size 1x630 Sq.mm. on +ve and 5 Nos. copper cables of size 1x630 Sq.mm. on -ve at Incoming side and similarly for connection of 5 Nos. copper cables of size 1x630 Sq.mm. on +ve bus-bar and 5 Nos. copper cables of size 1x630 Sq.mm. on -ve bus-bar at Outgoing side with required support insulators, clamps, connectors copper cable lugs and hardware etc.. This total arrangement shall be made at two different locations | ANY REPUTED MAKE | sets | 2
18 | REACTOR(Marked as 2 in SLD Drg. No.TGE-2386 , Rev.01) : 1000A, 6.6 KV, Air cooled REACTOR, 10% Reactance, with provision of bus-bar with support insulators,. connectors and accessories etc.for connection of 3 Nos., 1x630 Sq.mm. cable at Incoming and Out going of each reactor. The reactor shall be complete in all respect. | ABB, SIEMENS, AREVA AND L&T OR OTHER REPUTED MAKE | Nos. | 3
19 | UPGRADATION OF DC DISTRIBUTION IN MACHINE HALL BASEMENT( Refer Drg.No.TGE-2387) : |  |  |  | 0 | 0 | 0 | 0
19.1 | REPLACEMENT OF EXISTING D.C. DOUBLE POLE ISOLATOR, CAPACITY 3000 A, 800 VOLT with new 4000A, 800 Volt D.C. DOUBLE POLE ISOLATOR including support insulators, clamps, connectors and hardware etc. to be fitted in the space available for existing Isolator of 3000 A. | ABB, SIEMENS, AREVA AND L&T OR OTHER REPUTED MAKE | Nos. | 2 | 0 | 0 | 0 | 0
19.2 | REPLACEMENT OF EXISTING D.C. DOUBLE POLE BREAKER, CAPACITY 3000 A, 800 VOLT with new 4000A, 800 Volt D.C. DOUBLE POLE BREAKER including support insulators, clamps, connectors and hardware etc. suitable for control supply of 230 Volt DC,to be fitted in the space available for existing Isolator of 3000 A. | --do-- | Nos. | 2 | 0 | 0 | 0 | 0
19.3 | ONE NO. ALUMINIUM ADDITIONAL BUS-BAR OF SIZE 120X10 SQ MM HAS TO BE INSTALLED ON EXISTING THREE NOS. BUS BAR OF SIZE 120X10 SQ MM TO INCREASE CURRENT RATING FROM 3000 A TO 4000 A. This should be provided with required support insulators, clamps, connectors and hardware etc. | --- | Meter | 400 | 0 | 0 | 0 | 0
20 | CONTROL CABLES :- |  |  |  | 0 | #VALUE! | #VALUE! | 0
20.1 | 1.1 KV (E), PVC Insulated Flexible Copper Conductor, 6X1.5 Sq mm Cable with round steel Armouring as per IS 1544 (1/ 1988) with upto date Ammendments. (Required Lengths : 2 No. Drum of single length of 500 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour) | CCI, UNIFLEX, RPG, TORRENT, UNIVERSAL | Meter | 1000 | 0 | #VALUE! | #VALUE!
Contd…..5….
---- 5 ----
ANNEXURE-1 (Sheet 5/5)
Sl.No. | Item Description | Make | Unit | Qty
20.2 | 1.1 KV (E), PVC Insulated Flexible Copper Conductor, 12X1.5 Sq mm Cable with round steel Armouring as per IS 1544 (1/ 1988) with upto date Ammendments. (Required Lengths : 2 No. Drum of single length of 500 meter) (Cable shall be supplied with per meter lenght marking on cable it self in ascending order in white colour). | CCI, UNIFLEX, RPG, TORRENT, UNIVERSAL | Meter | 1000
21 | EARTHING :
21.1 | Earth Pits :Earth pits shall be made as per requirement of the site and shall be made as per IS. | --- | Nos. | 50
21.2 | Earth connection from earthing pit to control room and cable trench with M.S flat of size 65 x 10 mm duly painted with black paint. | --- | Meter | 200
21.3 | Double earth connections shall be provided for all the equipment installed in this project with GI flat.of (size 50 x 6 mm) | --- | Meter | 1000
NOTES :-
1. Supply of structure if any & other consumables like nuts & bolts for foundations and other equipments, clamps, connectors, fuses, lugs( Copper/ Alluminium as per cables) of different sizes for connection of cables in panels or any other instruments/machines required for the erection, testing & commissioning of the above project shall be in the scope of bidder.
2. Power supply of 415 Volt AC shall be available free of charge for the purpose of erection and commissioning .
3. Supply of the Copy of Type test certificate on similar equipment and routine test certificate of the equipment supplied ( In original and one photo copy) and O&M manual (3 sets) for individual equipment shall be in the scope of bidder.
4. All Foundation drgs, G.A. drawings, schemetaic diagrams, Cable Schedule , layouts of Power transformers and HT Panels, Cotrol & relay panels and other equipments for wiring scheme and foundations etc. shall be in the scope of bidder.
5. Plan, sections, layout for Transformer and other equipments and Cable etc., cable schedule, earthing layout, schematic diagram to be provided for approval from BHEL by the party well before the start of installation work.
6. Party has to arrange approval of drawings inspection for the above Project before commissioning of the system from Central Electrical Authorities/Inspectorate.
7. Detail designing of the project shall be done by the party and shall take the approval from BHEL.before start of work.
8. All the Control wiring shall be carried out with 1.1KV grade of standard flexible copper wire, PVC insulated. For CT & PT circuit the wire size shall be 2.5 Sq.mm. and other circuit shall be with 1.5 Sq.mm copper wire.
9. If required, Supplier may visit the site for assessment of the work.
BHEL, Haridwar Scope of Work :
1. Excavation & levelling of site, if required.
2. Preperation of Equipment foundations, cable trenches, oil soak pits etc., however the drawings shall be prepared by the supplier and got approved from BHEL and be submitted for making the foundations.
3. Electrical power & water supply will be provided free of charge for construction work.