BROAD SPECIFATION OF OXYGEN PLANT CAPACITY 80 M3/Hr

Supply, Installation, Commissioning & Testing of Two number complete energy Efficient Oxygen Gas Plant with all accessories, drive motor, 440 volt AC 50 c/s, control panel, chilling plant, etc. having each of capacity 80 m3 / Hr and Purity of oxygen 99.6%.

Quantity – 2 nos.                   Lot – 1                Delivery – 30-10-2007

Detailed specifications and other conditions of requirement are as per enclosed Annexure I.

1/11

Annexure –I

# SPECIFATION OF 80 M3 PER HOUR OXYGEN PLANT

- Requirement

Two no, Identical Oxygen Gas Plant based on most modern and proven design conforming to latest technology and standards are required for supplying oxygen gas on continuous basis.

- The Offer

The offer for Oxygen Plant must be furnished with complete technical information, design and technical parameters, constructional, dimensional and operational details, safety interlocks, layout plan etc. along with point to point detail reply as required in following. The offer must be in two parts, (a) Techno- Commercial bid and (b) Price bid, each sealed in separate envelope. The incomplete offer will not be considered. The commercial offer must be clearly indicated item-wise breakup of price in relation to scope of supply / work.

- Selection Basis

The selection of Oxygen Gas Plants will be done on the basis of overall merit viz. Operational ease, full load and part-load efficiency, operational economics, maintenance aspects and suitability of Oxygen Plant for long running stretches.

- Technical Specifications of the Oxygen plant detailing for scope of supply :-

BHEL requirement is for two numbers Oxygen Gas plants each of the capacity 80 m3 / Hr having Purity of   oxygen 99.6%.

4.1.   Suction Filter Air Intake- M.S. Vessel consists   of   perforated sheet

covered with  Wire Mesh.  This assists in removing dust from air before

suction to air  Compressor.

4.2.   Air Compressor - Reciprocating multistage horizontal, positive

Displacement, piston type with Inter-coolers, Electric Motor and Starter

Including flywheel, Foundation Bolts, Motor Pulley, V-belts, Belt Guard,

Slide Rails for the Motor, Compressor should be of Ingersoll Rand (India)

2/11

  - After Cooler of the Air compressor - M. S. High Pressure Cooler

Consisting of M.S.  High Pressure Tube Bundle submerged in cold

Circulating water.

4.4    Moisture Separator – 2 Nos. - This should be a cylindrical shape vessel

made of M.S. duly fitted with  drain  valves  for removal of moisture

present in the  process air path.

  - Cascade Air Cooler - This should be designed in to a vessel consisting of   High Pressure air cooling coils in two separate chambers. The process air should be allowed to pass trough the coils of the Cooler. This should be cooled down through water and incoming Nitrogen from the Air separation units. These coils should be immersed in water with a water level indicators facility.

4.6   Activated Carbon / Alumina Filter - This equipment is required

of Mild Steel  in cylindrical shape vessel  having activated carbon

& Alumina inside along with sand filters. The necessity is for the

absorption of Hydro-  Carbons in the process of the  air.

4.7  Molecular Battery -   Should filled with  Molecular sieve type  13X

(Imported)  heaters for  regenerating.(It absorbs moisture, CO2, traces of

Acetylene and other hydrocarbons.)

4.8  Ceramic Filter - This equipment  should be of   Mild Steel and in

cylindrical shape. The micro ceramic filter should be needed to avoid the

entry  of  the dust in side of the  Air Separation unit of the Oxygen plant.

4.9   Expansion Engine – Should be a vertical reciprocating machine for

Expanding air from pressure operating pressure to  5 kg / cm2.

Complete with Fly Wheel, Pressure Gauges, Motor, Motor Pulley, V-belts,     starter cable etc. The Belt Guard, Inter-connecting Copper Pipes and bursting disk for safety should also be taken care.

4.10. Cold  Box  - The Cold Box should consists of Air Separation Column  with

Heat Exchangers for heat transfer between the incoming air and the out

going cold  Nitrogen  and  Oxygen.  Cold Box should be equipped   with

expansion valves for controlling the operation of  the Plant  and  delivery

of the oxygen . Cold Box internal parts should be   made of Stainless Steel

3/11

duly argon welded wherever needed . The other internal parts i.e. copper

piping etc should also brazed & soldered for leak proof operation. The

cold box should  be insulated with perlite insulation powder. The

Control Panel should be equipped with temperature controlling system, on

line oxygen gas purity analyzer,Co2 analyser, Nirogen gas purity

analyzer. The  defrost  heater should  have ‘automatic temperature control

system’   for Defrosting of the Cold Box.

  - Liquid  Oxygen Pump -  Should be  designed for single cylinder

pumping facility  which   will fill bone  dry Oxygen  into cylinders up to  max 160 kg/cm2 pressure.  The Pump should be supplied with                                   suitable Motor, Pulley, & V- belts, belt guards & starter cable etc.

4.12   (a)  Gas/Air Lines - Pipelines  for  the  Process  Air, Nitrogen and Oxygen

as per  standard Layout should be needed.

(b)  Filling Manifolds, Gauges, Valves, Indicators, Safety Devices, and

Testing Kit etc shall also be part of supply.

  - Insulation – The Insulation wool with wire mesh, GI sheeting for insulation of cascade Cooler, Alumina Filter, Molecular Battery, Pipelines etc shall be a   part of supply.

  - Water Cooling System: - Cooling towers (one standby 100 %), suitable capacity pumps (one standby 100 %), along with motors, starter panel , suitable length and size of the pipe line, valves, temperature & pressure gauges and all other equipment required for efficient cooling system appropriate for  both the Oxygen Plants each of  80 Cu. M. capacity.

  - Chilling Unit: - It should design to control the inlet air temperature before Air Separation Unit automatically in between 10 *C to 20*C.

5.   Ambient Conditions at site for installation & designing  of oxygen plants :-

a. Temperature            : 50 *C Max.

b. Relative humidity   : 95% max.

4/11

6.   Details to be furnished by Manufacturer:-

    - Discharge Out put of oxygen plant per hours.

    - Specific power consumption at rated per cubic meter of oxygen Gas

    - Purity of oxygen Gas.

    - Lube oil consumption in compressor, expansion engine.

    - Vibration level of the compressor at a distance of one meter

- Designing condition for Air Compressor of the oxygen plant:-

  - One Compressor on each unit is to be design for continuous services at a stretch. The compressor must be capable for round the clock uninterrupted services and the supplier must specify the minimum period between the two overhauls of the compressor.

  - Selection of the Compressor must be maintenance friendly.

  - Noise level of combined unit (compressor and drive motor) should be less than 90 dbA at a distance of one Meter from the equipment without use of sound attenuation hoods on the compressor.

  - Heat exchangers shall be constructed to allow their removal with minimum dismantling of piping or compressor components. Inter coolers and after coolers should be provided with automatic drain valves for removal of condensed moisture.

  - Selection of the compressor unit should be of M/s Inger-soll Rand (India) Limited,

8.  Air Flow meter

Rate of Air Flow meter should be provided on each Oxygen Plant air path.   It should be highly reliable and capable for continuous monitoring of the compressor performance and analyzing of the likely faults in day to day performance. The installation and commissioning of the flow meters shall be in scope of Oxygen Gas Plant supplier.

9.  Electrical and Control Panel with switchgear and protection, indication, fuse unit volt meter ammeter etc suitable for operation of individual Oxygen Plant:

  - All electrical equipment shall be designed for in door   installation.

5/11

  - Compressor and main motor drive should be suitable for 440V,

3 Phase wire with neutral, 50 +/- 5%, Hz power supply variation.

  - Main motor shall be squirrel cage induction CACA type with

IP 55 protection and designed as per IS-325 or equivalent    international standard. It shall have class 'F' insulation with class 'B' temperature rise at an ambient of 45 Degree C. Bearing and winding temperature RTD should be provided and their values should appear on control panel.

  - Motor rating should be based on the rated shaft power drawn by

the compressor plus 10% margin over the rated shaft power.

  - All the motors should be of reputed make like Siemens/      Crompton /AEI / Kirloskar/ and shall be supplied with the starting panel.

  - Starting panel of main motor should have following features:-

              - Starter should be star delta fully automatic suitable for 440 power supply. This should be of L&T, Siemens, cutler Hammer etc.

b. On, off and Trip indication & remote control switching arrangement should be available,

- Digital motor protection relay for complete safety of motor.

- Starting interlock with panel isolator,

- Door interlock with 440 Volt power supply.

  - All the electrical interconnecting cables and wiring should be    Multi strand copper, insulated and to be supplied with the compressors. Both end of wiring should be provided with     crimped terminals and numbered ferrules. The same numbers should appear on electrical diagrams.

  - Control panel :

a.. Control system should be microprocessor based with     automatic  control providing complete integration of compressor, motor and auxiliaries.

b.  The controller should be allowed complete adjustment of all parameters. Alarm limits and trip set points from the data input device provided on the panel. It should have self-diagnostic feature.

c.  The Controller shall have all motor protection functions and  shall automatically record the energy consumption.

6/11

d.   Alarms and Trips facility

The controller should continuously monitor the following

Parameters (even when compressor is not running) and alert the

Operator when fault occurs.

Parameters                         Alarm                 Trip

- Low cooling water flow           x                        x

- Low bearing oil pressure          x                        x

- Low bearing oil temp.	              x                         -

-         High bearing oil temp.            x                        x

-         High air discharge Temp.       x                        x

-         Microprocessor fault               -                        x

-          Faulty Transmitters                -                        x

10.      Connecting pipelines and accessories;

All the connecting pipelines, isolation valves, regulating valves, control valves, drain valves etc. are to be provided along with the compressors and all the valves should be very reliable and reputed make. The make of the offered valves should be mentioned with details, in the offer. All other instruments, pressure gauges, safety valves, inter locks, vent valves, temperature gauge etc. should be provided as per design and requirement of smooth operation of the Oxygen Plant.

11.   Essential requirements of the offer;

Following details /information must be furnished in the offer, otherwise

the offer  shall  not be considered.

a).  Full technical information design and technical

parameters, constructional / dimensional details safety devices details,

Electrical and control panel wiring diagrams etc.

    - Complete layout of the Oxygen Plant and accessories along with

foundation details and drawing.

    - Total requirement of power, water, consumables and other utilities.

    - Details of works /equipments that are not included by the supplier and to be  provided by BHEL.

    - Item wise breakup of complete scope of supply including details like make, supplier and other technical information. The price breakup in relation to above should be mentioned in price bid.

7/11

      - List of customers to whom the identical / similar Oxygen Plant had been supplied in recent years along with details like model, date of supply and commissioning and full address of the contact person of the customer.

g.) Supplier should also mention in detail, the total number of Oxygen    Plant supplied so far and their market share.

12.   Inspection and Testing:

Both the Oxygen Plant units, complete in all respects, shall be offered       for witnessing, for inspection and testing. Dispatch of both the units will be done after submission of test result / documents and their approval. Vital equipment / accessories like electrical motor, control panel and other bought out items will also be inspected for ensuring good quality and workmanship at the works of Oxygen Plant.

Modifications, if found necessary during inspection,   will   have to be carried out, free of charge, by the supplier of Oxygen Plant. Four copies of the testing documents and inspection certificate for all the components should be furnished along with the dispatch of material. In case the inspection and testing is required to be carried out at OEM’s Works, the cost of the same shall be included in the offer.

13.   Erection commissioning and job proving:

- Both the Oxygen Plant with all accessories must reach the site in one lot. The Oxygen Plant must be supplied with all the foundation bolts, leveling, aligning, anchoring and other material required for erection of complete Oxygen Plants. The supplier shall assist in finalisation of layout plan, electrical plan etc., in line with BHEL's   requirements.

- The supplier shall furnish activity bar chart, civil                                   drawings, foundation design details, loading details, layout plan etc, immediately after receipt of LOI.

- Other activities, manpower, material, instruments etc., required for satisfactory installation, erection, commissioning, testing and job proving of both the oxygen plants shall be the responsibility of the supplier.

- Related Civil work shall be carried out by BHEL as per supplier's   drawings under their supervision and guidance.

8/11

- First fill of lubricants and other required consumables for commissioning shall be arranged by the supplier.

- The offer must be on turnkey basis including the charges for complete erection and commissioning of both the Oxygen Plant. This shall be completed and handed over with in the committed time bound period.

- The supplier shall also operate the Oxygen Plant for the desired performance and efficiency to the BHEL's entire satisfaction level at the site.

- The Oxygen Plant shall be operated for 72 hrs continuously one-by-one & / or both at full load parameters. For measuring the parameters during job proving such as energy per m3, Capacity per hour, pressure, purity of gas etc Supplier shall also bring all the required instruments / devices.

14.   Guarantees:

The manufacture shall cover for all items  erected & commissioned  in both the   oxygen plant  in respect to design, material, construction, performance,

Operation and against any manufacturing defects for a period of not less

18 months from date of commissioning & handing over. The manufacturer    should provide free after sales service and free replacement of defective parts during the guarantee period.

15.     Maintenance:

All the equipment & parts of the Oxygen Plant should have easy accessibility for Inspection, repair, replacement and other maintenance jobs. The material of construction and dimensional details for every part, assembly detail and other details required for Mechanical, Electrical and Electronics etc should be clearly shown in the drawings.

16.    Spares for minimum period of Two years:

Recommended spares for 2 year’s round the clock operation of the Oxygen    Plant including accessories must be quoted item wise with full technical details along with the offer .The supplier should bring the commissioning spares on returnable basis, if not consumed.

09/11

17.     Training of personnel

Free of charge training to our engineers, supervisor & working staff shall be provided at the supplier works in all respects of operation, maintenance (mechanical, electrical and electronics) and safety procedures.

18.     Documents

The manufacture / supplier of the Oxygen Plant should furnish 5 sets of   following Documents in English language: -

        - General layout plan for complete supply of Oxygen Plant with Dimensional details and floor space required.

        - Civil foundation plan for both the Oxygen Plant with foundation details, loading details and dimensional details.

        - General constructional and arrangement drawings for the Oxygen Plant installation, operation and maintenance (Mechanical, Electrical and Electronics) manuals for complete Plant including bought out items.

        - Spare parts manual clearly mentioning fast consuming spares along with the prevailing prices of all spares.

        - Preventive maintenance schedule and recommendations.

19.  MAINTENANCE OF UNITARY OXYGEN PLANT AND AUXILIARY EQUIPMENT

- The bidders shall quotes separately for comprehensive maintenance service for the unitary Oxygen Plant and auxiliary equipment installed at BHEL, Haridwar for a period of Two-years starting after completion of Guarantee/ Warrantee period. During this period the successful bidder is supposed to provide

10/11

preventive, routine and breakdown maintenance and shall repair and /or replace anything or everything defective and /or not operating correctly. He shall indicate the charges on item rate basis to be paid on raising the invoice duly certified by the Engineer after successful execution of the job.

- Maintenance will consist of inspection and preventive maintenance at regular intervals. The same will include the following but not limited to:

- Check the unit for any unusual heating of motors winding and  bearing, leakages in the oxygen plant

- Will check the  out put of oxygen plant,

- Inspect the units piping, heat exchangers for any visible signs of leaks   etc.

- Inspect the unit for objectionable noise, vibrations etc.

- Check system operating pressure and temperature.

- Inspect and keep a logging of all test readings in reference to original standards,

- Inspect and adjust all safety controls.

- Report to the owners in writing related to all defect, deficiencies and repairs carried out during the inspection.

- Servicing of unit shall include but not limited to:

3.1 	Cleaning of air filter.

3.2 	Cleaning of oil filters and replacement of lubricant as required.

3.3 	Checking of electrical parts and dressing of the wires.

3.4 	Checking of equipment and controls for proper functioning.

3.5	Checking of capacitor, contacts, and stabilizer and unit terminals. Check connections and tighten motor terminal and control circuit terminals.

4.	The contractor shall keep a minimum staff of one skilled worker who should be mobile to attend to any complaint within the complex within a reasonable time. The contractor shall confirm attending to all the problems reported to him within four working hours of information and they should rectify within reasonable time as specified hereunder on seven day a week basis.

Bidder shall indicate downtime in case of disagreement

11/11

5.  Preventive Maintenance:

At the beginning of the contract every year checking and servicing all              the unitary equipment shall be done to ensure satisfactory performance of the equipment involved in the contract.

6.  Break Down Calls:

Contractor shall ensure that all complaints are attended promptly and   equipment made operative with in the stipulated time period.

7.  Stand by equipment:

Contractor shall ensure operability of standby equipment to ensure                             steady operation of the equipment.