BHEL - JHANSI

TENDER DOCUMENT FOR VAPOUR ABSORPTION SYSTEM  , Qty -1 No.

Enquiry No. E7160023, DUE ON   27.01.07, Tender Cost: Rs. 500/-

C  O  N  T  E  N  T  S

Page No.

1.         Item Description & Technical Details                                         2-6

2.	Instructions for submission of Tender		                         7

3.	Commercial Terms & Conditions		                                 8-10

4.	Techno-Commercial Bid          		                                    11

( A.K.Banerjee  )		     ( P.K.Pathak )                                  ( Y K Verma )

DGM(MM)	                            Sr. PO (MM)                                      Sr. PO (MM)

1. Item Description & Technical Details :

EQUIPMENT                :	         Vapour Absorption System to chill water

###### SPECIFICATION :  9980

ITEM NUMBER : SP/MISC/9980/1

QUANTITY :        ONE SET

Vapour absorption system

Supply ,installation ,testing and commissioning of 100TR chilling plant based on vapour  absorption system, It will consist of the following

| S.No. | Description | Qty. |
| --- | --- | --- |
| 1. | Comprising of evaporator and absorber | 1 |
| 2. | Comprising of temperature generator and condenser | 1 |
| 3. | Safety devices | 1 |
| 4. | 1 st charge of chemicals | 1 |
| 5. | Absorbent pump set | 1 |
| 6. | Refrigerant pump set | 1 |
| 7. | Purge unit with vacuum pump | 1 |
| 8. | PLC based control panel | 1 |

Party has to include all the required items to meet required parameters.

Plant shall be installed in BHEL Jhansi , where ambient temp. during summer season above 45'c and during winter above 7'c ..

Our required parameters details as stated below:

| S. No. | Parameter | Desired values |  |
| --- | --- | --- | --- |
|  |  | Required Parameters |  |
| 1 | Capacity | 100 TR |  |
| 2 | Load range | 10-100% ( Stepless Modulation) |  |
| 3 | Type | Single effect |  |
| 4 | Chilled water |  |  |
|  | · Inlet temp. (DegC) | 21 to | 15 |
|  | · Outlet temp. (Deg C) | 15 to | 10 |
|  | · Flow rate (m3/hr) | 50.4 to | 60.48 |
| 5 | Cooling water |  |  |
|  | · Inlet temp. (Deg C) | 32 |  |
|  | · Min. tolerable (Deg C) | 10 |  |
| 6 | Steam circuit |  |  |
|  | · Pressure | 2 kg/cm 2 g |  |
| 7 | Construction / Materials |  |  |
|  | · Generator material | SS 430 Ti ferritic stainless steel tubes. |  |
|  | · Chilled water coil material | Finned Copper |  |
|  | · Circulating Cooling water coil material | Cu-Ni tubes to increase protection against corrosion . |  |
| 8 | Maintenance ease |  |  |
|  |  | Hinged Door for water headers |  |
|  |  | Marine type Headers and side exit nozzles |  |
| 9 | Shell design | Dual shell design to eliminates oxygen corrosion |  |
| 10 | Isolation Valves | Special angle valves |  |
| 11 | Nature of corrosion inhibitor | Non -Toxic (Lithium molybdate) |  |
| 12 | Controls | PLC based Siemens / ABB |  |
| 13 | Real time data | In English for all operating / monitoring parameters |  |
| 14 | Displays and graphics | Digital display of various parameters on the PLC .display |  |
|  | Operating data memory | 20-30 days |  |
| 15 | Safeties and alarms | Imported – reliable make sensors |  |
| 16 | Generator safety |  |  |
|  | Generators sensors | Omron Japan / equivalent |  |
| 17 | Chilled water safety |  |  |
|  | Differential pressure control for chilled water | Switzer / equi. |  |
| 18 | Refrigerant level probes | Provided |  |
| 19 | Sight glass in absorber & Evaporator | Bolted type |  |
| 20 | First Charge (LiBr & liquids) | Include |  |

# VARIOUS CONTROLS & SAFETIES

- PLC required Siemens make which enhances the flexibility & reliability of the m/c. Also, trouble shooting is easier as ‘Trip Log’ and ‘Data Log’ as per the frequency required is stored in the PLC. Unique display screen, feather touch keypad and software constitute a user friendly operator interface.

Controls –

(i) Temperature

Chilled Water outlet temp. controls the Steam control valve opening. Further, L-cut & antifreeze trip is also based on this temp.

- Generator temp. set pt is used to trip the m/c

- Generator vapour temp. set pt. Is used to trip the m/c

- COW temp. to trip the m/c below 10 deg C

(ii) Level

- 3 level electrodes each in Absorber – used to protect pump from dry running, control steam control valve & ref. Blow down

- 3 level electrodes in Generator – used to control Absorbent Pump

- 3 level electrodes in Evaporator – used to control the Refrigerant Pump

(iii) Others

- Dp switch in CHW line

- Flow switch in CHW line

- Chilled water pump interlock

- Diagnosis –

Various other temp.’s to be measured for diagnosis / trouble shooting

- Dilute solution temp. (before LTHE)

- Spray solution temp.

- Alarm cycle –

- Dilution cycle alarm

- Total shutdown alarm

- Motor Protection –

- Absorbent pump overload relay

- Refrigerant pump overload relay

- Purge pump overload relay

# Stepless modulation:

Machines are required to run at a stepless modulation of 10 to 100 % load.                                     So even at part loads the machine performance is not affected.

- CuproNickel tubes:

We required CuproNickel tubes in Cooling Water circuit. These tubes can tolerate upto 2,000 ppm of chlorides and have got much better resistance to Descaling Chemicals as compared to Copper tubes.

# Other features

- Machine should be with Marine type headers with hinged doors which avoids dismantling of piping and hence maintenance can be faster & easier.

- Isolation Valves for Pumps should be angle valves of SS Construction designed for High Vacuum Application.

- Electronic Control for Cavitations Protection for the Ref. Pump.

- Machines is required with level electrodes to measure the level of solutions in the shells.

.

Following parameters may asked by supplier suitable for  vapour absorption system

| Fouling factor of chilled water |  |
| --- | --- |
| Outlet temp.of water |  |
| Flow rate of water |  |
| Flow rate of water per TR |  |
| Fouling factor of cooling water |  |
| Consumption (kg per TR) |  |
| Specific stem consumption at (kg per /hr) |  |
| 25% load |  |
| 50%load |  |
| 75%load |  |
| 100%load |  |
| COP |  |
| Pumps kw |  |
| solution pump |  |
| refrigeration pump |  |
| purge pump |  |

Limits Scope

1.Exisiting  chilled water &condenser water pumps, & cooling tower shall be used.

2. Civil work & piping in the scope of BHEL

Supply of liquids by supplier

1. lithium bromide duly inhibited-                1lot

2. Refrigerant water with octyl alcohol          1 lot

V. PERFORMANCE CRITERIA AT SITE

Supplier shall carry out performance trial of the machine to demonstrate the capacity of VAHP.

SUPERVISION OF ASSEMBLING, ERECTION AND COMMITIONING OF HEAT PUMP

1. 	Party has to depute service engineer for commissioning & erection.

2. 	Drawing, foundation details, electrical circuit diagram, over all dimensional drawing with                        nozzle orientation to be submitted.

3. 	Three copies of maintenance, operations & erection manuals are required along with supply.

4. 	Any condition or other matters relating to erection & commissiong not expressly stipulated would be a matter of mutual discussion as our tech. requirement.

Guarantee:

1.	The equipments / materials & the whole system being supplied shall be without any wear and tear.

2.	 Repairs/replacement are carried out by party.

3.	 Electrical/Mechanical components and instruments are covered under Guarantee against  manufacturing defects .

4.   	The guarantee duration to be given by supplier..

2.INSTRUCTIONS FOR SUBMISSION OF TENDER

- The offer against the enquiry shall be submitted in two parts.  The first part called Techno-commercial bid i.e. Part - A shall be un-priced and will be submitted in line with given details in commercial terms and conditions .  The second part called Price-Bid  i.e. Part-B, in this you will have to mention the basic prices, taxes duties etc for basic equipment & Standard / optional accessories if any.

- The vendors shall submit Part-A and Part-B of their bids in two different sealed envelopes duly super-scribing Enquiry No. and Part No. of the bid.  These two parts of the bid shall be kept together in a third envelope super-scribing Enquiry No., due date and time of opening as indicated in the tender document.

- Part-A of the bid alone shall be opened on the due date in presence of the tenderers in the first instance.   This part of the bid shall be examined in detail.  Part B of the bid shall be opened only for such of the tenderers whose Techno-Commercial offers are found acceptable by BHEL.  Such tenderers shall be advised the date and time of opening of Part B i.e. price part of their bids.  Tenderers must carefully go through all the instructions and conditions before filling in Part B of the bid.  Any type of mistake in submission of the bids will make the tender liable for rejection.

- The bids shall be submitted only in the format given in the tender documents. The tenderer is  required to sign and stamp each and every page of the tender document clearly bring out deviations, if any.

- Tenders not complying with the above and other requirements of the tender shall be liable for rejection.  Tenderers are advised to read all the documents carefully before submission of the bids and ensure the fulfillments of all the technical and commercial parameters.

- No over-writing in any Part-A or Part-B is permitted.  Corrections in the bid should normally be avoided. However, when these become essential, bidder shall score out the incorrect information and put the correct information duly endorsing each correction with his signatures.

- Tender Cost (if any) is to submitted in the Form of  DD in favour of BHEL-Jhansi  payable at

Jhansi along with Techno –Commercial offer. This DD should not be kept in Sealed Price Bid.

3.COMMERCIAL TERMS & CONDITIONS FOR PURCHASE ENQUIRY

- Offer is invited in two bids, outer cover, inner cover-I (Techno-Commercial bid) and inner cover II (Price-Bid) must bear our tender no., due date and bidders name.  Offers received in single bid will be bypassed.

- The offer should reach this office on or before 13.15 hrs on the due date.  The tender can also be dropped in the Tender Box kept at Administrative Building Gate.  The tenders will be opened after 1400 hrs on the due date in presence of all bidders who will be present.

- Offer should be free from overwriting or erasures.  Corrections or additions, if any should be attested.

- No enhancement of rate for whatever cause is allowed once the offer is accepted and the order is placed.  Withdrawal from the quotation after it is accepted or failure to make the supply within the scheduled period will entail cancellation of order, forfeiture of earnest money if any and/or imposition of risk & cost purchase.

- Material offered should be of required quality and conforming strictly to our specifications / drawings or to the specifications in the drawings.  Any deviation must be clearly stated in the offer with particular clause /detail in our specification / drawing for which deviation is quoted.  All required documents/details  e.g. QA Plan, type TCs, drawings & data sheet etc. must be submitted along with the offer.

- Irrespective of whether it is mentioned in our specification, all machines / equipments are required to be calibrated in metric units and certificates must be issued where applicable.

- Work test  certificates / inspection certificates/guarantee certificate/ compliance certificate, etc. will be required to be submitted along with supplies in case an order is placed.

- Required Delivery  time for affecting supplies should be indicated in the offer.

- Failure to supply by the time specified on the order will make the supplier liable to pay unconditional penalty of ½% of the prices of goods in arrear per week subject to a maximum of 10% for Indian suppliers and max 5% for Foreign suppliers of the order value unless agreed otherwise.

- The quantities for each item to be purchased may vary from the tendered quantity according to our actual requirement at the time of placing orders.

- Bharat Heavy Electricals Ltd does not bind itself to accept the lowest of any tender, but reserves to itself the right to accept or reject all or a part of any tender at its discretion following BHEL Purchase Policy & Government guidelines.

- In all cases of disputes, the matter shall be referred for arbitration.  The arbitrator  shall be nominated by the Unit Head, Bharat Heavy Electricals Ltd., Jhansi or any other officer nominated by him.  The award of Arbitrator shall be final and binding on both the parties.

- In case of any suit or other legal proceedings under or relating to this tender, the courts at Jhansi shall have full jurisdiction.

- Total delivered cost at BHEL Jhansi Railway siding/Works shall be the criterion for deciding the tender.

- Unless otherwise specified, offer should be on ex-works basis (for Indian Suppliers) with freight & insurance to be borne by BHEL.

- Your quotation against this enquiry must be valid for ordering up to minimum of 120 days from the date of tender opening.

- ADDITIONAL FOR INDIAN SUPPLIERS:

I)        If any material is booked to selves or if it is not consigned to BHEL Jhansi, any warfage or

demurrage occurring from these shall be to the account of supplier.  In case of road transport,

material shall be booked only through our rate contract transporters mentioned in the purchase

order.

- Where there is provision for payment of Sales Tax extra, it will be paid only if the registration number both under State Sales Tax and Central Sales Tax are specifically mentioned on the bill/invoice.  Your Sales Tax Registration number should be mentioned in the offer positively.

- Excise Duty Gate Pass will be required in original.  Applicable taxes & duties must be included in the offer.

- ADDITIONAL FOR FOREIGN SUPPLIERS:

i)	For documentation and correspondence language shall be English only.

- Rates quoted should be on FOB basis.  All despatches are to be made by sea  by IPBC conference vessels only unless otherwise stated in purchase order.

- Agency commission, if any, will be paid out of the FOB value after receipt & acceptance of material at BHEL Jhansi in Indian Rupees.  TT Buying exchange rate prevailing on the tender opening date or the letter of credit date or date of purchase order whichever is lowest will be considered for calculating the agency commission.

- The rates quoted should be inclusive of charges of packing and delivery of material up to the port of shipment on FOB terms.  The material is required to be packed suitably in all respects considering the peculiarity of the material for normal transport by Sea/air and subsequently by Rail/Road in India suitably protected against the effect of tropical salt laden atmosphere in the event of consignment being delayed at Indian Ports before outward clearance.  You should also furnish details of shipping specification, sizes, volume, weight, number of cases etc. When articles are packed with packaging material of plant origin, phytosanitary certificate will be required.

- Our standard terms of payment is 100% payment through bank against despatch documents or 100% through sight irrevocable & unconfirmed letter of credit.

19.   Security deposit (SD) cum Performance Bank Guarantee  (PBG) for 10% basic value of the order (excluding taxes &

duties) for  execution of the purchase order (PO) & satisfactory Performance of the equipment before release of  PO

will be required to submit which will be valid from the date of issue of LOI to 24 months after acceptance of material by

BHEL with a further claim period of 3 months. PO will be issued only after receipt of SD cum PBG.

20. For fully imported equipments / plant/ machinery (no part or sub-assembly of Indian origin) :

a. No SD cum PBG will be applicable for basic order value up to Rs. 25.0 Lacs on foreign supplier.

b. No SD cum PBG will be applicable for basic order value up to Rs. 10.0 Lacs on Indian stockist / agent of

foreign manufacturer.

21.   B.G. shall be from Scheduled Banks/Public Financial Institutions as defined in the Companies Act.

22. The equipment shall be guaranteed for 24 months from the date of acceptance by BHEL irrespective of date of supply,

erection and commissioning.

23. Our standard terms of payment (for Indian Suppliers) is 80% of P.O. value be paid after 60 days of acceptance of the

equipment at BHEL Jhansi works and balance 20% after successful commissioning & handing over of the equipment

(where applicable).

24. Amount of Service Tax / Education Cess / any other Govt. duty ( as applicable on the date of offer) for erection or any

other activities associated with the scope of work in the tender must be indicated in Techno-commercial bid of the offer.

25 . Blank Price Bid (After erasing prices) must be submitted along with Techno commercial bid.

26.  If any goods are rejected, BHEL shall be at liberty to take action as per following at the

risk and cost of supplier:-

    - Allow the supplier, wherever mutually agreed, to rectify the rejected goods at BHEL's works within reasonable time as fixed by BHEL.

    - Allow the supplier to make free replacement within a specified period, rejected goods can be lifted by the supplier thereafter.

OR

Allow the supplier to refund the full amount paid to him by BHEL by a Demand Draft  before lifting the rejected goods.  Fresh replacement shall be regularized as per terms & conditions of the original purchase order.

OR

Take alternative  procurement action from elsewhere and recover the difference in cost, if any incurred by BHEL in this regard from the supplier.  The supplier shall not be entitled to any gain on purchase.

    - Terminate the contract either in part or in whole at the  discretion of BHEL and recover the loss, if any, from the supplier.

27. For any clarification on our tender terms and conditions please contact Sr. Purchase Officer (Capital Items)

before due date.

28. Inspection may be done at supplier works by BHEL.

## 4. TECHNO COMMERCIAL BID  PART-A

( Supplier should fill up this bid by putting the tick in accepted / non accepted column)

SUPPLIER’S NAME & ADDRESS

1.          Offered Equipment with complete technical details  :                      As per attached details

2.           Packing & Forwarding Charges, FOB charges (if any)                                                               ….%

3.   	Present rate of Excise duty (if any)         		                                                              ….%

4.     	Present rate of sales tax			 		                                                   %

(UPTT/CST, Not applicable in case of Foreign suppliers)

5.	Delivery period in  No. of  days from  date of LOI / PO                                                                                                                    6.	Taxes and duties shall be extra as applicable on 		              Accepted / Not accepted

the date of actual delivery.

7.	Penalty clause as well as other conditions given			Accepted / Not accepted

in general Terms & conditions

and Standard Enquiry terms & conditions are

acceptable to us.

8.           Rates quoted in the price bid are on Ex Works / F.O.R. 		---------------------------------

Jhansi .basis.

9.	Validity of the rates quoted is 120 days from the 			Accepted / Not accepted

date of opening of price bid.

10.          Security deposit (SD) cum Performance Bank Guarantee                      Accepted / Not accepted

(PBG) for 10% basic value of the order (excluding taxes & duties)

for  execution of the purchase order (PO) & satisfactory

Performance of the equipment up to Guarantee period

of 24 months  before release of PO will be submitted.

11.        The equipment shall be guaranteed for 24 months from                            Accepted / Not accepted

the date of acceptance by BHEL irrespective of date of

supply, installation.

Note :- If any of the above conditions are not accepted

the offer shall be liable for rejection.