ANNEXURE

- This document details the specifications for programmable temperature controller with display of measured values, set values and pattern display.

- Technical Specifications

| Sl No | Specification | Details |
| --- | --- | --- |
| 1.0 | GENERAL |  |
| 1.1 | Number of patterns/programmes | 4 or more |
| 1.2 | Display | Digital |
| 1.3 | Power supply | AC 100 to 240 Volts , 45 to 65 Hz both automatically adjusted |
| 1.4 | Mounting | Flush Panel mounting (Vertical) |
| 1.5 | Front panel | Water and dust proof to IEC529-IP65 |
| 1.6 | Dimensions | ###### 96 X 96 mm |
| 1.7 | Ambient Temperature | 0 to 50°C |
| 1.8 | No of segments | ###### 12 or more |
| 1.9 | ###### Panel Key-lock | With actual key : panel keys assigning selection should be provided |
| 2.0 | INPUT |  |
| 2.1 | Measurement intervals | 2.5 second max |
| 2.2 | Measurement range (user selectable) | ## DC Volts : 20 mV to 20 V ## Thermocouple : R, S, J, K RTD : Pt 100 |
| 2.3 | Thermo-emf in case of thermocouples | As per standard IEC 584/ASTM 230-96 |
| 2.4 | Linear scaling | DC Volts, TC and RTD to be scaleable |
| 2.5 | Square root | Scaleable input - DC Volts |
| 3.0 | DISPLAY FUNCTION |  |
| 3.1 | Display language | English |
| 3.2 | Program monitor | LED yellowish green |
| 3.3 | Set point/parameter display | 3 digits+4digits,7segment LEDs red |
| 3.4 | Display contents | Process variable(PV) Set point/Parameters |
| 3.5 | Process variable display | 4 digits, 7 segments LEDs red |
| 3.6 | Other display information | Ramp, soaking and cooling cycle |
| 4.0 | CONTROL SPECIFICATIONS |  |
| 4.1 | Time proportional PID | Current pulse out put for driving Thyristor |
| 4.2 | Out put signal | 4-20 mA DC Load resistance below 600 ohm |
| 4.3 | Out put action selectable | Direct / reverse selectable |
| 4.4 | Output accuracy | ± 1 % of span |
| 4.5 | Other functions | Auto tuning, Multi PID, Key lock, Input Burn out detection, Measuring input and control out put circuits isolated from each other. |
| 5.0 | ACCURACY |  |
| 5.1 | Measurement and display accuracy - DC Voltage range - Thermocouple (R/S) - Thermocouple J/K - RTD Pt-100 | - ± (0.3 % reading + 2 digits) - ± (0.3% of reading + 1°C) - ±( 0.3% of reading + 0.7°C) - ± (0.3% of reading + 0.3°C) or better |
| 5.2 | Reference junction compensation | Internal (automatic) |
| 5.3 | RJC accuracy | ± 1°C max |
| 6.0 | # DOCUMENTS |  |
| 6.1 | Operating, installation and communication manuals for the recorder and software | One set to be supplied with recorder |

- The supplier should furnish detailed catalog of the programmable temperature controller being quoted with his offer.

- The supplier should confirm point-wise adherence to all points of the technical specifications above.

- Necessary brackets for the mounting the instrument in a panel should be supplied with the instrument.

- The equipment shall be guaranteed for accuracy and failure, for a period of 12 months, from the date of acceptance at BHEL works. Guarantee certificate shall be sent with the despatch documents.