PAGE  
1

PRICE BID                                      Tender notice No: HY/FCD/OT-07/2007-08       
                                                                                  Dt: 10.09.2007 ,  Item no: 2
Name of Work:  Renovation of existing concrete floor in 03 Switch Gear Clean Hall
	Item No.
	               Description
	Quantity
	Unit
	         Rate in
	Amount 

in  (Rs)

	
	
	
	
	Fig
	words
	

	1
	Dismantling of cement concrete upto an average thickness of 10 cms and disposing off the debries upto a lead of 2 KM including loading, unloading, at specified places, etc., as directed complete.

	18.00 Cum
	One Cu.m
	
	
	

	2
	Providing P.C.C 1:2:4 with 20 mm downgraded granite stone metal over old concrete after thoroughly cleaning and compacting, leveling,curing etc., complete.

	15.00 Cum
	One Cu.m
	
	
	

	3
	Granolithic topping of 25 mm thick using 1 Cement and 1 Metal of 10 mm down graded granite stone chips, laid over suitable base concrete (when it is in green condition) and Ironite finishing 12mm thick using a mix of 50 Kg of ironite, 200 Kg of cement and 0.30 Cu.m of granite stone metal chips of 6 mm down graded metal including cost of all materials, labour, curing etc., complete.

	180.00

sq.m
	One 

Sq.m
	
	
	

	4
	Supply and applying 3000 microns thick medium duty flooring of epoxy polyurethane (EPU Based product) floor coat on concrete floor, of approved shade and brand. The scope of work includes surface preparation and application as directed by the manufacturer with a warranty of one year from the date of completion of work. The work should be carried through Authorized applicator of Cipy products. EPU coating should be carried after 2 month of completion of granolithic finish to ensure moisture free surface.


	180.00

sq.m
	One 

Sq.m
	
	
	

	CONTRACTOR(S)                                                              ISSUING/ACCEPTING AUTHORITY
                                                                Contd…



	Item No.
	              Description
	Quantity
	Unit
	     Rate in
	Amount 

in  (Rs)

	
	
	
	
	Fig
	words
	

	
	The detail specification for application of EPU flooring is as stated below :

Testing is done as directed by the manufacturer and the test like Clean, dry and sound test should be conducted. Moisture test should be conducted by moisture meter or plastic sheet method. The residual moisture in the concrete should not be more than 4-5%. The concrete must be clean, dry and sound before EPU coating is applied to it. 
• Clean means that there is no foreign matter such as dust, dirt, grease or oil on the concrete 

• Dry means no free water is present. 

• Sound means there is no laitance or weak surface skin on the top of the concrete.

a) Surface preparation

The surface should be free from oil grease and foreign particles, which will be achieved by mechanical power tool/manual cleaning and solvent cleaning and scarifier attached with vacuum cleaner up to the depth of 100 to 200 microns loose laitance will be removed.

b) Primer application: 

Providing and applying EPU primer, cipoxy 14 in the ratio 1:1on the scarified surface by brush or roller or trowel and allow for 6 hours curing.

c) Screed application: 

Providing and applying 3 component cipoxy 14 and FQ 150 sand 100% solids in the ratio 1:1 and mixed with one part of FQ 150 sand in power mixture to achieve homogeneous mix and applied and leveled by troweling to form a monolithically layer for a thickness 2000 microns and allow curing for 4 to5 hours
d)    Grinding:

The entire surface would be grounded mechanically to remove any undue protrusions after grinding the entire dust particles would be removed by the vacuum cleaner.

e)    Sealer application: 

A layer of Epoxy polyurethane sealer putty will be applied to seal all the micro porosities and allow to dry for 1 to 2 hours.

f)    Self leveling EPU top coat: 

Cipothane SL is a self leveling, two component EPU based pigmented top coat recommended for epoxy floor coatings. It has excellent flexibility & adhesion.

Ensure that the sealer coat is dried. Grind the surface with grinder. Cipothane SL resin is pigmented. Stir it well before mixing with hardener. Mix Cipothane SL (100% solids and solvents) resin and Cipothane SL Hardener in 2:1 ratio by volume. Agitate the mixture for 10 minutes. Apply by leveler at the thickness of 800 microns. Then deaerate by using spike roller. Allow to cure for overnight.
	
	
	
	
	

	
	
	
	
	
	
	Contd..



	Penalty:  0.5% of the   gross  value of  work  will  be  levied for every weeks delay  by  the  agency,  subject to maximum of 10 % value of the work
	
	
	Total: 
	
	
	


Note:   1.  In case of difference between quoted rates of agency. In figures and words, higher rate will  

                 be taken  for comparison and lowest rate will be  considered while awarding the work.

2. The contractor shall quote rates for all the items.   In case of any item missing in quoting 
      the entire offer  will  be rejected.  Incomplete offer will be rejected.  

            3.   The rate quoted is for the finished item in all respects, inclusive of all applicable taxes,  

                  leads, lifts if any.

            4.  The agencies are advised to familiarise  with the nature of work by inspecting the site 
                  before quoting. 

5. Bills /material proof of entry inside factory area shall be shown to the Engineer-in-charge 
      for the bought   out items.
6. The Contractor shall arrange all the necessary tools required for  demolishing  

       items.

7 Special time will be given for application of  EPU coating after two months of completion of granolithic finish to ensure moisture free surface.
 CONTRACTOR(S)



            ISSUING / ACCEPTING AUTHORITY

