- Specification  Solar Street Lights ( 28 nos.) for use in factory area ( 9FA Periphery Lighting)

(M207 CG7P0025)

| sl | Item | Type | Suppliers Comments |
| --- | --- | --- | --- |
| 1 | PV Module 12v, 75W X 2nos | BHEL / Tata BP make |  |
| 2 | Battery(Exide make SMF) | 12V 150AH X 1 |  |
| 3 | Autonomy | 5 Days |  |
| 4 | Lumina ire with assembly (Phillips / Osram make ) | SOX 26 X 1 |  |
| 5 | Illumination | Minimum of 3500 Lumens |  |
| 6 | ECU with inverter & DDC | 1 No. |  |
| 7 | GI Pole | 6 Mt. x 1 |  |
| 8 | Module mounting structure | 1 No. |  |
| 9 | Battery Box | 1 No. |  |
| 10 | Installation kit & manual | 1 No. |  |
| 11 | SCOPE: Supply comprises Lamp Pole, Battery, Battery Box, Electrolyte, Solar Module, and Module mounting structure, Luminaries, Luminaries assembly, connectivity within the system along with cables. Civil works like digging pits and concrete grouting for the pole is in vendor’s scope . The vendor has to take complete responsibility for installation and commissioning of solar street light in our premises . | ------------ |  |

ECU-Electronic Charger Unit

DDC – Dusk to Dawn Controller

Terms and conditions

| sl | item | type | Supplier’s comment |
| --- | --- | --- | --- |
| 1 | Guarantee: All supplies excluding lamp will be guaranteed for a period of eighteen months from the date of supply . | -------- |  |
| 2 | Spares : Following spare to be included in the scope : a) PV modules (make BHEL/TataBP) 1 no . b) Lumina ire with assembly 3 nos. c) ECU with inverter & DDC 3 nos. | BHEL/TataBP Philips/Osram ---- |  |
| 3 | THE PRICE OF SPARE TO BE QUOTED SEPERATELY AGAINST EACH ITEM . | ---- |  |
| 4 | The supplier shall depute their representative at least once every 3 months to check functioning of all solar street lights , maintenance of batteries , cleaning of PV panels Free of cost. | ---- |  |
| 5 | All equipment shall be suitable for outdoor conditions like rain and sun for temperature variations between 7° to 50°C. | ---- |  |
| 6 | Supplier to send his offers for commercial and technical bids in separate sealed covers. | ---- |  |
| 7 | The equipment shall be offered for inspection before dispatch . Only after obtaining clearance in writing the street lights can be Dispatched . | ---- |  |
| 8 | The vendor is required to submit test certificates of PV modules, Lumina ire , battery ,ECU, DDC, etc at the time of inspection. | ---- |  |
| 9 | The vendor is required to submit drawings and quality plan before commencement of manufacturing. |  |  |