## Prebid
Prebid Clarifications
Project: TSGENCO – YADADRI (5x800 MW) STPS
Item Description: Rotating Machine Condition Monitoring and Analysis System for HT drives and Vibration Analysis System for BFPDT
RFQ No.: NKK0002825
Clause Ref. | Clause Description | Bidder's Pre Bid Query/ Technical Comment | BHEL's Reply dated: 08/11/2019
BB Note to Bidder | Bidder to submit their offer meeting the spec requirements. However any product specific limitation/deviations with respect to API 670 standard...... | In this clause API 670 is mentioned but version is not mentioned, should the latest 5th edition to be followed | Yes, the latest edition of the standard shall be followed, i.e. API 670 Standard 5th Edition.
DD Technical req- Pt-1 | The system shall be complete with vibration transducer, mounting pads , necessary preamplifier /electronics mounted in local junction boxes, | Please confrim ,if vendor needs to consider structural steel required for installation of JBs or will it be supplied by BHEL at site | Bidder need not to offer structural steel for JB erection. However, bidders to consider all accessories as mentioned in the specification of junction boxes.
DD technical Req: Pt-3 | Sensors, proximitors and monitors shall be fully compliant to API. | Please confirm that refered API is API 670 latest edition. Please confirm if the analysis and diagonistics software should also comply to API 670-5th edition(Annex-N) | Refered API in the specification is the API 670 Standard latest edition i.e. 5th Edition. Please note that, Sensors, proximitors and monitors shall be fully compliant to API, as per specification clause DD 3. Compliance to API 670 Annexure-N is not mandatory. However, bidders may submit their compliance to API 670-5th Edition (Annex-N) for their offered Condition monitoring and management system.
DD technical Req:Pt-4 | Critical alarm & trip relay output shall be configured in 2 of 3, 2 of 2 or 1 of 2 voting logic as required for the machine criticality. Offer system shall provide three (3) binary contacts for each bearing, for very high vibration trip of drive. | Pl elaborate the exact requirement. | Three (3) binary contacts for "Vib .Trip Level" to be provided for each bearing of all "Machine" mentioned under the Section – A: Machine Data for Vibration Monitoring System. Three (3) binary Trip contacts should be considered from separate relays.
Pls clarify the following:
1. Which alarms are to be considered critical
2. which machines to be considered critical
3. For the 3 binary contacts to be provided for each bearing, should they be considered in same relay module or separate relays since specification calls for 2 of 3 or 2 of 2 etc.
|  | 4. As per API670 relay should be double pole throw type (i.e. SPDT/DPDT). Please confirm if vendor need to follow this requirement of API 670 | This requirement is not mandatory.
DD technical Req:Pt-7 | Grouping of modules in racks shall be equipment wise | Please note that as per API670 clause 7.1.3, multiple machines can be accomodated in single rack however each machine train shall have dedicated monitor modules. Please confirm if signals from more than one machine can be connected to single/common rack. | Yes, signal from more tham one machine can be connected to common rack, if the offered rack system is capable for the same as per the specification requirement. Bidders to comply the specification requirement, i.e. grouping of modules in racks shall be equipment wise.
DD technical Req:Pt-14 | This unit shall also have the ability to communicate to on line analysis system and DDCMIS / Turbineprotection system / PLC / through hardwired connection (4 - 20mA & relay output) for monitoring &alarm / protection and through software link (raw buffer signal) on line analysis system. | Please confirm if the analog 4-20mA signals should be isolated or not. | Isolated analog 4-20mA signal is not mandatory as per specification.
17.1 | 10 % spare channel shall be provided in each type of input / output unit | 10% hot spares for each type of I/O module is only required for the I/O modules or this is also required for the main processing modules in VMS & Analysis hardware etc. | 10% hot spare wired channel for each type of I/O module is required for the I/O modules, including its main processing modules in VMS & also for built-in or external Analysis hardware/ module.
Bidder's understanding is total 10% wired spare channels we need to consider. Pl confirm?
17.2 | 10% hot spare for each type of I/O modules (installed) shall be provided in each functional group, fully wired upto the marshalling/ termination TBs. | Please clarify what is functional group | 10% hot spare for each type of I/O modules (installed) shall be provided in each functional group. Please consider for each Units, the CER as one functional group and CWP Pump house as another functional group .
Pl. confirm that 10% wired spare we need to consider per cabinet or per Rack?
20.7 | It shall also have the capability to send advisories through pagers and emails in addition to the RC. | pager communication/advisories are not possible, please confirm if this is acceptable | Noted
21.6 | Time synchronization card for IRIG-B protocol | Bidder can provide NTP protocol, please confirm | SNTP / NTP protocol for time synchronization is acceptable in-lieu of IRIG-B protocol; if the bidder submit declaration that there is no other option for them to make good the deviation.
21.14 | Third party operating system, graphical users interface, Firewall, Anti-spam, Anti-virus & spywarefor Gateways. | 1.Bidder will provide windows 10, please confirm 2.Please confirm whether the firewall should be hardware or software type , if its hardware type please confirm the qty of firewalls required. | 1. Noted 2. Firewall shall be software type.
22.14 | Firewall, Anti-spam, Anti-virus & spyware for Gateways. | Please confirm whether the firewall should be hardware or software type , if its hardware type please confirm the qty of firewalls required. | Firewall shall be software type.
24.2 | All Ethernet switches to be used in the plant shall be of same type and shall conform the specification requirements | Kindly provide the make/model No. that BHEL is planning to supply so that same can be considered for this RFQ | Bidders to comply the specification requirement.
24.3 | All managed switches shall work in IEC-61850-3 protocol environment and shall support IEC-62439 standard ring redundancy topology (MRP) and also fast MRP. | Ring topology is not applicable as we shall be using STAR topology for CMS.If ring network is required please provide expected system architecture. | Noted
24.4 | Switch shall have the capacity for maximum of 4 Giga bit fiber port and 24 fast ethernet port. | Please confirm if we can offer switch with lesser no.of ports. We don't envisage switch with so many ports for this applications | Noted
25.3 | RAM-16GB DDR3 | Bidder will provide DDR4, please confirm | Noted
26 | Optical fiber cabling-Cabling distance between various offiste control room is given. | In price bid format total 9400m is mentioned please confirm whether the above mentioned total length is in consideration of redundant cables that shall run in two physically seperate conduits optical fiber distribution box | Yes, redundant FO cables have been considered in this calculation.
26.C | Main CERs to respective Computer Room = 100 meter separate for each Unit | For distance of 100m FO cable is not required ,please confirm if standard copper cable is acceptable for this application. | Please consider FO cable from Main CERs to respective Computer Room.
27 | Indigenous / Bought-out items shall be from following sub-vendors | Some of the vendors specified in sub vendor list (for Eg-D-link/Cisco) do not manufacture items as per the product specification mentioned else where. Please confirm if we can source an item from a vendor as per clause 27 but not meeting required product specification. | Not acceptable. Bidders to comply the specification requirement.
Section A5 | Buffered Vibration Signal List of Steam Turbine Generator (STG) | Please specify the make model & sensor and VMS system along with latest data sheet to verify the compatibility of buffer outputs of VMS with RMCMAS interfacing hardware. | Scope of supply for Vibration Analysis System for STG, have been deleted from RFQ Specification Rev. 01.
Section A6 | Buffered Vibration Signal List of BFP Drive Turbine (BFPDT) | Please share the latest data sheet of Shinkawa make model no. that are mentioned in RFQ. Also provide the make and part no. of VMS system along with latest data sheet to verify the compatibility of buffer outputs of VMS with RMCMAS interfacing hardware. | Please obtain the requisite information from the official website of M/s Shinkawa.
HH Training | 6 no. of End-user’s Control Engineers for two weeks each on operation. 6 nos. of End-user’s C&I engineer for two weeks each on system maintenance. | Please note for VMS/CMS 1 week training per batch is enough. Hence we shall be offering only one week training per batch, please confirm. | Not acceptable. Bidders to comply the specification requirement.
DD 18.5 | Panel size: 750 mm W X 800 mm D X 2067 mm H (including top canopy- 60 mm + Bottom frame 50 mm + Antivibration pad 15mm) | Bidder is proposing Panel size 2115(H) including 100mm base frame & 15mm anti vibration pad & 800mm W x 800mm D. | Noted
DD 20.3 | The system shall be provided with redundant server, workstation and 24 inch TFT monitor, A3 laser printer and one no. Laptop | All these items required Unit wise? | The redundant server, workstation and 24 inch TFT monitor, A3 laser printer are all required Unit wise. Laptop one (1) no. is required common for all Units.
Section-A | Section – A: Machine Data for Vibration Monitoring System, under Measuring Parameter "Absolute bearing vibration" is specified. | As per bidder's understanding requirement is Radial vibration (suitable sensor accelerometer / Velomitor) not the Absolute bearing vibration. Kindly Confirm? | Requirement is for absolute bearing vibration using accelerometer/ velomitor sensor. Pl. refer Prebid clarification dated: 04/11/2019, for clarity on the type of machine bearings.
Section-A |  | As per bidder's understanding all 66 machines VMS rack shall place in same control room except CWP. Kindly Confirm? | VMS for CWP and ACWP machines are in CW Pump House control room. Please refer Note # 3) in the Machine Data at Section-A.
DD technical Req:Pt-7 |  | As per bidder's understanding we can merge different machines in One MMS rack. Pl Confirm? | Yes, signal from more tham one machine can be connected to common rack, if the offered rack system is capable for the same as per the specification requirement. Bidders to comply the specification requirement, i.e. grouping of modules in racks shall be equipment wise.
Section-A |  | As per bidder's understanding for below given machines, Panels need to consider in Field (CW Pump House). Pl Confirm? | Please refer Note # 3) of the Machine Data at Section-A. The vibration monitoring system panels for CWP and ACWP machines, shall be placed at CW Pump House. Please note that, CWP Pump House control room is air-conditioned.
DD 18 |  | Cabinet to mount Interface hardware for STG & BFPDT shall be in BHEL or bidder's scope. Kindly Clarify? | Cabinet/ Panel to mount analysis hardware for BFPDT shall be in bidder's scope. Scope of supply for Vibration Analysis System for STG, have been deleted from RFQ Specification Rev. 01.
DD 5. |  | Redundant Communication required in between VMS racks to DCS. Pl Confirm? | It is confirmed that, redundant soft-communication is required between VMS racks to DCS.
DD 17.3 | Wired-in "usable" space for 20% modules along with Field Terminal assemblies, PCB/Connectors (if any in the offered system) in each of the system cabinets for mounting electronic modules shall be provided for future use; same is also specified in clause DD13 above. | Please clarify whether 20% usable space shall be mandatorily provided for the cabinet in the CWP Phump House area? Wether overall space including cabinets of CER and CWP area can be considered? | Noted, bidders to consider wired-in 20% usable module space on overall basis i.e. considering Unit-wise panels in CER and CWP functional areas.