## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.0 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: SDGM/WCC HSE Safety, BHEL SBD, BENGALURU
Name of Work: Operation and Maintenance works of 1 MW PV Plant at ONGC, Rajahmundry for a period of 47.7 months NOTE: 1. CONTRACTOR SHOULD QUOTE PERCENTAGE (%) ABOVE/BELOW (OR) AT PAR WITH RESPECT TO TOTAL AMOUNT. 2. QUOTED PERCENTAGE (%) IS APPLICABLE ON ALL ITEM RATES UNIFORMLY. 3. Measurement of Services / Activities carried out at Site shall be as per O&M Log book records and deductions will be passed in case of services / activities not completed in the month / year. IMPORTANT NOTE: 1. To carry out above activities One technical-cum-administrative in-charge with working experience to be appointed who will be the overall O&M incharge of the plant and 2 numbers of semi-skilled labour need to be provided. Monthly Reports as per the above chart need to be submitted for payment purpose. 2. O & M staff be available at site 7 days a week including national holidays. 3. O & M Staff shift should be in such a way that during inverter ON & OFF time minimum one person should be present at site. 4. Manpower indicated is only minimum requirement. However, vendor to deploy required manpower to complete each activity in specified time duration. 5. The value of the Contract will remain same throughout contract period and no escalation is allowed. Hence bidder has to quote the price, considering the revision of minimum wages by State/ Central Govt., whichever is higher (Currently Central wages are higher) from time to time. Further proof of payment to engineer and workmen, ESI, PF payment shall be submitted along with invoice. 6. Monthly/Annual O&M payment to the contractor will be released on comparison of generation as per guaranteed parameter vis-a-vis Actual generation. The shortfall (if any) w.r.t guaranteed generation shall be duly supported by documentary evidence. In case of shortfall w.r.t guaranteed generation parameter, BHEL Engineering department to certify that "the reasons submitted by contractor are beyond its reasonable control". The amount equivalent to shortfall in generation may be absorbed by BHEL on exceptional basis.
Contract No: WCC-ASR-202223-021
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (To be read in conjuction with Technical Specification) (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [7 empty] | Minimum Manpower | Type of Manpower | [21 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | SCHEDULE OF WORKS FOR OPERATION AND MAINTENANCE OF 1 MW SOLAR POWER PLANT AT ONGC BASE COMPLEX RAJAHMUNDRY ANDHRA PRADESH FOR A PERIOD OF 47.7 MONTHS | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Water cleaning of solar modules of approximately 4,800 modules. Each solar module of 2m x 1m size. Water from borewells already installed at site will be used through installed pipeline network to facilitate water flow for modules cleaning. PV modules shall cleaned minimum once in 15 days. Required tools and consumables shall be supplied by bidder. 1% of the Monthly payment for this activity shall be associated with achieving the Monthly guaranteed generation and shall be certified for payment by BHEL Site in Charge based on Generation of the Month |  | 96 | Cycles | 6000 |  |  | Excess(+) | 1 | Full Conversion | INR | [17 empty] | 2 | Engineering Graduate | [21 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Grass cutting - maintaining of plant without grass PV array and nearby area shall be kept free from grass. Shall be cut once in two months. Required tools and consumables shall be supplied by bidder. |  | 24 | Cycles | 5000 |  |  | Excess(+) | 1 | Full Conversion | INR | [17 empty] | 10 | Highly Skilled | [21 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | (i) Logging of DC, AC, grid parameters (current, voltage, power, energy) at PCUs & HT panels, transformer temperatures, equipment tripping/ breakdown, grid outage as per BHEL formats. (ii) SCADA data station / PC operations/CCTV operation for daily monitoring of weather parameters, trend graphs and urgent reporting to BHEL in case of any problems / anomalies observed with any of the parameters. (iii) Monthly earth resistance measurement (Grid and individual) (iv) Solar modules string currents measured at SMBs (v) Watering of chemical earth pits Report need to be downloaded from SCADA. Daily Generation report need to be prepared and submitted to ONGC and BHEL. Monthly Generation reports to be prepared and submitted by mail to BHEL for the various parameters as Earth resistance, String current, Energy exported. String current need to be checked once in 15 days to confirm the string healthiness. If required repair need to be carried out. All cable Lugs and MC-4 connector supply in the scope of bidder. Required tools and consumables shall be supplied by bidder. |  | 47.7 | Months | 30000 |  |  | Excess(+) | 1 | Full Conversion | INR | [17 empty] | 9 | 3 Skilled + 6 Unskilled | [21 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.04 | O & M works related to Repair and maintenance with respect to 11kV Switchyard. General cleaning and Housekeeping of PV plant, Control room (with toilet cleaning) Inspection of transformer oil and silica gel need to be carried out on monthly basis. Required tightening of nut-bolts to be carried out for stopping oil leakage. Regular cleaning shall be carried out to keep PV plant in neat and clean condition. Required tools and consumables shall be supplied by bidder. |  | 47.7 | Months | 30000 |  |  | Excess(+) | 1 | Full Conversion | INR | [17 empty] | As per Requirement | As per Requirement | [21 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.05 | Carrying out Preventive and Breakdown maintenance of PV area, Inverters, Transformers and 11kV Breakers as per O&M schedule / OEM guidelines / maintenance manual. Cleaning of Inverter filter and cleaning of breaker contact and bus bar. Required tools and such as MCBs, all type of Fuses (for SMB, PCU and for all other equipments), Lights in buildings , fans, indication lamps, gaskets, silica gel, transformer oil for top-up. Acid for battery, Fastners, termination kits, cable lugs, glands and heat shrinkable sleeves of all required sizes, MC4 connectors, PCU dust filter, sanitary fittings, if required shall be supplied by vendor. Annual maintenance of all transformers with respect to BDV measurement, Oil filtering as required or annually, tightness of cables, earthing and hardwares, tightening of MMS Fasteners replacement of gasket, silica gel breather, paint touch-up, arresting oil leakages and oil top-up of all transformers and other related electrical works. |  | 47.7 | Months | 20000 |  |  | Excess(+) | 1 | Full Conversion | INR | [17 empty] | As per Requirement | As per Requirement | [21 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.06 | Checking and re-filling of all type of Fire Extinguishers All the fire extinguishers to be checked for healthiness and re-filling to be carried out as and when required. Qty: 04 nos. DCP 10 Kg, 04 nos. CO2 9 Kg, 01 no. Water 9 Ltr, 02 nos M Foam 9 Ltr. |  | 47.7 | months | 842.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [17 empty] | As per Requirement | As per Requirement | [21 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.07 | Suppy of Exide 30 nos. 6LMS75 C10 75Ah Solar Battery with battery box with fixing provision to light post (existing 2 nos bolt fixed with post), 5 nos. 18 MW Solar Street Lights, 100 meters 1.5 Sq. mm 2 core copper wire cable. Make shall be reputed and approval shall be taken from BHEL before procurement. |  | 1 | AU | 327512 |  |  | Excess(+) | 1 | Full Conversion | INR | [17 empty] | As per Requirement | As per Requirement | [21 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K14: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K15: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K16: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K17: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K18: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K19: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K20: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information