## 1AF
|  |  |  | ANNEXURE NO 1A-F |  | ind no 87959
| DETAILS OF FEEDERS /MODULES |  |  | PDB1-A | INDICATING LAMPS |  |  |  | VOLTMETER WITH VSS
|  |  | TPN-415V AC |  |  |  | DIGITAL AMETER
S NO | DESCRIPTION | AMPS | ACB/SFU RATING | CABLE SIZE FOR | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
CONNECTIONS
AMPS
1 | INCOMER > | 800A | ACB-1000A | 240MM SQX4 .X4 RUNS ARM | 3NOS. | 3NOS. | YES | NO | YES | YES
| OUTGOINGS |  | TPN SFU-
1 | I SPDL-5AXIS | 200 | 250 AMP | 185MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
2 | I SPDL-5AXIS | 200 | 250 | 185MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
3 | I SPDL-5AXIS | 200 | 250 | 185MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
4 | 3SPDL-5AXIS | 300 | 400 | 240MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
5 | T&CG | 70 | 100 | 70MM SQ X3.5 | 3NOS. | NIL | NO | YES | NO | YES
6 | ENCAPSUL M/C | 120 | 125 | 120MM SQ X3,5 | 3NOS. | NIL | NO | YES | NO | YES
7 | AREA MANAGER | 20 | 32 | 35M SQX3.5 | 3NOS. | NIL | NO | YES | NO | YES
8 | BAND SAW | 20 | 32 | 35 MM SQ.X3.5 | 3NOS. | NIL | NO | YES | NO | YES
9 | SPARE | 100 | 100 | 70MM SQ X3.5 | 3NOS. | NIL | NO | YES | NO | YES
10 | PLUG/SOCKET | 350 | 400 | 240X3.5 X2 | 3NOS. | NIL | NO | YES | NO | YES
11 | SPARE | 200 | 250 | 185MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
12 | SPARE | 70 | 100 | 70MM SQ X3.5 | 3NOS. | NIL | NO | YES | NO | YES
13 | SPARE | 20 | 32 | 35M SQX3.5 | 3NOS. | NIL | NO | YES | NO | YES
14 | EXTEN PLAN | 200 | 250 | 185MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
15 | EXTEN PLAN | 200 | 250 | 185MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
16 | EXTEN PLAN | 200 | 250 | 185MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
17 | EXTEN PLAN | 300 | 400 | 240MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
18 | EXTEN PLAN | 20 | 32 | 35M SQX3.5 | 3NOS. | NIL | NO | YES | NO | YES
19 | EXTEN PLAN | 20 | 32 | 35M SQX3.5 | 3NOS. | NIL | NO | YES | NO | YES
20 | EXTEN PLAN | 40 | 63 | 35M SQX3.5 | 3NOS. | NIL | NO | YES | NO | YES
21 | AHU 1A | 150 | 160 | 120MM SQ X3,5 | 3NOS. | NIL | NO | YES | NO | YES
22 | AHU2A | 150 | 160 | 120MM SQ X3,5 | 3NOS. | NIL | NO | YES | NO | YES
23 | AHU | 150 | 160 | 120MM SQ X3,5 | 3NOS. | NIL | NO | YES | NO | YES

## 2AF
|  |  |  | ANEEXURE NO 2AF |  | ind no 87959
|  |  |  | PDB 2-A | INDICATING LAMPS
S NO | DESCRIPTION | AMPS | ACB/SFU RATING | AL CONDUCTORCABLE SIZE FOR CONNECTIONS |  |  | DIGITAL AMETER |  | VOLTMETER WITH VSS
[5 empty] | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
1 | INCOMER > | 800A | 1000A ACB | 240MM SQX4 .X4 RUNS ARM | 3NOS. | 3 NOS. | YES | NO | YES | YES
| OUTGONGS |  | SFU
1 | H MACHINING CENTRE | 180 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
2 | H MACHINING CENTRE | 180 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
3 | H MACHINING CENTRE | 180 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
4 | 2 SPDL-5AXIS | 240 | 400 | 240MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
5 | 2 SPDL-5AXIS | 240 | 400 | 240MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
6 | EOT CRANE-1 | 30 | 32 | 35MM SQ.X3.5 | 3NOS. | NIL | NO | YES | NO | YES
7 | 3D CMM | 10 | 32 | 35MM SQ.X3.5 | 3NOS. | NIL | NO | YES | NO | YES
8 | VIBRO | 40 | 63 | 70 MM SQ.X3,5 | 3NOS. | NIL | NO | YES | NO | YES
9 | EOT CRANE-2 | 30 | 32 | 35MM SQ.X3.5 | 3NOS. | NIL | NO | YES | NO | YES
10 | SPARE | 200 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
11 | SPARE | 40 | 63 | 70 MM SQ.X3,5 | 3NOS. | NIL | NO | YES | NO | YES
12 | SPARE | 30 | 32 | 35MM SQ.X3.5 | 3NOS. | NIL | NO | YES | NO | YES
13 | EXTN PLAN | 200 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
14 | EXTN PLAN | 200 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
15 | EXTN PLAN | 240 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
16 | EXTN PLAN | 240 | 250 | 185 MM SQ. X3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
17 | EXTN PLAN | 40 | 63 | 70 MM SQ.X3,5 | 3NOS. | NIL | NO | YES | NO | YES
18 | EXTN PLAN | 40 | 63 | 70 MM SQ.X3,5 | 3NOS. | NIL | NO | YES | NO | YES
19 | EXTN PLAN | 40 | 63 | 70 MM SQ.X3,5 | 3NOS. | NIL | NO | YES | NO | YES
20 | EXTN PLAN | 240 | 400 | 240MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
21 | EXTN PLAN | 30 | 32 | 35MM SQ.X3.5 | 3NOS. | NIL | NO | YES | NO | YES
22 | AHU3A | 150 | 160 | 120MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
23 | AHU4A | 150 | 160 | 120MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
24 | AHU | 150 | 160 | 120MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES

## 3AF
|  |  |  | ANNEXURE NO - 3AF |  |  |  | IND NO 87959
|  |  |  | PDB3-A | INDICATING LAMPS |  |  |  | VOLTMETER WITH VSS
|  |  | TPN-415V AC |  |  |  | DIGITAL AMETER
S NO | DESCRIPTION | AMPS | SFU RATING | CABLE SIZE FOR | INCOM | OUTGOING | INCOMING | OUTGOING | INCOMING | OUTGOING
|  |  | AMPS | CONNECTIONS
1 | INCOMER > | 400 | SFU-400A | 240MM SQX4 .X2 RUNS UNARM | 3NOS. | 3NOS. | YES | NO | YES | YES
OUTGOINGS
1 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
2 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
3 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
4 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
5 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
6 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
7 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
8 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
9 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
10 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
11 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
12 | PS | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
13 | SPARE | 63 | 63 | 35MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
14 | LIGHT OH | 100 | 125 | 70MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES
15 | LIGHT OH | 100 | 125 | 70MM SQX3.5 UNARM | 3NOS. | NIL | NO | YES | NO | YES

## 1AC
|  | ANNEXURE NO. - 1A-C | IND NO 87959
ITEM | DESIGNATION | DESCRIPTION | TYPE MAKE | QTY | REMARK
1 | ACB | AIR CKT. BREAKER(ACB), 1000A, 415V AC, BREAKING CAPACITY 50 K.A., 3 POLE, 240 VAC MOTORCONTROL, DRAWOUT WITH CRADLE SH. REL EA1-240V AC, CT'S 800A6NO+6NC AUX. CONTACTS, 24 WAY SIC SERVICE POS. MICROSWITCH, EQUIPPED WITH REL.SR21 SHUTTERASSY.,DOOR INTERLOCKING RACKING INTERLOCK KIT | CN-CS1000C G E POWER MAKE ,ABB MAKE , C&S , SIEMENS OR L& T MAKE | 1
2 | CT1 TO CT3 | C T 800/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3
3 | F1 TO F6 | HRC FUSE LINKS 2 A | NS2 GE
4 |  | FUSE BASE 20 A | NSH GE
5 | MCB | MINIATURE CIRCUIT BREAKER 10 A 2 POLE 240 V AC COMBINED RELEASE | SIEMENS OR HAGER
6 | PB | PUSH BUTTON UNSHROUD ACTUATOR GREEN RED | 3SB1200-OAE01 SIEMENS |  | COLOUR SHALL BE AS PER DRG
7 |  | CONTACT BLOCK 1 NO + 1 NC FOR PUSH BUTTON | 3SB1400-OA SIEMENS
8 | V | DIGITAL VOLTMETER, TYPE 3 1/2 DIGITS,OPERATING VOLT. 415V ACRESOLUTION 10V RANGE, AUX. SUPPLY 240V AC, INSCRIPTIONS RY, YB, RB ENGRAVED ON INDICATING PLATE,MODEL VSS 96D IS :1248 | VSS 96 D A.E. MAKE
9 | ACB | DIGITAL AMMETER, TYPE 4 1/2 DIGITS, OPERATING CURRENT 5A, DULY CALIBRATED FOR CTR 800/5,RESOLUTION 10A RANGE, AUX. SUPPLY 240V AC, MODEL ASS 96D IS :1248 | ASS 96 D A.E. MAKE |  | RATINGS AS PER DRG / FEEDER DETAILS
10 | R,Y, B | LED PILOT LIGHT, RED,YELLOW , BLUE VOLTAGE SUITABLE FOR 42-240V AC AND 42-220V DC.TYPE 3SB14 01-2WZ3 | 3 SB 1401-2W23 SIEMENS |  | COLOUR SHALL BE AS PER DRG
11 | FSU | SWITCH DISCONNECTOR FUSE UNIT TPN, 400A, OPEN EXECUTION, (INTERIOR) WITH DIN TYPE FUSE LINKS WITH DOOR INTERLOCKING, WITH 1 NO + 1NC AUX CONTACTS TYPE FN 400 IS : 13942-3 | FN 400 L&T OR SIEMENS,ABB,C&S ,GE |  | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER DRG/FEEDER
12 |  | HRC FUSE LINKS 400 A |  |  | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER DRG/FEEDER
13 | CT1 TO CT3 | C T 400/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3 | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER DRG/FEEDER

## 2AC
|  | ANNEXURE NO. - 2A-C | IND NO 87959
ITEM | DESIGNATION | DESCRIPTION | TYPE MAKE | QTY | REMARK
1 | ACB | AIR CKT. BREAKER(ACB), 1000A, 415V AC, BREAKING CAPACITY - 50 K.A., 3 POLE, 240 VAC MOTORCONTROL, DRAWOUT WITH CRADLE SH. REL EA1-240V AC, CT'S 800A6NO+6NC AUX. CONTACTS, 24 WAY SIC SERVICE POS. MICROSWITCH, EQUIPPED WITH REL.SR21 SHUTTERASSY.,DOOR INTERLOCKING RACKING INTERLOCK KIT TYPE CN-CS 1000C | CN-CS1000C G E POWER MAKE OR OF SIEMENS OR L& T ,ABB , C&S MAKE | 1
2 | CT1 TO CT3 | C T 800/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3
3 | F1 TO F6 | HRC FUSE LINKS 2 A | NS2 GE
4 |  | FUSE BASE 20 A | NSH GE
5 | MCB | MINIATURE CIRCUIT BREAKER 10 A 2 POLE 240 V AC COMBINED RELEASE | SIEMENS OR HAGER
6 | PB | PUSH BUTTON UNSHROUD ACTUATOR GREEN RED | 3SB1200-OAE01 SIEMENS |  | COLOUR SHALL BE AS PER DRG
7 |  | CONTACT BLOCK 1 NO + 1 NC FOR PUSH BUTTON | 3SB1400-OA SIEMENS
8 | V | DIGITAL VOLTMETER, TYPE 3 1/2 DIGITS,OPERATING VOLT. 415V ACRESOLUTION 10V RANGE, AUX. SUPPLY 240V AC, INSCRIPTIONS RY, YB, RB ENGRAVED ON INDICATING PLATE,MODEL VSS 96D IS :1248 | VSS 96 D A.E. MAKE
9 | ACB | DIGITAL AMMETER, TYPE 4 1/2 DIGITS, OPERATING CURRENT 5A, DULY CALIBRATED FOR CTR 800/5,RESOLUTION 10A RANGE, AUX. SUPPLY 240V AC, MODEL ASS 96D IS :1248 | ASS 96 D A.E. MAKE |  | RATINGS AS PER DRG / FEEDER DETAILS
10 | R,Y, B | LED PILOT LIGHT, RED,YELLOW , BLUE VOLTAGE SUITABLE FOR 42-240V AC AND 42-220V DC.TYPE 3SB14 01-2WZ3 | 3 SB 1401-2W23 SIEMENS |  | COLOUR SHALL BE AS PER DRG
11 | FSU | SWITCH DISCONNECTOR FUSE UNIT TPN, 400A, OPEN EXECUTION, (INTERIOR) WITH DIN TYPE FUSE LINKS WITH DOOR INTERLOCKING, WITH 1 NO + 1NC AUX CONTACTS TYPE FN 400 IS : 13942-3 | FN 400 L&T OR SIEMENS ,ABB, C&S ,GE |  | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER DRG/FEEDER
12 |  | HRC FUSE LINKS 400 A |  |  | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER DRG/FEEDER
13 | CT1 TO CT3 | C T 400/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3 | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER DRG/FEEDER

## 3AC
|  | ANNEXURE NO.--3A-C | IND NO 87959
ITEM | DESIGNATION | DESCRIPTION | TYPE MAKE | QTY | REMARK
1 | FSU | SWITCH DISCONNECTOR FUSE UNIT TPN, 400A, OPEN EXECUTION, (INTERIOR) WITH DIN TYPE FUSE LINKS WITH DOOR INTERLOCKING, WITH 1 NO + 1NC AUX CONTACTS TYPE FN 400 IS : 13942-3 | FN 400 L&T OR SIEMENS,ABB,GE,C&S MAKE | 1
2 |  | HRC FUSE LINKS 400 A | HN L&T OR EQUIVALENT SIEMENS
3 | CT1 TO CT3 | C T 400/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3
4 | F1 TO F6 | HRC FUSE LINKS 2 A | NS2 GE
5 |  | FUSE BASE 20 A | NSH GE
6 | MCB | MINIATURE CIRCUIT BREAKER 10 A 2 POLE 240 V AC COMBINED RELEASE | SIEMENS OR HAGER
7 | PB | PUSH BUTTON UNSHROUD ACTUATOR GREEN RED | 3SB1200-OAE01 SIEMENS |  | COLOUR SHALL BE AS PER DRG
8 |  | CONTACT BLOCK 1 NO + 1 NC FOR PUSH BUTTON | 3SB1400-OA SIEMENS
9 | V | DIGITAL VOLTMETER, TYPE 3 1/2 DIGITS,OPERATING VOLT. 415V ACRESOLUTION 10V RANGE, AUX. SUPPLY 240V AC, INSCRIPTIONS RY, YB, RB ENGRAVED ON INDICATING PLATE,MODEL VSS 96D IS :1248 | VSS 96 D A.E. MAKE
10 | ACB | DIGITAL AMMETER(0-400), TYPE 4 1/2 DIGITS, OPERATING CURRENT 5A, DULY CALIBRATED FOR CTR 400/5,RESOLUTION 10A RANGE, AUX. SUPPLY 240V AC, MODEL ASS 96D IS:1248 | ASS 96 D A.E. MAKE |  | RATINGS FOR DIFFERENT FEEDERS SHALL VARY AS PER DRG/FEEDER .AS PER DRG / FEEDER DETAILS
11 | R,Y, B | LED PILOT LIGHT, RED,YELLOW , BLUE VOLTAGE SUITABLE FOR 42-240V AC AND 42-220V DC.TYPE 3SB14 01-2WZ3 | 3 SB 1401-2W23 SIEMENS |  | COLOUR SHALL BE AS PER DRG
12 | FSU | SWITCH DISCONNECTOR FUSE UNIT,TPN, 63A, OPEN EXECUTION, (INTERIOR) WITH DIN TYPE FUSE LINKS WITH DOOR INTERLOCKING , WITH 1 NO +1NC AUX CONTACTS TYPE FN63 IS :13942-3 | FN 63 L&T OR SIEMENS ,ABB,GE, C&S |  | RATINGS FOR DIFFERENT FEEDERS SHALL VARY AS PER DRG/FEEDER .AS PER DRG / FEEDER DETAILS
13 |  | HRC FUSE LINKS 63 A |  |  | RATINGS FOR DIFFERENT FEEDERS SHALL VARY AS PER DRG/FEEDER DETAILS