## Sheet1
1x370 MW YELAHANKA CCPP
TECHNICAL SPECIFICATION FOR OZONE GENERATION PLANT
REPLY TO PRE BID CLARIFICATIONS
Sr. No. | Volume No. | Page No. | ANNEXURE/Section | Clause No. | Clause Title | As mentioned in the Tender | Bidder's Query | BHEL REPLY
1 | NIT | 1 | -- | --- | Due Date | Due date of 22.06.2016 | Bidder Requesting BHEL to Provide 4 Weeks Extension for Bid Submission i.e is 25th of July 2016 | Already extended
2 | II B | Page 20 of 245 | C1-A | 9.3 | Exclusion | Air Condioning | Is BHEL is going to Provide air condiioning wherever is required? | As per Technical specification ( VOLUME II-B, SECTION –C1-A, Clause no. 9.3, Page 20 of 245) Air conditioning is excluded from Bidder's scope. Bidder to please follow technical specification.
3 | II B | Page 28 of 245 & | C1-B | 3.1 & 3.2 | 1) CAPACITY SELECTION OF OZONISATION SYSTEM AT CONDENSER 2) CAPACITY SELECTION OF RO + CW MAKE UP OZONISATION SYSTEM | CAPACITY SELECTION OF OZONISATION SYSTEM AT CONDENSER: 6Kg (N + 1)& CAPACITY SELECTION OF RO + CW MAKE UP OZONISATION SYSTEM 2kg (N + 1) Both Above systems are in One Building. | As both systems are situated in one Builiding i.e (Ozone Generation Building 1- bidder is Proposing ( N + 1) for total Capacity of 8Kg. (6kg + 2kg ) Further we will then control & maintain Ozone flow. This will help to reduce No of Equipment & future Cost of doing Maintenance Work,spare Parts etc. Requested BHEL to Accept above starement | Please follow technical specification.
4 | II B | Page 35 of 245 | C1-C | 1.1 | PG Test Procedure | To measure residual ozone at Cooling Tower basin and Raw water reservoir. Residual ozone will be 0.02 ppm at CT basin and 0.02 ppm at Raw water reservoir. | The ozone residual after the suggested pipe length will not be applicable. We are predicting large ozone gas bubbles coming out of the dosing point periodically leading to high ambient air concentration of ozone and danger to the operator. Ozone dissolution over long period of time in the side stream cannot be achieved. The ozone in the side stream is overdosed, will separate from the water phase and will travel through the pipe uncontrolled and will degas at the dosing point. This can be prevented only by moving the ozone injection point closer to the dosing point or by increasing the side stream volume to achieve max. 10 g/m³ of water; factor is approx. 10x more water. Side stream pump will be gigantic. 2) BHEL to Re - look on Location of Mixing Point ( Injector Skid Inclusive of Venturi Injector, Booster Pump, Static Mixer etc.). Ozone have to Mixed with Motive Water at Injection Point close to Dosing Point to avoid Above Condition & To Maintain Residual Ozone in Water. | Please follow technical specification.
5 | II B | Page 202 of 245 | IV | --- | SERVICE WATER ANALYSIS |  | • Suspended solids = ? mg/l • Iron = ? mg/l • manganese = ? mg/l • chloride = ? mg/l # Temperature, flow, Pressure. | Sufficient parameters have been indicated to design the system. Bidder to please follow technical specification.
6 | II B | Page 20 of 245 | C1-A | 3.36 | Under Piping | Permanent ladder for approaching the top of tanks & valves, mechanical plant and equipment, mechanical services and pipe work associated with Ozone generation Plant. | Kindly Clarify ladder Requirement.?.please specify height level above which we have to consider ladder. | As per Technical specification ( VOLUME II-B, SECTION –C1-A, Clause no. 3.36, Page 16 of 245) All necessary structural steel for pipe supporting structure, platforms, permanent ladder for approaching the top of tanks & valves, mechanical plant and equipment, mechanical services and pipe work associated with Ozone generation Plant is in Bidder's scope. Bidder to please follow technical specification.
7 | II B | Page 239 of 245 | C | --- | Common RW+ CW Ozone PID Rev.03 | As Mention in Tender PID | From Tender PID, 1 of 3 Please clarify Piping MOC from Air dryer Unit to Oxygen Generator | Piping material has been indicated in Datasheet - A ( VOLUME II-B, SECTION –C1-F, Sr. No. no. 5.1, Page 62 of 245). Bidder to please follow technical specification.
8 | II B | Page 240 of 245 | C | --- | Common RW+ CW Ozone PID Rev.03 | As Mention in Tender PID | From Tender PID, 2 of 3 Please clarify following : A) 1) Pressure,tempearture of inlet Motive Water Flow from CW Makeup Pump discharge Header 2) To Select Capacity of Booster Pump , please furnish Pressure required at dosing point. B) 1) Pressure,tempearture of inlet Motive Water Flow from ACW Makeup Pump discharge Header 2) To Select Capacity of Booster Pump , please furnish Pressure required at dosing point. | Please refer Amendment # 2.
9 | II B | Page 241 of 245 | C | --- | Common RW+ CW Ozone PID Rev.03 | As Mention in Tender PID | From Tender PID, 3 of 3 Please clarify following : 1) Way of dosing in raw water reservior Tank. 2 ) Pressure Temperature of inlet Motive Water Flow from Raw water reservior to dosing Pump. 3) To Select Capacity of Booster Pump , please Furnish Pressure required at dosing point. | Please refer Amendment # 2.