## ANNX I
REV 02
ANNEXURE - I TO NIT REF NO-PE/PG/YE1/E-5240/2016, DTD-27.05.2016
1 X 370 MW YELAHANKA CCPP
PRICE SCHEDULE FOR VENTILATION SYSTEM - SUPPLY, E&C AND MANDATORY SPARES
INDIAN BIDDER |  |  |  | SUPPLY | [5 empty] | ERECTION AND COMMISIONING |  |  | GRAND TOTAL
SL No | DESCRIPTION OF EQUIPMENT/ ITEM | QTY | UOM | UNIT EX-WORKS PRICE (DULY PACKED) (INR) | TOTAL EX- WORKS PRICE (DULY PACKED) (INR) | ED (INCLUDING CESS) @... % (INR) | CST/VAT @ ….% AGAINST FORM 'C' /EI/EII (INR) | FREIGHT CHARGES (INCLUDING SERVICE TAX) @ ….% OF TOTAL EX WORKS (INR) | TOTAL F.O.R SITE PRICE (INR) | E&C (INR) | SERVICE TAX @ …...% (INR) | E&C INCLUDING SERVICE TAX (INR) | TOTAL LUMPSUM PRICE FOR SUPPLY AND E&C WITH SERVICE TAX. (INR)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 = 2+3+4+5 | 7 | 8 | 9 = 7+8 | 10 = 6+9
1 | Total lumpsum firm prices for equipment & Services as specified, Comprising Engineering, design, manufacture, inspection & Testing at manufacturer's/subvendor's works, Painting at manufactures works, duly packed for transportation, delivery to site, unloading, storage & handling at site, fabrication, erection and commissioning, minor civil work,performance and guarantee testing, submission of as built drawing, O&M Manual, carrying out acceptance tests at site, and final painting of complete Ventilation system on turnkey basis as per specification PE-TS-409-554-A001 including mandatory spares, special tool & tackels for maintenance, commissioning spares, all taxes, duties etc.
2 | Break up prices for items covered in clause 1.0 above.
2.1 | Double skinned Packaged ambient air handling unit shall comprise of centrifugal fans (DIDW) with TEFC Squirrel Cage induction motors, drive pkg, prefilter with filter mounting frame, inlet air louvers, bird screen, VI pads, cadmium plated foundation bolts, nuts, & washers, canvass connection, outlet damper, VCD and all other accessories as required for complete installation as per specifications. The capacity of each fan shall be 100,000 CMH at 65 mm SP. | 10 | NO
2.2* | Supply air ducting (finished) for above area complete with dampers, grills (with VCD & without VCD), supports (painted) and all accessories as specified.
2.2.1* | Finished GSS (zinc coating 275 gms/sq.m) Ducting with support structure etc.
a)* | 18 G | 1700 | SQM*
b)* | 20 G | 2000 | SQM*
c)* | 22 G | 2500 | SQM*
d)* | 24 G | 200 | SQM*
2.2.2* | MS Duct With Epoxy paint for battery room. | 50 | SQM*
2.2.3* | MS Grilles with VCD | 70 | SQM*
2.2.4* | MS Grilles without VCD | 5 | SQM*
2.2.5* | Exposed duct insulation as per specifications. | 1500 | SQM*
2.2.6* | Wall mounted dampers (gravity operated) for different areas. | 20 | SQM*
2.2.7* | Inlet Louvres | 20 | SQM*
2.3* | FIRE DAMPER
a)* | Fire damper | 10 | SQM*
b)* | Motorized Actuator with single phase power supply for the above Fire damper with auto resetting, limit switches, indication lamps etc | 18 | SQM*
c)* | Fusible Link type Fire Damper | 5 | SQM*
2.4* | Roof extractor units (axial flow type) with hood, disconnect switch and all accessories as specified. Following fan shall have 15 mmwc static pressure.
a)* | Capacity 50,000 CMH with Motor rating 5.5 KW | 10 | Nos.*
b)* | Capacity 40,000 CMH with Motor rating 5.5 KW | 2 | Nos.*
c)* | Capacity 20,000 CMH with Motor rating 2.2 KW | 2 | Nos.*
2.5* | Axial flow supply fans with pre and fine filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3-phase supply). Following fan shall have 30 mmwc static pressure.
a)* | Capacity 10,000 CMH with Motor rating 2.2 KW | 12 | Nos.*
b)* | Capacity 7,500 CMH with Motor rating 1.5 KW | 2 | Nos.*
c)* | Capacity 6,000 CMH with Motor rating 1.1 KW | 2 | Nos.*
d)* | Capacity 4,000 CMH with Motor rating 0.75 KW | 8 | Nos.*
2.6* | Axial flow supply fans with pre filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3-phase supply) as specified. Following fan shall have 20 mmwc static pressure.
a)* | Capacity 10,000 CMH with Motor rating 1.5 KW | 10 | Nos.*
b)* | Capacity 7,500 CMH with Motor rating 1.1 KW | 14 | Nos.*
c)* | Capacity 6,000 CMH with Motor rating 1.1 KW | 2 | Nos.*
d)* | Capacity 4,000 CMH with Motor rating 0.75 KW | 2 | Nos.*
2.7* | Axial flow exhaust fans (Bifurcated type, spark proof construction, wall mounted) complete with casing, flame proof motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3-phase supply) as specified. Following fan shall have 15 mmwc static pressure.
a)* | Capacity 15,000 CMH with Motor rating 2.2 KW | 4 | Nos.*
b)* | Capacity 10,000 CMH withMotor rating 1.5 KW | 4 | Nos.*
c)* | Capacity 7,500 CMH with Motor rating 1.1 KW | 2 | Nos.*
d)* | Capacity 4,000 CMH with Motor rating 0.55 KW | 4 | Nos.*
e)* | Capacity 2,000 CMH with Motor rating 0.55 KW | 6 | Nos.*
2.8* | Axial flow exhaust fans (Wall mounted) complete with casing,TEFC sq cage induction motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3-phase supply) as specified.Following fan shall have 10 mmwc static pressure.
a)* | Capacity 15,000 CMH with Motor rating 1.1 KW | 4 | Nos.*
b)* | Capacity 10,000 CMH with Motor rating 0.75 KW | 6 | Nos.*
c)* | Capacity 7,500 CMH with Motor rating 0.55 KW | 6 | Nos.*
d)* | Capacity 6,000 CMH with Motor rating 0.55 KW | 2 | Nos.*
e)* | Capacity 4,000 CMH with Motor rating 0.55 KW | 2 | Nos.*
f)* | Capacity 2,000 CMH with Motor rating 0.37 KW | 10 | Nos.*
2.9 | Exhaust fan (propeller type) completes with induction motor & mounting frame MS rain protection cowl, bird screen and all other accessories as specified (suitable for 240V/ 1 phase). Following fan shall have 5 mmwc static pressure.
a)* | Capacity 1200 CMH with Motor rating 100 watts | 30 | Nos.*
2.1 | Total lumpsum price for special tools & tackles for maintenance inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up). | 1 | LOT | [6 empty] | NA | NA | NA
2.11 | Total lumpsum price for commissioning spares inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up). | 1 | LOT | [6 empty] | NA | NA | NA
2.12 | Instruments and accessories for complete hookup of ventilation system with main central control system. | 1 | LOT
2.13 | Manually operated trolly of 1 Ton cap with base area 2 m X 1.5 M | 3 | Nos. | [6 empty] | NA | NA | NA
2.14 | Total lumpsum price for Mandatory Spare inclusive of packing forwarding, transportation up to site, etc. (Bidder to submit item-wise price break-up seperately). | 1 | LOT | [6 empty] | NA | NA | NA
NOTES
1 | The bidder shall furnish unit rates for variable item (marked *) for necessary adjustment (plus or minus) variation during detailed engg. stage.
2 | Price format shall not be changed by the bidder as the bidder may get disqualified by doing so.
3 | Item mentioned against Sl. No. 2.10,2.11,2.13 and 2.14 are supply item only, E&C for the same is not applicable.

## MANDATORY SPARES
REV02
ANNEXURE - II TO NIT REF NO-PE/PG/YE1/E-5240/2016, DTD-27.05.2016
1 X 370 MW YELAHANKA CCPP
PRICE SCHEDULE FOR VENTILATION SYSTEM - MANDATORY SPARES
MANDATORY SPARES SUPPLY
SL No | DESCRIPTION OF EQUIPMENT/ ITEM | QTY/UOM | UNIT EX-WORKS PRICE (DULY PACKED) (INR) | TOTAL EX- WORKS PRICE (DULY PACKED) (INR) | ED (INCLUDING CESS) @... % (INR) | CST/VAT @ ….% AGAINST FORM 'C' /EI/EII (INR) | FREIGHT CHARGES (INCLUDING SERVICE TAX) @ ….% OF TOTAL EX WORKS (INR) | TOTAL F.O.R SITE PRICE (INR)
1 | CENTRIFUGAL FANS
1.1 | V-BELTS | 1 SET
1.2 | BLOWER BEARING | 1 SET
1.3 | BLOWER MOTOR BEARINGS | 1 SET
1.4 | GASKET | 1 SET
1.5 | MOTOR | 1 NO
2 | AXIAL FANS/ ROOF EXTRACTOR (FOR EACH SIZE)
2.1 | FAN BEARINGS | 1 SET
2.2 | FAN MOTOR BEARING | 1 SET
2.3 | FAN MOTOR | 1 NO
NOTES
1 | The bidder shall furnish unit rates for variable item (marked *) for necessary adjustment (plus or minus) variation during detailed engg. stage.
2 | Price format shall not be changed by the bidder as the bidder may get disqualified by doing so.

## COW
DEVIATION SHEET (COST OF WITHDRAWL)
PROJECT:- 370 MW YELAHANKA CCPP
PACKAGE:- VENTILATION SYSTEM
TENDER ENQUIRY REFERENCE:-PE/PG/YE1/E-5240/2016, DTD-27.05.2016
NAME OF VENDOR:-
SL NO | VOULME/ SECTION | PAGE NO. | CLAUSE NO. | TECHNICAL SPECIFICATION/ TENDER DOCUMENT | COMPLETE DESCRIPTION OF DEVIATION | COST OF WITHDRAWL OF DEVIATION | REFERENCE OF PRICE SCHEDULE ON WHICH COST OF WITHDRAWL OF DEVIATION IS APPLICABLE | NATURE OF COST OF WITHDRAWL OF DEVIATION (POSITIVE/ NEGATIVE) | REASON FOR QUOTING DEVIATION
TECHNICAL DEVIATIONS
COMMERCIAL DEVIATIONS
PARTICULARS OF BIDDERS/ AUTHORISED REPRESENTATIVE
NAME |  |  |  | DESIGNATIONS |  | SIGN & DATE
NOTES:
1. For self manufactured items of bidder, cost of withdrawl of deviation will be applicable on the basic price (i.e. excluding taxes, duties & freight) only.
2. For directly dispatchable items, cost of withdrawl of deviation will be applicable on the basic price including taxes, duties & freight.
3. All the bidders have to list out all their Technical & Commercial Deviations (if any) in detail in the above format.
4. Any deviation not mentioned above and shown separately or found hidden in offer, will not be taken cognizance of.
5. Bidder shall submit duly filled unpriced copy of above format indicating "quoted" in "cost of withdrawl of deviation" column of the schedule above along with their Techno-commercial offer, wherever applicable.
6. Bidder shall furnish price copy of above format along with price bid.
7. The final decision of acceptance/ rejection of the deviations quoted by the bidder shall be at discretion of the Purchaser.
8. Bidders to note that any deviation (technical/commercial) not listed in above and asked after Part-I opening shall not be considered.
9. For deviations w.r.t. Payment terms, Liquidated damages, Firm prices and submission of E1/ E2 forms before claiming 10% payment, if a bidder chooses not to give any cost of withdrawl of deviation loading as per Annexure-VIII of GCC, Rev-06 will apply. For any other deviation mentioned in un-priced copy of this format submitted with Part-I bid but not mentioned in priced copy of this format submitted with Priced bid, the cost of withdrawl of deviation shall be taken as NIL.
10. Any deviation mentioned in priced copy of this format, but not mentioned in the un-priced copy, shall not be accepted.
11. All techno-commercial terms and conditions of NIT shall be deemed to have been accepted by the bidder, other than those listed in unpriced copy of this format.
12. Cost of withdrawl is to be given seperately for each deviation. In no event bidder should club cost of withdrawl of more than one deviation else cost of withdrawl of such deviations which have been clubbed together shall be considered as NIL.
13. In case nature of cost of withdrawl (positive/negative) is not specified it shall be assumed as positive.
14. In case of descrepancy in the nature of impact (positive/ negative), positive will be considered for evaluation and negative for ordering.

## GPC
NIT REF NO-PE/PG/YE1/E-5240/2016, DTD-27.05.2016
1 X 370 MW YELAHANKA CCPP
VENTILATION SYSTEM - GAURANTEE POWER CONSUMPTION
S.NO. | DESCRIPTION OF EQUIPMENT | NO OF EQUIPMENT |  | TOTAL GUARANTEED POWER CONSUMPTION FOR EACH EQUIPMENT AT MOTOR INPUT TERMINAL AND CONTROL PANEL (IN KW) | DUTY FACTOR | TOTAL KW
|  | WORKING | STANDBY
|  | 3A | 3B | 4 | 5 | 6=3Ax4x5
1 | VENTILATION SYSTEM FOR TG BUILDING
1.1 | Centrifugal Fan of cap. 1, 00,000 CMH at 65 mmwc static pr for air washers. | 10 | 0
1.2 | RE Units 50,000 CMH at 15mmwc | 10 | 0
|  |  |  | TOTAL (KW) |  | 370
NOTES:
1 | Estimated power consumption (EPC) figure for the system (for working drives only) has been considered as 390 KW. So long bidder's quoted guaranteed power consumption (GPC) above remains within this EPC, there will be no technical loading of bid on power consumption for evaluation. However, if bidder's quoted GPC exceeds EPC, there shall be technical loading of bid for evaluation @ Rs 136000/-per KW of additional power over EPC.
2 | Bidder’s guaranteed power consumption at motor input terminals (not shaft power) as furnished in relevant schedule shall be demonstrated by the successful bidder during performance testing at works/ site. In case power consumption is noted higher than EPC / bidder's quoted GPC whichever is higher, during inspection/ PG test, penalty @ Rs 136000/-per KW shall be levied on vendor.