## MAIN SHEET
Main Price Schedule
NAME OF THE BIDDER
NAME OF PROJECT: |  | 2X660MW ENNORE TPS
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-412-554-A002
[5 empty] | Supply |  |  | Service |  | Taxes
S. No. | DESCRIPTION |  | UOM | QTY | Total Ex-Works (excluding GST) (INR) | Freight in % | Total Freight | Unit Price (INR) | Total Price (INR) | GST type | GST rate in % | GST amount in Rs. | Total Price Including Freight & GST (INR)
1 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part, Services part and Mandatory spares, comprising of Design, Engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables, mandatory spares alongwith spares for erection, startup and commissioning as required, forwarding, proper packing, shipment and delivery at site, unloading, handling, transportation & storage at site, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), submission of “As Built” drawings and O&M manuals, training of customer/client O&M staff and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. |  | Lot | 1 | [8 empty] | 0
2 | MAJOR BREAK-UP OF PRICES GIVEN IN 1.0 ABOVE.
2.1 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part comprising of Design, Engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables alongwith spares for erection as required, startup and commissioning spares as required, forwarding, proper packing, shipment and delivery at site for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | 0 |  | 0 | NA |  |  |  | 0 | 0
2.2 | Total lumpsum firm prices inclusive of all prevailing taxes, duties and other levies for Services part comprising of service part for unloading, handling, transportation & storage at site, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | NA |  |  | 0 | 0 |  |  | 0 | 0
2.3 | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for Mandatory spares comprising of manufacture, fabrication, assembly, inspection / testing (as applicable) at vendor's & sub-vendor’s works, painting, forwarding, proper packing, shipment, delivery at site & guarantee as per tender technical specification above, amendment & agreements till placement of order. (Price break up of mandatory spares is to be furnished as per Annexure- II) |  | Lot | 1 | 0 |  | 0 | NA |  |  |  | 0 | 0
Note: 1) Bidder to quote the Prices in ‘figures’ along with corresponding ‘words’. 2) Lumpsum price quoted at Sl.no 1.0 shall be considered for evaluation.

## ANNEXURE-I
ANNEXURE - I : PRICE BREAKUP FOR SUPPLY PART
NAME OF PROJECT: |  | 2X660MW ENNORE TPS
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-412-554-A002
| ITEM DESCRIPTION | QTY. | UOM | SUPPLY |  | E&C
|  |  |  | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR) | Unit E&C Price (INR) | Total E&C Price (INR)
BREAK-UP OF ITEMS MENTIONED AT S. NO. 2.1 OF MAIN SHEET
1 | Sheet metal type air washer unit with centrifugal fan (DIDW) with motor, pumps with motors, air washer internals, inlet air louvers, filters, piping as per IS:1239, part-I(heavy class galvanised), valves, nozzles, level switch, temp indicators, back wash arrangement, galvanised drain piping etc as per specification of capacity 2,50,000 CMH. Each air washer has 3 no centrifugal fan ( 3 x 33% duty) of capacity 83,500 CMH each at min. 90 mm SP. | 8 | Nos. |  | 0 |  | 0
2 | Unitary air filtration unit with centrifugal fan (SISW) with motor, pumps with motors, filters, UAF internals, piping as per IS: 1239 part-I (heavy class galvanised), valves for auto start of standby equipment, nozzles, level switch, pressure switches, Temp. indicators, back wash arrangement, galvanised drain piping etc. as per spec. of capacity 80,000 CMH. Each UAF has 1 no centrifugal fan ( 1 x 100% duty) of capacity 80,000 CMH at min.75 mm SP. | 2 | Nos. |  | 0 |  | 0
3* | Supply air ducting (finished) for above area complete with dampers, grills (with VCD & without VCD),supports (painted) and all accessories as specified.
3.1* | Finished GSS (zinc coating 275 gms/sq.m) Ducting with support structure etc.
a)* | 18 G | 6500 | SQM* |  | 0 |  | 0
b)* | 20 G | 1500 | SQM* |  | 0 |  | 0
c)* | 22 G | 5000 | SQM* |  | 0 |  | 0
d)* | 24G | 1000 | SQM* |  | 0 |  | 0
3.2* | MS Duct With Epoxy paint for battery room. | 10 | SQM* |  | 0 |  | 0
3.3* | MS Grilles with VCD | 170 | SQM* |  | 0 |  | 0
3.4* | MS Grilles without VCD | 5 | SQM* |  | 0 |  | 0
3.5* | Exposed duct insulation with fibre glass insulation with cladding as per specifications. | 2100 | SQM* |  | 0 |  | 0
3.6* | Wall mounted dampers (gravity operated) for different areas. | 20 | SQM* |  | 0 |  | 0
3.7* | Inlet Louvres | 25 | SQM* |  | 0 |  | 0
3.8* | VOLUME CONTROL DAMPERS in GI construction as per specifications | 70 | SQM* |  | 0 |  | 0
4* | FIRE DAMPER
a)* | Fire damper | 25 | SQM*
b)* | Motorized Actuator with single phase power supply for the above Fire damper with auto resetting, limit switches, indication lamps etc | 24 | Nos.* |  | 0 |  | 0
c)* | Fusible Link type Fire Damper | 2 | SQM* |  | 0 |  | 0
5* | Roof extractor units (axial flow type) with hood, disconnect switch and all accessories as specified. Following fan shall have 15 mmwc static pressure.
a)* | Capacity 50,000 CMH with Motor rating 5.5 KW | 46 | Nos.* |  | 0 |  | 0
b)* | Capacity 40,000 CMH with Motor rating 5.5 KW | 14 | Nos.* |  | 0 |  | 0
c)* | Capacity 20,000 CMH with Motor rating 2.2 KW | 1 | Nos.* |  | 0 |  | 0
6* | Axial flow supply fans with pre and fine filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3‐phase supply). Following fan shall have 32 mmwc static pressure.
a)* | Capacity 10,000 CMH with Motor rating 2.2 KW | 29 | Nos.* |  | 0 |  | 0
b)* | Capacity 7,500 CMH with Motor rating 1.5 KW | 2 | Nos.* |  | 0 |  | 0
c)* | Capacity 6,000 CMH with Motor rating 1.1 KW | 2 | Nos.* |  | 0 |  | 0
d)* | Capacity 4,000 CMH with Motor rating 0.75 KW | 2 | Nos.* |  | 0 |  | 0
7* | Axial flow supply fans with pre filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3 ‐phase supply) as specified. Following fan shall have 20 mmwc static pressure.
a)* | Capacity 10,000 CMH with Motor rating 1.5 KW | 8 | Nos.* |  | 0 |  | 0
b)* | Capacity 7,500 CMH with Motor rating 1.1 KW | 2 | Nos.* |  | 0 |  | 0
c)* | Capacity 6,000 CMH with Motor rating 1.1 KW | 2 | Nos.* |  | 0 |  | 0
d)* | Capacity 4,000 CMH with Motor rating 0.75 KW | 2 | Nos.* |  | 0 |  | 0
8* | Axial flow exhaust fans (Bifurcated type, spark proof construction, wall mounted) complete with casing, flame proof motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3‐phase supply) as specified. Following fan shall have 15 mmwc static pressure.
a)* | Capacity 15,000 CMH with Motor rating 2.2 KW | 38 | Nos.* |  | 0 |  | 0
b)* | Capacity 10,000 CMH withMotor rating 1.5 KW | 2 | Nos.* |  | 0 |  | 0
c)* | Capacity 7,500 CMH with Motor rating 1.1 KW | 3 | Nos.* |  | 0 |  | 0
d)* | Capacity 4,000 CMH with Motor rating 0.55 KW | 13 | Nos.* |  | 0 |  | 0
e)* | Capacity 2,000 CMH with Motor rating 0.55 KW | 8 | Nos.* |  | 0 |  | 0
9* | Axial flow exhaust fans (Wall mounted) complete with casing,TEFC sq cage induction motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3‐phase supply) as specified.Following fan shall have 10 mmwc static pressure.
a)* | Capacity 15,000 CMH with Motor rating 1.1 KW | 39 | Nos.* |  | 0 |  | 0
b)* | Capacity 10,000 CMH with Motor rating 0.75 KW | 16 | Nos.*
c)* | Capacity 7,500 CMH with Motor rating 0.55 KW | 4 | Nos.* |  | 0 |  | 0
d)* | Capacity 6,000 CMH with Motor rating 0.55 KW | 3 | Nos.* |  | 0 |  | 0
e)* | Capacity 4,000 CMH with Motor rating 0.55 KW | 3 | Nos.* |  | 0 |  | 0
f)* | Capacity 2,000 CMH with Motor rating 0.37 KW | 1 | Nos.* |  | 0 |  | 0
10* | Exhaust fan (propeller type) completes with induction motor & mounting frame MS rain protection cowl, bird screen and all other accessories as specified (suitable for 240V/ 1 phase). Following fan shall have 5 mmwc static pressure.
a)* | Capacity 1200 CMH with Motor rating 100 watts | 178 | Nos.* |  | 0 |  | 0
11* | Handling arrangement for Ventilation equipments
a)* | Manually operated, platform trolley of 1 Ton capacity with base area 2m x 1.5m | 1 | Nos.* |  | 0 |  | 0
b)* | 1T Chain pulley block with travelling trolley | 1 | Nos.* |  | 0 |  | 0
12 | Total lumpsum price for special tools & tackles for maintenance inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item‐wise price break‐up‐As per Appendix A). | 1 | LOT | 0 | 0
13 | Total lumpsum price for commissioning spares inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item‐wise price break‐up‐As per Appendix B). | 1 | LOT | 0 | 0
14* | FIELD INSTRUMENTS like pressure gauge, temperature gauge, pressure switch, differential pressure switch, velocity sensor/static pressure sensor,flow switch and other instrument required for Ventilation System etc | 1 | LOT |  | 0 |  | 0
a)* | Pressure guage | 20 | Nos.* |  | 0 |  | 0
b)* | Differential pressure switch | 10 | Nos.* |  | 0 |  | 0
c)* | Differential pressure guage | 10 | Nos.* |  | 0 |  | 0
d)* | Level Guage | 10 | Nos.* |  | 0 |  | 0
e)* | Level switch | 20 | Nos.*
f)* | Pressure transmitter (Air Duct) | 20 | Nos.* |  | 0 |  | 0
g)* | Pressure transmitter (Water Line) | 20 | Nos.* |  | 0 |  | 0
h)* | Temperature guage | 10 | Nos.* |  | 0 |  | 0
i) | Any other instrument required for completion and proper funcitioning of the system | 1 | LOT |  | 0 |  | 0
15* | Non Chemical Type Scale Preventor
a)* | 250 CMH | 8 | Nos.* |  | 0 |  | 0
b)* | 80 CMH | 2 | Nos.* |  | 0 |  | 0
16* | Local Control panel for local operation of each air washer and UAF along with their accessories for hooking up with DCS | 10 | Nos.* |  | 0 |  | 0
17 | Any other item not indicated above, but required to make the system complete in all respects. | 1 | LOT |  | 0 |  | 0
Total |  |  |  |  | 0 |  | 0
NOTES
1 | The bidder shall furnish unit rates for variable item (marked *) for necessary adjustment (plus or minus) variation during detailed engg. stage. The unit rates quoted above shall be considered for adjustment and no separate unit rates shall be quoted. Unit rates shall be valid throughout the contract. Final qty. shall be paid as per actual measurment at site for erection for all the variable items.
2 | Bidder to note that above BOQ for this tender has to be read in conjunction with tender specification. Any item, if not mentioned in above BOQ but indicated in tender specification and required for completion of the system shall deemed to be included in above price.
3 | Price format shall not be changed by the bidder as the bidder may get disqualified by doing so.
4 | Any cell left blank in the unpriced schedule shall be treated as "Quoted" and is included in total price.
5 | In case of difference in capacities /rating of various equipment mentioned in this price format vis a vis those mentioned in approved /finalised drawing documents attached in tender specification or as per requirement of the system, more stringent capacity /rating as per purchasers interpretation shall be supplied by the bidder without any commercial implication to BHEL.

## APPENDIX-A
APPENDIX-A Special tools & tackles for maintenance
NAME OF PROJECT: |  | 2X660MW ENNORE TPS
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-412-554-A002
SL NO | DESCRIPTION | UOM | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | Measuring tape | NO. | 1 |  | 0
2 | Tachometer | NO. | 1 |  | 0
3 | Double ended spanner | SET | 1 |  | 0
4 | Ring spanners | SET | 1 |  | 0
5 | Gasket punch | NO. | 1 |  | 0
6 | Center punch | NO. | 1 |  | 0
7 | Hammer with wooden handles | NO. | 1 |  | 0
8 | Scissors for sheet metal cutting | NO. | 1 |  | 0
9 | Torch light (suitable for 2 cells) | NO. | 1 |  | 0
10 | Multimeter | NO. | 1 |  | 0
11 | Anemometer | NO. | 1 |  | 0
12 | Compound pressure gauge | NO. | 1 |  | 0
13 | Slide wrench 8” | NO. | 1 |  | 0
14 | Slide wrench 10” | NO. | 1 |  | 0
15 | Slide wrench 6” | NO. | 1 |  | 0
16 | Box spanner set | SET | 1 |  | 0
17 | Screw driver set | SET | 1 |  | 0
18 | Align key set | SET | 1 |  | 0
19 | MS tool box | NO. | 1 |  | 0
Total |  |  |  |  | 0
NOTES
1 | ABOVE IS THE MINIMUM LIST. ANY OTHER TOOL / TACKEL REQUIRED FOR THE SYSTEM SHALL ALSO BE PROVIDED BY THE VENDOR WITHOUT ANY COST IMPLICATION.

## APPENDIX-B
APPENDIX-B Commissioning spares
NAME OF PROJECT: |  | 2X660MW ENNORE TPS
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-412-554-A002
SL NO | DESCRIPTION | UOM | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | FAN BELTS | SET | 1 |  | 0
2 | PRESSURE GAUGE | NO. | 1 |  | 0
3 | TEMPERATURE GAUGE | NO. | 1 |  | 0
4 | FILTER | SET | 1 |  | 0
Total |  |  |  |  | 0
NOTES
1 | Above is the minimum list. Any other commissioning spare required for AC system w.r.t. Mechanical, Electrical and C&I part shall also be provided by the Bidder as per system / customer requirement without any commercial & Delivery implication to BHEL.

## ANNEXURE-II
ANNEXURE - II LIST OF MANDATORY SPARES
NAME OF PROJECT: |  | 2X660MW ENNORE TPS
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-412-554-A002
S. No. | Description | QTY | Total Ex-Works Price (INR)
A | MECHANICAL AND GENERAL
1 | CENTRIFUGAL FANS
1.1 | V-BELTS | 2 SETS OF EACH TYPE
1.2 | BLOWER BEARING SETS | 2 SETS OF EACH TYPE
1.3 | BLOWER MOTOR BEARINGS | 2 SETS OF EACH TYPE
1.4 | SEAL GASKET AND OTHER WEAR OUT PARTS IN SETS | 2 SETS OF EACH TYPE
1.5 | VIBRATION ISOLATORS | 2 SETS OF EACH TYPE
2 | AXIAL FANS
2.1 | FAN BEARINGS | 2 SETS OF EACH TYPE
2.2 | FAN MOTOR BEARING | 2 SETS OF EACH TYPE
2.3 | DRY FILTERS | 2 SETS OF EACH TYPE AND SIZE
3 | AIR WASHER SYSTEM
3.1 | WATER STRAINERS | 2 SETS OF EACH SIZE
3.2 | SPRAY NOZZLES | 2 SETS OF EACH SIZE
3.3 | WATER REPELLANT TYPE FILTERS | 2 SETS OF EACH SIZE
4 | HORIZONTAL CENTRIFUGAL PUMP
4.1 | IMPELLER FOR EACH OF PUMP SET | 2 SETS OF EACH TYPE
4.2 | BEARINGS | 2 SETS OF EACH TYPE
4.3 | SHAFT SLEEVES | 2 SETS OF EACH TYPE
4.4 | BEARINGS MOTOR | 2 SETS OF EACH TYPE
B | ELECTRICAL
1 | Terminal plates
a | For motors upto 30 KW | 10 NOS. EACH FOR SMALL MOTORS UPTO 30 KW
b | For motors above 30 KW | 4 NOS. EACH FOR MORE THAN 30 KW
2 | Heaters | 2 SETS
3 | Greasing arrangements | 4 SETS OF EACH TYPE OF MOTOR.
4 | Motor of each type and rating | 10% OF THE INSTALLED QUANTITY OR MINIMUM 1 NUMBER WHICHEVER BE HIGHER
5 | Bearings (DE and NDE) for each type and rating of motor | 4 SETS
C | CONTROL AND INSTRUMENTATION
| Each type of lamps, PBs, ILPBs, fuse, MCB, MCCB used in the equipment/system. | 20% OF QTY INSTALLED.
a) | Measuring Instruments
1 | Indicators, Recorders, Electrical Metering and Skid Mounted Instruments
1.1 | Indicators, recorders and meters offered from each model for the project. These instruments shall be supplied with three sets of blank scales. | 10% OF INSTALLED OF EACH TYPE/MODEL OR A MINIMUM OF ONE NUMBER FOR EACH MODEL AND TYPE, WHICHEVER IS MORE
1.2 | For skid mounted instruments | 10% OF INSTALLED OF EACH TYPE/MODEL OR A MINIMUM OF ONE NUMBER FOR EACH MODEL AND TYPE, WHICHEVER IS MORE
2 | Temperature Elements and Thermowells
2.1 | Thermocouple/RTD elements | 10% SPARE FOR EACH TYPE AND LENGTH OF ELEMENT FURNISHED WITH THERMOCOUPLE/RTD ASSEMBLIES, OR A MINIMUM OF ONE NUMBER OF EACH TYPE & LENGTH, WHICHEVER IS MORE.
2.2 | Thermowells | 10% SPARE FOR EACH TYPE TEMPERATURE SENSORS OR MINIMUM OF ONE FOR TYPE, WHICHEVER IS MORE
3 | Temperature Transmitters and Electronic Transmitters (For Pressure, DP, Temp, Flow, Level), Temperature, Pressure, Flow & Level Switch, safety switches, Gauges, meters, Transducer or any other instrument etc. | 10% OF TOTAL NUMBER OF INSTRUMENTS/TRANSDUCERS OFFERED FOR EACH MODEL AND TYPE FOR THE PROJECT OR A MINIMUM OF ONE NUMBER, WHICHEVER MORE.
b) | Relay based Control Panels
1 | LEDs for indicating lights | 10% OF QTY INSTALLED.
2 | Control circuit fuses/MCB/MCCB/ Semiconductor Fuses | 300% OF INSTALLED OF EACH TYPE, CURRENT RATING.
3 | Relays modules & contactors. | 20% SPARE OF QTY INSTALLED OF EACH TYPE & RATING
c) | Erection hardware
1 | Instrument valves | 10% OF EACH TYPE & SIZE INSTALLED
2 | Condensate pots of each type & Size installed | 10% OF TOTAL NUMBER OF INSTALLED OR FOUR NUMBERS WHICHEVER IS HIGHER .
3 | Manifold | 10% OF EACH TYPE & SIZE INSTALLED
4 | Fittings | 10% OF EACH TYPE & SIZE INSTALLED
e) | Mandatory Spares for Control valves, Power Cylinder, Control Dampers, Actuators and Accessories
1 | Following spares shall be furnished for control valves, Power Cylinder, Control Dampers as applicable.
2 | One set of spare control valve stem packing for each control valve.
3 | Two moulded rubber diaphragms for each control valve.
4 | One sets of each of O-rings and rubber gaskets for each control valve.
5 | 100 percent qty. of lubricants for gaskets for each control valve on one year consumption basis.
6 | 2 sets of limit switches and 1 set of valve positioner for each control valve.
7 | 20 percent of position transmitter (4-20mA) for total qty. of control valve.
8 | One (1) set of valve trims (such as plug, stem, seat ring /cage, guide bushing, stem lock pin, packing retaining ring, etc) for each control valve.
9 | One completes actuator of each type or min 10% for each type and size whichever is more.
10 | 20 percent of Solenoid valves or min 2 no. of each type for total qty. of control valves.
11 | 20% of I to P converters, Pressure regulators.
f) | Mandatory spares not covered above
Bidder to supply 10% or 1 no. (whichever is more) of each type of sensor/instrument, instrumentation/mechanical fittings etc for any other electronic system, feeder control cabinets, hydrastep (EWLI), Vibration Monitoring System, CCTV, C&I Lab Instruments, On line Carbon in Ash analyser system, On line Coal mass flow/speed measurement system, On line secondary air flow measurement system Mass Flow meter, Solid flow meter, 3 D Acoustic type level transmitters, Nucleonic & non nucleonic density transmitter etc
| TOTAL |  | 0
Notes: a) Mandatory spares listed above is bare minimum requirement. In case any additional mandatory spares requirement is covered elsewhere in the tender specification apart from specified above, same shall be deemed to have been covered in bidders scope of supply. b) One set corresponds to actual quantity of components and devices as installed for the equipment at Site. c) All mandatory spares shall be supplied as per the requirement of the specifications. In case any spare indicated in the specification is “not applicable” for particular equipment, then suitable applicable alternate spare has been offered / shall be supplied by the bidder without any financial implication." d) Any item which is quoted as “not applicable” by the bidder in the above list and is found to be “applicable” at a later date shall be supplied by the bidder without any commercial and delivery implication. e) For spares mentioned in %age of the total quantity, the quantity of mandatory spares offerred shall be rounded up to the next higher number. f) Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price