## MAIN SHEET
PRICE FORMAT
NAME OF THE BIDDER
NAME OF PROJECT: |  | 2X 660 MW TALCHER TPP STAGE-III
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-497-554-A002
[5 empty] | Supply |  |  | Service |  | Taxes
S. No. | DESCRIPTION |  | UOM | QTY | Total Price (INR) | Freight in % | Total Freight | Unit Price (INR) | Total Price (INR) | GST type | GST rate in % | GST amount in Rs. | Total Price Including Freight & GST (INR) | Total Price Including Freight & GST (INR) in words
1 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part, Services part and Mandatory spares comprising of design (i.e.preparation and submission of drawing /documents including “As Built” drawings and O&M manuals), engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable) fill of lubricants & consumables, mandatory spares alongwith spares for erection, startup and commissioning as required, forwarding, proper packing, shipment and delivery at site, unloading, handling, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff, Operation & Maintenance of Ventilation System (24x7) before handing over after commissioning, and handover in flawless condition of the package to the end customer complete with all accessories, for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. |  | Lot | 1 | [8 empty] | 0
2 | MAJOR BREAK-UP OF PRICES GIVEN IN 1.0 ABOVE.
2.1 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part comprising of Design (i.e. Preparation and submission of drawing /documents including “As Built” drawings and O&M manuals) manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables along with spares for erection as required, start-up and commissioning spares as required, forwarding, proper packing, shipment and delivery at site for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | 0 |  | 0 | NA |  |  |  | 0 | 0
2.2 | Total lumpsum firm prices inclusive of all prevailing taxes, duties and other levies for Services part comprising for unloading, handling, transporation to site, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff and handover in flawless condition of the package to the end customer complete with all accessories, for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | NA |  |  | 0 | 0 |  |  | 0 | 0
2.3 | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for Mandatory Spares comprising of manufacture, fabrication, assembly, inspection / testing (as applicable) at vendor's & sub-vendor’s works, painting, forwarding, proper packing, shipment, delivery at site & guarantee as per tender technical specification above, amendment & agreements till placement of order. (Price break up of mandatory spares is to be furnished as per Annexure- II) |  | Lot | 1 | 0 |  | 0 | NA |  |  |  | 0 | 0
2.4* | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for providing Operation and Maintenance Service (24x7) including manpower, supervision, consumables etc. for operation & maintenance of Ventilation System after commissioning of Ventilation system before final handing over to end customer in flawless condition for the scope defined as per technical specification. |  | Months* | 6 | NA |  |  |  | 0 |  |  | 0 | 0
Note: 1) Bidder to quote the Prices in ‘figures’ along with corresponding ‘words’. 2) Lumpsum price quoted at Sl.no 1.0 shall be considered for evaluation. 3) For detailed scope of Operation and Maintenance Services, Technical Specification to be referred. Any variation in no. of months shall be exercised based on unit rate arrived from price quoted against Sl.no 2.4 above.

## ANNEXURE-I_VENT
ANNEXURE - I : PRICE BREAKUP
NAME OF PROJECT: |  | 2X 660 MW TALCHER TPP STAGE-III
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-497-554-A002
| ITEM DESCRIPTION | QTY. | UOM | SUPPLY |  | E&C
|  |  |  | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR) | Unit E&C Price (INR) | Total E&C Price (INR)
BREAK-UP OF ITEMS MENTIONED AT S. NO. 2.2 OF MAIN SHEET
1* | Double skin Sheet metal containerized type modular air washer unit (closed from all around and bottom) with centrifugal fan (DIDW) with motor, pumps with motors, air washer internals, inlet air louvers, non returm damper, motorised damper, manual damper, filters, piping as per IS:1239, Part-I (heavy class galvanised), valves, instruments, nozzles, back wash arrangement, galvanised drain piping etc. along with support for suction and discharge plenum etc as per specification of capacity 1,00,000 CMH. Each air washer has 1 number centrifugal fan ( 1 x 100% duty) of capacity 1,00,000 CMH at min. 60 mm SP. All parts of Fans & Motors shall be fixed on channel. | 20 | NO* |  | 0 |  | 0
2* | Double skin Sheet metal containerized type modular air washer unit (closed from all around and bottom) with centrifugal fan (DIDW) with motor, pumps with motors, air washer internals, inlet air louvers, non returm damper, motorised damper, manual damper, filters, piping as per IS:1239, Part-I (heavy class galvanised), valves, instruments, nozzles, back wash arrangement, galvanised drain piping etc. along with support for suction and discharge plenum etc as per specification of capacity 50,000 CMH. Each air washer has 1 number centrifugal fan ( 1 x 100% duty) of capacity 50,000 CMH at min. 60 mm SP. All parts of Fans & Motors shall be fixed on channel. | 2 | NO* |  | 0 |  | 0
3* | Double skin Sheet metal containerized type modular Unitary air filtration unit (closed from all around and bottom) with centrifugal fan (DIDW) with motor, pumps with motors, filters, UAF internals, inlet air louvers, non returm damper, motorised damper, manual damper, piping as per IS: 1239 part I (heavy class galvanised), valves, instruments, nozzles, back wash arrangement, galvanised drain piping, etc. along with support for suction and discharge plenum as per specification of capacity 75,000 CMH. Each Unitary air filtration unit has 1 number centrifugal fan (1 x 100% duty) of capacity 75,000 CMH at min. 50 mmwc static pressure. | 4 | NO* |  | 0 |  | 0
4* | Double Skinned (0.6 mm thick pre coated outer skin, 0.6 mm thick plain GI inner skin with CFC free PUF nsulation in between) Fan Filter Unit (FFU) shall comprise of centrifugal fans (DIDW) with TEFC Squirrel Cage induction motors, drive pkg, prefilter with filter mounting frame, inlet air louvers, bird screen, VI pads, Support Channel, SS foundation bolts, nuts, & washers, Fire retardent canvass connection, outlet damper, VCD and all other accessories as required for complete installation. All parts of Fans & Motors shall be fixed on channel. Entire skid shall be placed on flat foundation without any pocket. The capacity of FFU shall be 25,000 CMH at min. 40 mmwc SP having 1x 100% fan. | 4 | NO* |  | 0 |  | 0
5 | Supply air ducting (finished) for above area complete with dampers, grills (with VCD & without VCD), supports (painted) and all accessories as specified.
5.1* | Finished GSS (zinc coating 275 gms/sq.m) Ducting with support structure etc.
a)* | 18 G | 3600 | SQM* |  | 0 |  | 0
b)* | 20 G | 2500 | SQM* |  | 0 |  | 0
c)* | 22 G | 6200 | SQM* |  | 0 |  | 0
d)* | 24 G | 3100 | SQM* |  | 0 |  | 0
5.2* | MS Duct With Epoxy paint for battery room. | 200 | SQM* |  | 0 |  | 0
5.3* | MS Grilles/Diffusers with VCD complete with fixing frames, nuts, bolts, gaskets, washers etc | 100 | SQM* |  | 0 |  | 0
5.4* | MS Grilles/Diffusers without VCD complete with fixing frames, nuts, bolts, gaskets, washers etc | 10 | SQM* |  | 0 |  | 0
5.5* | Powder Coated extruded Aluminium Grilles/Diffusers with VCD complete with fixing frames, nuts, bolts, gaskets, washers etc | 100 | SQM* |  | 0 |  | 0
5.6* | Powder coated extruded Aluminium Grilles/Diffusers without VCD complete with fixing frames, nuts, bolts, gaskets, washers etc | 10 | SQM* |  | 0 |  | 0
5.7* | Powder Coated extruded Aluminium Nozzle type/ Jet type Diffuser with fixing frames, nuts, bolts, gaskets, washers etc as per specification | 50 | SQM* |  | 0 |  | 0
5.8* | Thermal insulation as per specification for air duct | 1500 | SQM* |  | 0 |  | 0
5.9* | Wall mounted dampers (gravity operated) for different areas as per specifications | 50 | SQM* |  | 0 |  | 0
5.10* | Inlet Louvres as per specifications | 100 | SQM* |  | 0 |  | 0
5.11* | VOLUME CONTROL DAMPERS in GI construction as per specifications | 100 | SQM* |  | 0 |  | 0
5.12* | Acoustic insulation as per specification | 1000 | SQM* |  | 0 |  | 0
6* | FIRE DAMPER
a)* | Fire damper | 30 | SQM* |  | 0 |  | 0
b)* | Motorized Actuator with single phase power supply for the above Fire damper with auto resetting, limit switches, indication lamps etc | 30 | Nos.* |  | 0 |  | 0
c)* | Fusible Link type Fire Damper | 10 | SQM* |  | 0 |  | 0
7* | Roof extractor units (axial flow type) with hood, disconnect switch and all accessories as specified (suitable for 415V/3-phase supply). Following fan shall have 15 mmwc static pressure.
a)* | Capacity 50,000 CMH with Motor rating 5.5 KW | 32 | Nos.* |  | 0 |  | 0
b)* | Capacity 40,000 CMH with Motor rating 5.5 KW | 2 | Nos.* |  | 0 |  | 0
c)* | Capacity 20,000 CMH with Motor rating 2.2 KW | 2 | Nos.* |  | 0 |  | 0
8* | Axial flow supply fans with pre and fine filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3-phase supply). Following fan shall have 30 mmwc static pressure.
a)* | Capacity 10,000 CMH with Motor rating 2.2 KW | 57 | Nos.* |  | 0 |  | 0
b)* | Capacity 7,500 CMH with Motor rating 1.5 KW | 11 | Nos.* |  | 0 |  | 0
c)* | Capacity 6,000 CMH with Motor rating 1.1 KW | 8 | Nos.* |  | 0 |  | 0
d)* | Capacity 4,000 CMH with Motor rating 0.75 KW | 2 | Nos.* |  | 0 |  | 0
9* | Axial flow supply fans with pre filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3-phase supply) as specified. Following fan shall have 20 mmwc static pressure.
a)* | Capacity 15,000 CMH with Motor rating 2.2 KW | 55 | Nos.* |  | 0 |  | 0
b)* | Capacity 10,000 CMH with Motor rating 1.5 KW | 6 | Nos.* |  | 0 |  | 0
c)* | Capacity 7,500 CMH with Motor rating 1.1 KW | 1 | Nos.* |  | 0 |  | 0
d)* | Capacity 6,000 CMH with Motor rating 1.1 KW | 2 | Nos.* |  | 0 |  | 0
e)* | Capacity 4,000 CMH with Motor rating 0.75 KW | 2 | Nos.* |  | 0 |  | 0
10* | Axial flow exhaust fans (Bifurcated type, spark proof construction, wall mounted) complete with casing, flame proof motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3-phase supply) as specified. Following fan shall have 15 mmwc static pressure.
a)* | Capacity 15,000 CMH with Motor rating 2.2 KW | 33 | Nos.* |  | 0 |  | 0
b)* | Capacity 10,000 CMH withMotor rating 1.5 KW | 18 | Nos.* |  | 0 |  | 0
c)* | Capacity 7,500 CMH with Motor rating 1.1 KW | 19 | Nos.* |  | 0 |  | 0
d)* | Capacity 6,000 CMH with Motor rating 0.75 KW | 2 | Nos.* |  | 0 |  | 0
e)* | Capacity 4,000 CMH with Motor rating 0.55 KW | 20 | Nos.* |  | 0 |  | 0
f)* | Capacity 2,000 CMH with Motor rating 0.55 KW | 5 | Nos.* |  | 0 |  | 0
11* | Axial flow exhaust fans (Wall mounted) complete with casing,TEFC sq cage induction motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3-phase supply) as specified.Following fan shall have 10 mmwc static pressure.
a)* | Capacity 15,000 CMH with Motor rating 1.1 KW | 8 | Nos.* |  | 0 |  | 0
b)* | Capacity 10,000 CMH with Motor rating 0.75 KW | 15 | Nos.* |  | 0 |  | 0
c)* | Capacity 7,500 CMH with Motor rating 0.55 KW | 5 | Nos.* |  | 0 |  | 0
d)* | Capacity 6,000 CMH with Motor rating 0.55 KW | 1 | Nos.* |  | 0 |  | 0
e)* | Capacity 4,000 CMH with Motor rating 0.55 KW | 2 | Nos.* |  | 0 |  | 0
f)* | Capacity 2,000 CMH with Motor rating 0.37 KW | 9 | Nos.* |  | 0 |  | 0
12* | Exhaust fan (propeller type) completes with induction motor & mounting frame MS rain protection cowl, bird screen and all other accessories as specified (suitable for 240V/ 1 phase). Following fan shall have 5 mmwc static pressure.
a)* | Capacity 1200/1000 CMH with Motor rating 100 watts | 200 | Nos.* |  | 0 |  | 0
13* | Single phase Circular Duct inline Fan of capacity 1000 CMH | 35 | Nos.* |  | 0 |  | 0
14* | Air Curtain of suitable CFM for Doors/ Rolling Shutters for preventing dust ingress, suitable to operate 24X 7 in coal dust environment Air Curtain should be as per latest OEM standard.
a)* | Air Curtain Height up to 10 feet & width up to 12 feet | 5 | Nos.* |  | 0 |  | 0
b)* | Air Curtain Height up to 10 feet & width from 13 feet to 24 feet | 5 | Nos.* |  | 0 |  | 0
c)* | Air Curtain Height up to 11-15 feet & width up to 12 feet | 2 | Nos.* |  | 0 |  | 0
d)* | Air Curtain Height up to 11-15 feet & width 13 feet to 24 feet. | 2 | Nos.* |  | 0 |  | 0
e)* | Air Curtain Height up to 16-24 feet & width up to 12 feet | 2 | Nos.* |  | 0 |  | 0
f)* | Air Curtain Height up to 16-24 feet & width 13 feet to 24 feet. | 2 | Nos.* |  | 0 |  | 0
15* | Junction Box, Cable tray, conduit, cable gland and lugs, conduit and conduit accessories, FIELD INSTRUMENTS like pressure gauge, temperature gauge, pressure switch, transmitters, differential pressure switch, flow switchs, any other instruments required for Ventilation System including necessary control panel for hook up with main DDCMIS as per specifications. | 1 | LOT |  | 0 |  | 0
16* | Fibre optic cable. | 50 | Rmt* |  | 0 |  | 0
17* | Handling arrangement for Ventilation system.
a* | 1 Ton Chain Pulley Block with tripod stand (without Travelling trolley). | 2 | Nos.* |  | 0 |  | 0
b* | Manual operated trolley, platform trolley of 1 ton capacity with base area 2mx1.5m. | 2 | Nos.* |  | 0 |  | 0
c* | 1T chain pulley block with travelling trolley | 2 | Nos.* |  | 0 |  | 0
18* | Providing full support during FAT of DDCMIS, preparation of control scheme, and commissioning of DDCMIS as per specification. | 21 | Mandays* | NA | NA |  | 0
19* | Total lumpsum price for special tools & tackles for maintenance inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up, Appendix-A) | 1 | LOT | 0 | 0 | NA | NA
20* | Total lumpsum price for commissioning spares inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up, Appendix-B). | 1 | LOT | 0 | 0 | NA | NA
21 | Any other item not indicated above, but required to make the system complete in all respects. | 1 | LOT |  | 0 |  | 0
Total |  |  |  |  | 0 |  | 0
NOTES
1 | The bidder shall furnish unit rates for variable item (marked *) for necessary adjustment (plus or minus) variation during detailed engg. stage. The unit rates quoted above shall be considered for adjustment and no separate unit rates shall be quoted. Unit rates shall be valid throughout the contract. Final qty. shall be paid as per actual measurment at site for erection for all the variable items..
2 | Price format shall not be changed by the bidder as the bidder may get disqualified by doing so.
3 | Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price.
4 | The BOQ mentioned above shall be read in conjunction with technical specification requirement. Any other item required as per technical specification but not specifically indicated in above BOQ, shall deemed to be inculded in total prices quoted by bidder. No additional price shall be payable against such items.

## APPENDIX-A_VENT
APPENDIX-A Special tools & tackles for maintenance
NAME OF PROJECT: |  | 2X 660 MW TALCHER TPP STAGE-III
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-497-554-A002
SL NO | DESCRIPTION | UNIT | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | Measuring tape | NO | 1 |  | 0
2 | Tachometer | NO | 1 |  | 0
3 | Double ended spanner | SET | 1 |  | 0
4 | Ring spanners | SET | 1 |  | 0
5 | Gasket punch | NO. | 1 |  | 0
6 | Center punch | NO. | 1 |  | 0
7 | Hammer with wooden handles | NO. | 1 |  | 0
8 | Scissors for sheet metal cutting | NO. | 1 |  | 0
9 | Torch light (suitable for 2 cells) | NO. | 1 |  | 0
10 | Multimeter | NO. | 1 |  | 0
11 | Anemometer | NO. | 1 |  | 0
12 | Compound pressure gauge | NO. | 1 |  | 0
13 | Slide wrench 8” | NO. | 1 |  | 0
14 | Slide wrench 10” | NO. | 1 |  | 0
15 | Slide wrench 6” | NO. | 1 |  | 0
16 | Box spanner set | SET | 1 |  | 0
17 | Screw driver set | SET | 1 |  | 0
18 | Align key set | SET | 1 |  | 0
19 | MS tool box | NO | 1 |  | 0
Total |  |  |  |  | 0
NOTES
1 | Above is the minimum list. Any other Tools and tackles required for Ventilation system w.r.t. Mechanical, Electrical and C&I part shall also be provided by the Bidder as per system / customer requirement without any commercial & Delivery implication to BHEL.
2 | Supply of special tools and tackle including tool box required for operation, maintenance and overhauling of the system is in the scope of the bidder.

## APPENDIX-B_VENT
APPENDIX-B Commissioning spares
NAME OF PROJECT: |  | 2X 660 MW TALCHER TPP STAGE-III
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-497-554-A002
SL NO | DESCRIPTION | UNIT | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | FAN BELTS | SET | 1 |  | 0
2 | PRESSURE GAUGE | NO | 1 |  | 0
3 | TEMPERATURE GAUGE | NO | 1 |  | 0
4 | FILTER | SET | 1 |  | 0
Total |  |  |  |  | 0
NOTES
1 | Above is the minimum list. Any other commissioning spare required for AC system w.r.t. Mechanical, Electrical and C&I part shall also be provided by the Bidder as per system / customer requirement without any commercial & Delivery implication to BHEL.

## ANNEXURE-II_VENT
ANNEXURE - II LIST OF MANDATORY SPARES
NAME OF PROJECT: |  | 2X 660 MW TALCHER TPP STAGE-III
NAME OF PACKAGE: |  | VENTILATION SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-497-554-A002
S. No. | Description | QTY | Total Ex-Works Price (INR)
1 | Air Washer Units (for each type) |  |  | 0
1.1 | Supply Air fans |  |  | 0
1.1.1 | V-belts for Supply air fans | 2 Sets |  | 0
1.1.2 | Supply air fan bearings | 1 Set |  | 0
1.2 | Air Washer pump |  |  | 0
1.2.1 | Impeller for Pump | 1 no of each type.
1.2.2 | Pump Shaft | 1 no of each type
1.2.3 | Pump Bearing | 1 Set
1.2.4 | Shaft Sleeves | 1 Set
1.2.5 | Gland Packings for pumps | 2 Sets
1.3 | Spray nozzles | 5% of total population or 100 numbers whichever is higher.
1.4 | Air Washer Pump inlet water strainer | 1 No.
1.5 | Brass suction screen/strainer for air washer tank | 1 Set
2 | Electrical Actuators
2.1 | Actuators | 1 No. of each type, model and rating.
2.2 | Motor for Centrifugal fan for air washer unit | 1 No of each rating
3 | Unitary air filtration unit (for each type)
3.1 | Supply Air fans
3.1.1 | V-belts for supply air fans | 2 Sets
3.1.2 | Supply air fan bearings | 1 Set
3.2 | UAF Pump
3.2.1 | Pump bearings | 1 Set
3.2.2 | Impeller for pump | 1 no.
3.2.3 | Pump Shaft | 1 no.
3.2.4 | Shaft sleeves | 1 Set
3.2.5 | Gland Packings for pumps | 1 Set
3.3 | Nylon Filter | 1 Set
3.4 | Spray nozzles | 5% of total population or 50 Numbers whichever is higher.
3.5 | Water strainer | 1 No.
3.6 | Brass suction screen/strainer for unitary air filtration tank. | 1 Set
3.7 | Motor for Centrifugal fan for UAF | 1 No
4 | Motor (Other than Centrifugal Fan) | 1 No of each type & rating
Control & Instrumentation
5 | Measuring Instruments
5.1 | Level transmitter | 1 No. of each type and model
5.2 | Pressure transmitter | 1 No. of each type and model
| TOTAL |  | 0
Notes:
a) | Mandatory spares listed in Price Schedule are bare minimum requirement. In case any additional mandatory spares requirement is covered elsewhere in the tender specification apart from specified above, same shall be deemed to have been covered in bidder’s scope of supply.
b) | Wherever "set" is indicated, it shall mean complete replacement for one main equipment of similar size & capacity.
c) | All Spares shall be supplied as per the requirement of the specifications. In case any spare indicated in the specification is “not applicable” for particular equipment, then suitable applicable alternate spare has been offered / shall be supplied by the bidder without any financial implication."
d) | Bidder to write “Quoted / Not Applicable” against all items. Any item which is quoted as “not applicable” by the bidder in the above list and is found to be “applicable” at a later date shall be supplied by the bidder without any commercial and delivery implication.
e) | For quantities indicated in percentage, fractions are to be rounded-off to next higher integer.
f) | Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price.
g) | Bidder to note that even though there may be some spares which are repetitive at various sl.no mentioned above, bidder to ensure that prices are quoted against each sl.no. In case any cell is left blank in the unpriced schedule shall be treated as "quoted" and included in total price.