|  | BHARAT HEAVY ELECTRICAL LIMITED RAMACHANDRPURAM :: HYDERABAD 502 032. |  | Enquiry No. : |  |
| --- | --- | --- | --- | --- |
|  |  |  | Due Date : |  |
| HYDERABAD | CONTACT DETAILS |  | Supplier Qtn. No.: |  |
|  | Sr. Manager/ Pur-CG e-mail: burre@bhelhyd.co.in Phone No. 040-23182250 |  | Date : |  |
| TECHNICAL SPECIFICATION CUM COMPLIANCE CERTIFICATION FOR |  |  |  |  |
| POWER CABLES FOR PUMPS TEST PLANT |  |  |  |  |
| NOTE:- |  |  |  |  |
| 1. Vendor (OEM) must submit complete information against clause no. 12.1.0 The offer meeting this clause would only be processed. |  |  |  |  |
| 2. The "Offered" Column and where applicable, the "Deviations" & "Remarks" Column of this format shall be filled in by the Vendor and submitted along with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specifications/requirements shall be treated as non-compliance. |  |  |  |  |
| 3. The offer and all documents enclosed with offer should be in English language only. |  |  |  |  |
| 4. Vendor to submit offer in two parts in closed envelops viz. Technical bid and Price bid. |  |  |  |  |
| ADDRESS OF THE SUPPLIER : |  | ADDRESS OF THE INDIAN AGENTS : |  |  |
| TELEPHONE NOS.: |  | TELEPHONE NOS.: |  |  |
| FAX NOS.: |  | FAX NOS.: |  |  |
| E-MAIL ADDRESS : |  | E-MAIL ADDRESS : |  |  |
| SCOPE: DESIGN, MANUFACTURE, ASSEMBLY, TESTING, PACKING AND DISPATCH OF POWER CABLES FOR PUMPS TEST PLANT |  |  |  |  |

| 1.0.0 | Purpose of the Equipment: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1.1.0 | This specification specifies the requirement of Design, Engineering, Manufacture, Assembly, Inspection, Testing and Delivery of Various types of power cables with required quantity to Pumps Testing. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.0.0 | Basic Requirements: Various types of power cables are to be supplied with required quantity. This specification covers total four variants of power cables. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.1.0 | Technical Specification |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.2.0 | Variant -1 : 11kV unearthed grade 1C x 500 Sq.mm copper flexible cables. (Annealed Tinned copper conductor (class-5), EPR (type IE-3)insulated, Insulation screened with extruded semi conducting compound and ATC wire braid, NBR PVC (Tupe SE-4), Overall sheathed 22KV grade cable (suitable for 11KV UE system) to IS-9968/II/2002 ) |  |  |  |  |  | : | 800 meters |  |  |  |  |  |  |  |
| 2.2.1 | Variant -2 : a) 6.6kV unearthed grade 1Cx300 Sq.mm copper flexible cables. b) 6.6kV unearthed grade 1Cx240 Sq.mm copper flexible cables (Annealed Tinned copper conductor (class-5), EPR (type IE-3)insulated, Insulation screened with extruded semi conducting compound and ATC wire braid, NBR PVC (Tupe SE-4), Overall sheathed 11KV grade cable (suitable for 6.6 KV UE system) to IS-9968/II/2002 ) |  |  |  |  |  | : | - 1000 meters - 1000 meters |  |  |  |  |  |  |  |
| 2.2.2 | Variant -3 : 3.3 kV unearthed grade 1Cx500 Sq.mm copper flexible cables (Annealed Tinned copper conductor (class-5), EPR (type IE-3)insulated, Insulation screened with extruded semi conducting compound and ATC wire braid, NBR PVC (Tupe SE-4), Overall sheathed 11KV grade cable (suitable for 3.3 KV UE system) to IS-9968/II/2002 ) |  |  |  |  |  | : | 800 meters |  |  |  |  |  |  |  |
| 2.2.3 | Variant -4 : a) 415V unearthed grade 1Cx240 Sq.mm copper flexible cables b) 415V unearthed grade 1Cx120 Sq.mm copper flexible cables c) 415V unearthed grade 1Cx95 Sq.mm copper flexible cables (Annealed Tinned copper conductor (class-5), EPR (type IE-3)insulated, Insulation screened with extruded semi conducting compound and ATC wire braid, NBR PVC (Tupe SE-4), Overall sheathed 1.1 KV grade cable (suitable for 415 V UE system) to IS-9968/II/2002 ) |  |  |  |  |  | : | - 2000 meters - 2000 meters - 2000 meters |  |  |  |  |  |  |  |
| 3.0.0 | Technical specification : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.0 | Variant -1 : 11kV unearthed grade 1C x 500 Sq.mm copper flexible cables. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.1 | No. of core X Area of cross section |  |  | 1 X 500 sq.mm |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.2 | Voltage grade |  |  | 22KV grade cable (suitable for 11KV UE system) |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.3 | Conductor |  |  | Tinned Copper and shall confirm to IS 6380 |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.4 | Flexibility class as per IS 8130/84 |  |  | Class -5 |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.5 | Inner Sheath |  |  | Extruded PVC/extruded FRLS PVC |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.6 | Conductor screening material |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.7 | Insulation screening material (non metallic) |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.8 | Insulation screening material (Metallic) |  |  | Annealed Tinned copper |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.9 | Outer sheath material |  |  | NBR PVC (Type SE-4), IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.10 | Insulation material |  |  | EPR (type IE-3)insulated as per IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.1.11 | Approx. over all diameter of cable |  |  | Vendor to specify |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.0 | Variant -2 : a) 6.6kV unearthed grade 1Cx300 Sq.mm copper flexible cables. b) 6.6kV unearthed grade 1Cx240 Sq.mm copper flexible cables |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.1 | No. of core X Area of cross section |  |  | - 1 X 300 sq.mm - 1 X 240 sq.mm |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.2 | Voltage grade |  |  | 11KV grade cable (suitable for 6.6KV UE system) |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.3 | Conductor |  |  | Tinned Copper and shall confirm to IS 6380 |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.4 | Flexibility class as per IS 8130/84 |  |  | Class -5 |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.5 | Inner Sheath |  |  | Extruded PVC/extruded FRLS PVC |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.6 | Conductor screening material |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.7 | Insulation screening material (non metallic) |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.8 | Insulation screening material (Metallic) |  |  | Annealed Tinned copper |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.9 | Outer sheath material |  |  | NBR PVC (Type SE-4), IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.10 | Insulation material |  |  | EPR (type IE-3)insulated as per IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.2.11 | Approx. over all diameter of cable |  |  | Vendor to specify |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.0 | Variant -3 : 3.3 kV unearthed grade 1C X 500 Sq.mm copper flexible cables |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.1 | No. of core X Area of cross section |  |  | 1 X 500 sq.mm |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.2 | Voltage grade |  |  | 6.6KV grade cable (suitable for 3.3 KV UE system) |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.3 | Conductor |  |  | Tinned Copper and shall confirm to IS 6380 |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.4 | Flexibility class as per IS 8130/84 |  |  | Class -5 |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.5 | Inner Sheath |  |  | Extruded PVC/extruded FRLS PVC |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.6 | Conductor screening material |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.7 | Insulation screening material (non metallic) |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.8 | Insulation screening material (Metallic) |  |  | Annealed Tinned copper |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.9 | Outer sheath material |  |  | NBR PVC (Type SE-4), IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.10 | Insulation material |  |  | EPR (type IE-3)insulated as per IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.3.11 | Approx. over all diameter of cable |  |  | Vendor to specify |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.0 | Variant -4 : a) 415V unearthed grade 1Cx240 Sq.mm copper flexible cables b) 415V unearthed grade 1Cx120 Sq.mm copper flexible cables c) 415V unearthed grade 1Cx95 Sq.mm copper flexible cables |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.1 | No. of core X Area of cross section |  |  | - 1 X 240 sq.mm - 1 X 120 sq.mm - 1 X 95 sq.mm |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.2 | Voltage grade |  |  | 1.1KV grade cable (suitable for 415V UE system) |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.3 | Conductor |  |  | Tinned Copper and shall confirm to IS 6380 |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.4 | Flexibility class as per IS 8130/84 |  |  | Class -5 |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.5 | Inner Sheath |  |  | Extruded PVC/extruded FRLS PVC |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.6 | Conductor screening material |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.7 | Insulation screening material (non metallic) |  |  | Extruded semi conducting compound |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.8 | Insulation screening material (Metallic) |  |  | Annealed Tinned copper |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.9 | Outer sheath material |  |  | NBR PVC (Type SE-4), IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.10 | Insulation material |  |  | EPR (type IE-3)insulated as per IS 8130/84 |  |  |  |  |  |  |  |  |  |  |  |
| 3.4.11 | Approx. over all diameter of cable |  |  | Vendor to specify |  |  |  |  |  |  |  |  |  |  |  |
| 4.0.0 | APPLICABLE STANDARDS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1.0 | IS-9968, Part2 | : | Specification for Elastromer Insulated Cables. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2.0 | IS-8130 | : | Conductors for insulated electric cables and flexible cords. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.3.0 | IS-10462 | : | Fictitious calculations method for determination of dimensions of protective covering of cables: part1 Elastomer and thermoplastic insulated cables. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.4.0 | ASTM-D2843 | : | Standard for smoke generation test. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.5.0 | IE-332-1 | : | Standard for Flammability test. |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.6.0 | SS 424 1475 | : | Standard for Flammability test |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.0.0 | TESTS All acceptance and routine tests shall be carried out on all cables at vendor’s works in the presence of purchaser’s representative. Type test reports of similar cables whenever they are called for shall be furnished. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6.0.0 | CABLE LENGTHS Cables shall be delivered in maximum possible lengths of not less than 500M neatly rolled on wooden drums, with both ends sealed with moisture proof sealing. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.0.0 | DOCUMENTATION - 2 copies of filled up Technical data sheets. - Quality assurance schedules. - 6 copies of test certificates within one week after the inspection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.0.0 | TECHNICAL DATA SHEETS ( To be filled in and sent along with the Bid for each type of cable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. | Make |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. | Type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. | Applicable standard |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. | Voltage Grade |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. | Suitable for system with |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Service voltage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Neutral Earthed / unearthed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. | Max. Conductor temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Continuous degC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Short time deg C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7. | Conductor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Size (Sq.mm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) No.of wires & Diameter of each wire |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8. | Shielding on Conductor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) Thickness (Nominal) mm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | d) Short time current rating kA/Sec |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9. | Insulation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) Thickness (Nominal) mm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10. | Shielding of Insulation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) Thickness (Nominal) mm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | d) Short time current rating kA/Sec |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11. | Inner Sheath |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) Thickness (Nominal) mm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | d) Extruded (Yes/No) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | e) Approx. outside dia. Over inner sheath (mm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12. | Overall sheath |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) Thickness (Nominal) mm. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13. | Approx. overall Dia (mm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14. | Standard drum length with tolerance (M) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15. | Net weight of able (Kg/Km) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16. | Continuous current rating for standard IS condition laid direct (Amps) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) In ground |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) In duct |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) In air |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17. | Short circuit current for 1 Sec. (kA) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18. | Electrical parameters at max. operating temperature (Ohm/km) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) Resistance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Reactance at 50 Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) Capacitance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19. | Recommended minimum bending radius |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20. | Losses (watts/Metre) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21. | List of routine and type tests certificate enclosed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9.0.0 | Preservation: - Preservation should be accomplished in accordance with acceptable commercial practice for the type of supply. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10.0.0 | Packing and forwarding: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10.1.0 | Name Plate: Each cable drum shall be marked with following information at a visible place. - Manufacturer’s Name. - Details of cable - Length of the cable. - Gross weight. - Direction of rotation of drum by means of an arrow for un-winding. - Purchase Order Number. - BHEL Material Code. - Dispatch information. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10.2.0 | Cables shall be dispatched in wooden drums, securely battened with take off end fully protected against damage. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10.3.0 | The ends of the cable shall be sealed with suitable PVC / rubber caps to prevent ingress of moisture. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11.0.0 | Guarantee: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11.1.0 | 18 months from the date of Commissioning at BHEL. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12.0.0 | Qualification of vendors: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12.1.0 | Vendor should have supplied two such supplies’ earlier. References of similar supply are earlier to be furnished with the offer. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13.0.0 | Other conditions: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13.1.0 | The complete offered system will be considered for procurement. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13.2.0 | In case the quoting agency for this system is not OEM, then it is mandatory that the supplier should provide a letter from the respective OEM stating that, they will support the equipment in both technical and logistic for at least two years. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13.3.0 | The complete system engineering is the responsibility of supplier. Vendors who supply in part will be disqualified |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13.4.0 | The system, any unit or parts there in, if found defective during commissioning or there after shall be replaced within a week of detection of such defects. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14.0.0 | In case of any clarification required, the party taking part in tender shall contact BHEL and obtain written clarification regarding this tender. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |