## Sheet1
Sl. No. | Clause No. | Description as per Specification | Queries by Bidder | BHEL Replies
1 | Cl. No. 20 & Section D 26 (Annexure-1 of tender specification) | No make is mentioned for FDA system and its components | Since no make is mentioned, we want to consider out of reputed makes NOTIFIER/ SCHRACK/ EDWARD/ MORLEY | Bidder may consider the following makes for Fire Alarm Panel:- ESSER SIEMENS SIMPLEX EDWARDS NOTIFIER SCHRACK GE In addition to above, bidder may propose other makes & models (with UL/FM/Vds approval) having proven track records and requires purchaser approval.
2 | Cl. No. 20 and Sub vendor list of Instrumentation & Control Equipment | Microprocessor based annunciation system - Hathaway & Ronan | Annunciation system is part of FDA system. Also we are unable to identify these vendors. You are requested to share contact address & numbers. | Bidder to note that, annunciation system is a part of FDA system and shall be from the FDA makes only.
3 | VOID
4 | FDA Scheme (1-383-16-00004 Rev-03), Interconnection Details of Sub Fire Alarm Panels (4-383-16-00001 Rev-0) and Cl. No. 9.7 of tender specification | We note that network cabling has been shown as 4C x 2.5 sq.mm in FDA Scheme and shown as Cat5e in Interconnection Details of Sub Fire Alarm Panels | In accordance with International Fire Alarm system practice, when long runs of cable has to be installed between panels, the manufacturer’s use a RS485 networking arrangement which requires a 4C x 2.5 sq.mm cables. We request you to confirm that MFAP and SFAP shall be 4C x 2.5 sq.mm cables. | Noted & confirmed.
| FDA Scheme (1-383-16-00004 Rev-03), Interconnection Details of Sub Fire Alarm Panels (4-383-16-00001 Rev-0) and Cl. No. 9.7 of tender specification | We note that network cabling has been shown as 4C x 2.5 sq.mm in FDA Scheme and shown as Cat5e in Interconnection Details of Sub Fire Alarm Panels | The cabling between MFAP and Plant communication system shall be relay based using potential free contacts suitable for the zones of alarm required. Note 15 of FDA Scheme may be ammended accordingly. | Note 15 of FDA Scheme shall be replaced with " Communication between MFAP with SFAP / repeater panel, plant communication system, LCP shall be through redundant communication network cable"
5 | - | - | Please furnish the location and quantity of Local control Panels for water spray systems to be connected to MFAP and SFAP on a panel wise basis. Clause 9 of the technical specifications indicates only at toal No of 250 Nos DVs but not their location. Also furnish the Bill of materials for the Cables required for the purpose. | With reference to FDA Scheme (1-383-16-00004) of tender specificaiton, bidder to note that one relay based panel located in fire water pump house and one relay based panel located in foam pump house shall be conidered for interfacing with MFAP (Supply of these panels is not in the scope of bidder, however supply of network cable and interfacing of these panels with Main Fire Alarm Panel shall be in the scope of bidder). Bidder to note that location of deluge valves shall be furnished during detail engineering. Bidder to note that Engineering and BOQ generation of cables is in the scope of bidder.
6 | - | - | Please furnish the Bill of materials for detectors and cables for Fire alarm system proposed in various areas. Alternately, please furnish dimensional details and or plan and sectional details of rooms with beam dimensions to enable us to estimate the material requirement . | The rooms /building dimensions are available in drawings furnished along with the tender specification. Bidder to note that, Engineering and BOQ generation of complete fire detection and alarm system is in the scope of bidder. Bidder may consider an additional 5% detectors of each type to cover damages during erection.
7 | - | - | BHEL to clarify whether erection and testing is included in the scope of this NIT. | Erection & testing is not in the scope of bidder. However,bidder to note that supply, shop testing and supervision of E&C is in bidders scope. Bidder to refer the Cl. No. 12 of tender specification for further scope of services.
8 | - | - | Please clarify how a PC is proposed to be connected to a Relay Based Panel in the Pump House. | Panels and PC's in Fire water pump house and foam pump house are not in bidder's scope as per Cl. No. 13.3 of tender specification. However interfacing of these panels with Main Fire Alarm Panel shall be in the scope of bidder.
9 | - | - | Please clarify how many potential free contacts are required by BHEL under clause 7 of drawing No 4-383-16-0004 Rev 3 for HVAC interlocks, power supply trip, Close dampers tripping motors, etc. | Bidder to consider a total of 500 potential free contacts as per Cl. No. 14.2.
10 | - | - | Please confirm size of cables for wiring Fire alarm detectors, manual call points, Modules to Exit signs etc. | Bidder to note that, Cables used for looping of detectors and devices is 2C x 2.5 sq.mm. The supply of loop and power cables are not part of bidder scope. However networking cable between between MFAP, SFAP, Repeater Panel, Operator Work Station and DCS shall be in the scope of bidder. Please refer Cl. No. 13.1 for scope of supply of cables.
11 | - | - | BHEL to clarify how many Pressure switches and or solenoid valves are proposed per Deluge valve and the rating of the same. | Bidder to note that, for deluge valves of HVWS there shall be 2 pressure switches and 1 SOV where as for deluge valves of MVWS there shall be 1 pressure switche and 1 SOV. Rating: SOV - 24 V DC Pressure Switch - 15A 250 V AC, 0.25A 220 V DC
12 | - | - | With reference to clause 9.17 of the technical specifications, the Exit signs are photo luminescent and not back lit type. We request BHEL to clarify whether the interconnection of the CM with Exit sign via hooter is required? | Bidder to note that, as per Cl. No. 9.17 Exit sign boards shall be rigid photoluminescent based glow-in-the-dark rigid sheet with high intensity luminious properties enclosed in a transparent weather-proof UV stabilized coated sheet with UV screen printing by imported inks. are not back-lit type. Hence, interconnection of exit sign with the FDA loop is not required.
13 | - | - | We request BHEL to furnish the belt speed for conveyors, width of the belts. | Bidder to refer GA of conveyors in the tender drawings for dimention details and speed.
14 | - | - | We request BHEL to clarify the extent of interconnection with the panels in the scope of others as per clause 13.3 of the specifications. | Bidder to note that, Interconnection of other panels to MFAP shall be such that all the signals are available in MFAP.
15 | - | - | We request BHEL to confirm that Relay modules with a rating of 2A and 110V AC/30 V DC are acceptable for interlock purposes. | Bidder to note that, Relay modules shall be considered such that they are compatable with fire alarm panel.
16 | Cl. No. 9.4 | All detectors shall have inbuilt fault isolators. | Please clarify whether all addressable Detectors and Devices are to be provided with isolators , since in similar requirement for the same plant in Switchyard area the TS requirement is isolators after every 20/25 Detectors and devices. | Bidder to note that, All detectors shall have inbuilt fault isolators as per Cl. No. 9.4 of tender specification.
17 | Cl. No. 10.4 | - | Please clarify whether 2 Spark /Ember detectors are to be considered for each belt or 2 Spark/Ember detectors are to be considered for the entire conveyor i.e. I for 1 A/B where the belts run parallel whether we need to consider 4 no or 2 no Spark/Ember detectors. | As per cl. No. 10.4 (d) of tender specification, minimum 2 no. of spark / ember detectors shall be provided for each conveyor (for example minimum 2 no. of spark / ember detectors shall be provided for conveyor 1 A)
18 | - | - | Please clarify whether flameproof manual call points are to be considered distributed over the entire length of the conveyors inside conveyors or Flame proof manual call points to be considered only at the entry and exit points for the conveyor floor. | Bidder to note that, Flame proof manual call points shall be provided at entry and exit points of the conveyor floor.
19 | Cl. No. 14.2 | - | Please confirm whether 500 potential free contacts shall be provided with each FAP for interfacing or a total of 500 potential free contacts are to be considered for interfacing. | Bidder to consider a total of 500 potential free contacts as per Cl. No. 14.2 for interfacing.
20 | - | - | Please clarify whether flameproof hooters are to be considered distributed over the entire length of the conveyors inside conveyors or Flame proof hooters to be considered only at the entry and exit points for the conveyor floor. | Bidder to note that, Flame proof hooters shall be provided at entry and exit points of the conveyor floor.
21 | Cl. No. 10.15 | - | Please clarify whether laying of LHS cables would be as per TAC rules or the same shall be as depicted in TS clause no 10.15 (c ). | Bidder to note that, Laying of LHS cable shall be as per TAC rules.
22 | - | - | We have considered the ‘SCHRACK’ make for fire alarm system which have redundant panel and max.250 devices per loop. | Bidder may consider the following makes for Fire Alarm Panel:- ESSER SIEMENS SIMPLEX EDWARDS NOTIFIER SCHRACK GE In addition to above, bidder may propose other makes & models (with UL/FM/Vds approval) having proven track records and requires purchaser approval.
23 | Cl. No. 9.10 | Siren control panel shall be mounted inside fire alarm panel. | Siren control panel shall be provided outside the fire alarm panel. | Sire shall be operated through control module and this module shall be located inside the fire alarm panel.
24 | - | - | Provide the approved vendor list of all items required for fire alarm system. | Bidder may consider the following makes for Fire Alarm Panel:- ESSER SIEMENS SIMPLEX EDWARDS NOTIFIER SCHRACK GE In addition to above, bidder may propose other makes & models (with UL/FM/Vds approval) having proven track records and requires purchaser approval.