## Sheet1
| PROJECT | RCC COOLING TOWER FOR 1 X 51 MW COMBINED CYCLE POWER PLANT FOR ONGC, HAZIRA
| ENQUIRY | T7B1O88410 & NIT No. 23749
| DATE | 2015-08-08
PRE BID QUERIES
SL.NO. | VOLUME / PART | SUB-SECTION / PAGE NO. / CLAUSE NO. | DESCRIPTION AS PER SPECIFICATIONS | QUERIES BY HAMON SHRIRAM COTTRELL PVT. LTD. DATED 20/08/2015 | BHEL REPLY ON THE PRE BID QUERIES DATED 08.09.2015
I. | TECH SPECIFICATION
1 | Part 1 of 2 / PEMC-05255 Rev.01 | Section I / 4 of 70 / 1.4.0 | Painting on concrete structures shall be done as per Annexure-2 | Kindly confirm the painting specifications for the following (which is applicable for cooling tower for this project) : | Bidder to note that Painting on RCC Cooling tower shall be done as per Clause 5.4.18 Doc. 5111168-ME-SPC-100-001 Rev. 01 , Volume III seection 5 attached as Annexure 2 in the technical specification.
|  |  | (Volume III Section 5). | a) Inside surface of RCC cold water basin and RCC cold water outlet channel
b) Outside surface of RCC cold water basin and RCC cold water outlet channel
c) Inside surface of RCC superstructure
d) Outside surface of RCC superstructure
e) Whether the inside structure above hot water distribution level needs to be painted or not ? (as there will not be any spray of water in these area)
2 | Part 1 of 2 / PEMC-05255 Rev.01 | Section I / 5 of 70 / 1.6.0 | Make up water analysis | Kindly provide us the following on circulating water & make up water to select the right kind of PVC Film type fill.
|  |  |  | a) Total Suspended Solids (TSS) | Please note that Filtered water (make up water) analysis data is already furnished. The same is available in the bid document. Bidder to proceed with the same.
b) Total Dissolved Solids (TDS)
|  |  |  | c) Cycle of concentration (COC) | COC is 5
3 | Part 1 of 2 / PEMC-05255 Rev.01 | Section I / 6 of 70 / 1.7.0 | Thermal analysis of cooling tower | Kindly confirm whether the thermal design of our proposed cooling tower can be of our (Hamon) design or we should follow Fulkerson’s handbook as mentioned in Annexure B (page 53 of 69 under Part 2 of 2). Please note that there is no specific mentioning of the design calculations as per Fulkerson’s calculations vide page no. 10 to 12 of 70 under section II. Kindly clarify. | Bidder to follow Fulkerson's handbook for thermal design of cooling tower.
4 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 13 of 70 / 2.4.16 | Maximum pumping head available at : 12 mwc ground level at terminal point of CT | We presume that the ground level refer to EL 101.2 (FGL of new CCCPP area). Kindly confirm. | Bidders understanding is correct.
5 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 15 of 70 / 2.7.5 | Partition wall in RCC. | As there is no load on the partition wall, can we consider Pre-cast Concrete block wall? Kindly confirm. | Bidder to comply with the specification. RCC partition wall shall be provided in such a way that each cell can be taken out of service without affecting the operations of the other cell. Bidder to use cast in situ for partition wall.
6 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 15 of 70 / 2.7.7 | Fan stack access door in MS. | For GRP fan stack, the stack door shall be of GRP. Kindly confirm. | Noted.
7 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 15 of 70 / 2.7.9 | RCC staircase one each at both the ends of the cooling tower from ground level to fan deck shall be provided. | Since the length of cooling tower is less than 50 mtr., we suggest to have RCC staircase at one end and cat ladder at the other end. Kindly confirm. | Bidder to comply with the specification requirement of two staircases, one at each end.
8 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 17 of 70 / 2.9.0 | CW pipes shall be Steel pipe conforming to IS-3589 with “Pipecoat ” or equivalent coatings externally applied on buried / underground (u/g) pipes. | Kindly provide us the complete specifications such as IS standard, thickness of coat etc. | As per Terminal point and layout details there is no buried pipe in the scope of work of bidder. Hence, underderground piping with buried coating is not applicable.
9 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 17 of 70 / 2.9.0 | Buried pipe thickness shall be designed as per AWWA M11 standard for Steel pipes. Minimum corrosion allowance of 3.2 mm shall be provided for all buried underground pipes. | Kindly confirm us the following : a) Thickness of pipe having diameter varies from 150 NB to 1400 NB to be required for the proposed cooling tower. b) Depth of buried pipe below finished ground level. c) We shall consider the thickness of pipes as per your clarifications and we shall not provide any corrosion allowance for the buried pipe. | Please note that there is no Buried pipe in bidder's scope of supply. Bidder shall follow PMS 11D for piping specification which is for above ground piping. (Attached with this mail)
10 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 18 of 70 / 2.9.0 | The material of construction for the valves, rubber expansion bellows, fittings provided shall be subjected to Owner/Owner’s representative’s approval. | Kindly provide us the complete specifications for valves, rubber expansion bellows, fittings etc. at this stage itself, as this will have commercial implications. | Bidder to follow PMS 11D which is enclosed alongwith this document.
11 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 18 of 70 / 2.9.0 | Cathode protection | Kindly provide us the detailed specifications for this to enable us to consider our price accordingly. | Please note that there is no Buried pipe in bidder's scope of supply. Hence cathodic protection is not applicable.
12 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 20 of 70 / 2.10.8 | Two vibration cut-off switches with adjustment for sensitivity for each fan shall be provided. | As a standard practice, one vibration cut off switch for each fan (ie one for each cell) shall be provided. Kindly confirm. | Bidder to comply with the specification requirement of two vibration cut-off switches with adjustment for sensitivity for each fan.
13 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 20 of 70 / 2.10.9 | Three nos. of Sludge cum dewatering pumps (one number for each cell) along with motors and accessories shall be provided. | As a standard practice, one sludge cum dewatering pump per cooling tower shall be provided. Kindly confirm. | Bidder to comply with the specification requirement of Three nos. of Sludge cum dewatering pumps (one number for each cell) along with motors and accessories.
14 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 21 of 70 / 2.12.0 | Drift losses and power consumption shall be within the guaranteed limit mentioned in data sheets. | Drift loss value shall be indicative and not guarantee, as we shall not measure the drift loss during performance guarantee testing of cooling tower. Kindly clarify. | Noted.
15 | Part 1 of 2 / PEMC-05255 Rev.01 | Section II / 23 of 70 / 2.15.0 | Water levels in CT basin & CW Pump sump | Kindly confirm the FGL for the proposed cooling tower, whether EL 99.70 or EL 101.20. | FGL shall be EL 101.20
16 | Part 1 of 2 / PEMC-05255 Rev.01 | Section III / 24 of 70 / 3.2.0 | The soil investigation report attached with this specification is preliminary. The detailed soil investigation is being done by BHEL and report will be furnished later. | Kindly provide us the final soil investigation report, co-ordinates of cooling tower, existing ground level, cut off level of pile. | Soil report is awaited from Agency and will be furnished to bidders after receipt from site.
17 | Part 1 of 2 / PEMC-05255 Rev.01 | Section IV / 35 of 70 / 4.8.1.1 | The motor name-plate rating at site ambient shall have at least 15% margin over the input power requirement of the driven equipment at rated duty point. | As per page no. 12 of 70, Margin for selection of fan drive motor shall be 25% over the maximum input power requirement of the driven equipment. (i.e. drive shaft ) at rated duty point, whereas this is a contradictory with clause no.4.8.1.1 vide page no.35 of 70. | Bidder to note that margin for selection of fan drive motor shall be 25% over the max. input power requirement of the driven equipment (i.e. drive shaft ) at rated duty point.
18 | Part 1 of 2 / PEMC-05255 Rev.01 | Section IV / 36 of 70 / 4.8.1.7 | Insulation class : Motor shall have insulation class F with temperature rise limited to class B. | Insulation class contradicts with clause no.2.10.5, vide page 19 of 70. | Bidder to note that Motors shall have class F insulation and limiting temperature rise to class B limit.
19 | Part 1 of 2/ PY51016 Rev.01 | 3 of 31 / 1.5.0 | Sludge pit | Since the cold water basin is above ground level, the sludge pit is not required. Kindly confirm. | CW Basin is slightly higher than FGL of the proposed CCCPP. However sludge cum dewatering pumps and sludge pits are required in each of the cell of cooling tower as specified in the specification.
20 | Part 1 of 2/ PY51016 Rev.01 | 4 of 31 / 1.5.0 | 2 nos chain pulley blocks( one for handling screens and one for handling mechanical components at : Yes Fan deck level) | We shall consider manually operated, chain pulley block butterfly wafer type, Cast Iron body valve and the standard shall be of BS 5155. Kindly confirm. | Query is not relevant to the Specification Point being referred to. Bidder to comply with the specification requirement.
21 | Part 1 of 2/ PY51016 Rev.01 | 6 of 31 / 1.5.0 | Side Stream Filters & its auxiliaries | As we are not finding side stream filters specifications, we presume that side stream filters & its auxiliaries are not included in cooling tower vendor’s scope of supply. | As per Specification, Side stream filters are not in bidder's scope of supply.
22 | Part 1 of 2/ PY51016 Rev.01 | 6 of 31 / 1.7.1 | Hot water - At ground level and at a distance of 1.0 m from the edge of tower. | Kindly confirm whether the hot water common header is at ground level or below ground level. | The terminal point of hot water header is N: 814.690 and E: 1797.000 (approx) and elevation of bottom of pipe is: 0.5m above FGL.
23 | Part 1 of 2/ PY51016 Rev.01 | 6 of 31 / 1.7.1 | Over flow and drain - At a distance of 1.0 m from the edge of tower. | 1) Over flow pipe of each cell shall be terminated at drain pipe of the cell. 2) Drain pipe of each cell shall be terminated at common drain pipe / trench. 3) We presume that the common drain pipe / trench shall be terminated at a distance of 1 mtr. from the edge of the tower. Kindly confirm whether our above understanding is correct or not. | Dewatering cum sludge pumps are provided for removal of sludge and water from each cell. The discharge line of this pump including valves are in bidder scope. The outlet from each cell is connected to a drain header and terminal point for this line is at 1.0m from edge of cooling tower. The individual cell overflow lines are also connected to this drain header. For details refer to CW P&ID 2-38101-04546.
24 | Part 2 of 2/ PY51016 Rev.01 | 7 of 69 | BH no.4,5,6,9 | Kindly confirm the Bore hole number applicable for proposed cooling tower. | Please note that the preliminary soil data provided is that of other project within ONGC Plant premises. The data for the present cooling tower location will be provided after receipt of data from site.
25 | Part 2 of 2/ PY51016 Rev.01 | 49 of 69 | CW & ACW Pump house layout | Kindly provide us the exact co-ordinates of cooling tower. | The coordinates of cooling tower (staircase end) at north west end are N: 813.190 E: 1792.80.
V. | OTHERS
1 |  |  |  | After award of contract, our drawings / documents will be submitted to BHEL and we shall not undertake any responsibility for getting approval from your consultants like Fichtner / Engineers India Limited. Kindly confirm. | Noted. However, bidder's shall submit all drawing / documents applicable for the package and get them approved by BHEL.
2 |  |  |  | Kindly confirm whether Pavement around the periphery of cooling tower is required or not ? If required, kindly provide us the specifications and width of pavement required. | Please refer PEMC-05255 page 24 of 70 clause 3.1.0 Scope. Minimum 1.5m paving all round the periphery of cooling tower is required.
3 |  |  |  | We request client to provide us the following :
|  |  |  | 1) Free & uninterrupted construction water and drinking water at site | Please refer attached the facility details which shows scope demarcation between Bidder and BHEL for all the facilities required.
2) Free & uninterrupted construction power at site
3) Free space for construction of our site office, labour hutment, store, stack yard for construction materials and equipments.
4) Approach road up to battery limit shall be provided to us.
|  |  |  | 5) Cutting of trees, bushes etc., Site levelling and grading in cooling tower area. | Cutting of trees, bushes etc. site levelling and grading in cooling tower area are not in Bidder's scope of supply.
|  |  |  | 6) Disposal of underground objects/services if any (like pipes, cables, scraps, debris, slag, rock etc) are to be cleared / rerouted by you before construction of civil works. | Noted.
|  |  |  | 7) Drain trench for cooling tower, beyond the drain pipe. | The drain header shall be terminated at 1m away from the cooling tower for further disposal by BHEL as indicated in the P&ID for cooling water system (Drg. No. 2-38101-04546).