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	PID
	Annexure-1A,1B & 1C
	[image: ]

Tap-Offs of 3” is shown for DPG & DPT. Please review the same.
	[bookmark: _GoBack]This is a typographical error. Please consider them as ½” from inlet & outlet piping instead of 3”.
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	PID
	Annexure-1A,1B & 1C
	[image: ]

Some instruments are marked with**. 
	This is a typographical error. Please note that all the instruments, piping etc. within the skid boundary is in bidder’s scope of supply.
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	PID
	Annexure-1B Supply of 1 No. of 2X100% Natural
Gas Filter Separator Skid For Gas
Turbine #4 &5 -Aneexure-1B
	Typo Error[image: ]
	
Bleeder connection was missed in attached annexure-1B of tender specification.
Bidder to consider bleed connection (3/4” tap-off with vale & blind flange for 6816 A/B & 6819 A/B as indicated below.
[image: ]
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