## CRS
Prebid Clarifications
Project: TSGENCO – YADADRI (5x800 MW) STPS
Item Description: Rotating Machine Condition Monitoring and Analysis System for HT drives and Vibration Analysis System for STG & BFPDT
RFQ No.: NKK0002825
Sl. No. | Bidder's Query dated: 31/10/2019 | BHEL's Reply dated: 04/11/2019
1 | Cloud-based monitoring system would be acceptable or it must be a local visualization and/or local input into DCS system required? | The system shall be provided with local server for storage of data and other functionalities mentioned in the RFQ specification. Cloud based monitoring system is not specified in the RFQ specification; hence not acceptable.
2 | What are the size of the equipment in kW, Voltage rating wise in reference to listed Motors ? | Please find the size of the equipment in KW, mentioned in separate worksheet along with this CRS.
3 | What type of bearings are there in motor/ pump: How many equipment with Antifriction bearings and sleeve bearings. | Please find the bearing type of each equipment, mentioned in separate worksheet along with this CRS.
4 | Can we add more components (vibration sensors) to be more standardized in our picture? | Yes, additional casing vibration sensors can be offered, without any cost implication on BHEL.

## Machine Size & Bearing details
Sl. No. | Machine | No. of M/c per Unit | Orientation | Machine RPM | Rated Continuous output (kW) | Bearing Type
1 | Boiler Feed Pump | 3 | Horz | 4985 | 14272 KW | Sleeve
2 | Booster Pump | 3 | Horz | 1495 | 1134 KW | Sleeve
3 | BFP Motor | 1 | Horz | 1496 | 20500 KW | Sleeve
4 | Cond. Extrn. Pump-CEP | 3 | Vert | 1492 | 1045 KW | Tilting pad
5 | CEP - Motor | 3 | Vert | 1492 | 1450 KW | Antifriction
6 | Drip Pump | 2 | Horz | 1479 | 186 KW | Tilting pad
7 | Drip Pump Motor | 2 | Horz | 1479 | 250 KW | Antifriction
8 | TG DMCW Pump | 3 | Horz | 1500 |  | Antifriction
9 | TG DMCW Pump Motor | 3 | Horz | 1500 |  | Antifriction
10 | SG DMCW Pump | 2 | Horz | 1500 |  | Antifriction
11 | SG DMCW Pump Motor | 2 | Horz | 1500 |  | Antifriction
12 | Mill Motor | 8 | Horz | 985 | 807 KW | Antifriction
13 | ID Fan | 2 | Horz | 745 |  | Antifriction
14 | IDF - Motor | 2 | Horz | 747 | 11800 KW | Sleeve
15 | FD Fan | 2 | Horz | 990 |  | Antifriction
16 | FDF - Motor | 2 | Horz | 995 | 2125 KW | Antifriction
17 | PA Fan | 2 | Horz | 1490 |  | Antifriction
18 | PAF - Motor | 2 | Horz | 1490 | 4700 KW | Sleeve
19 | ACW Pump - ACWP # | 3 | Vert | 1500 |  | Antifriction
20 | ACWP - Motor # | 3 | Vert | 1500 |  | Antifriction
21 | CW Pump - CWP # | 5 | Vert | 420 |  | Antifriction
22 | CWP - Motor # | 5 | Vert | 424 | 2700 KW | Antifriction