## TECHNCIAL
Pre-Bid Clarification Sheet
Tender- | ENQUIRY NO. T7B1R15331 / NIT NO. 39372 ELECTRIC HEATER SKID AND MANDATORY SPARES FOR HPCL, VIZAG, ANDHRA PRADESH PROJECT
Tender Number | T7B1R15331 |  |  |  | DATE - 11/07/2018
Bidder -
Document - TECHNICAL SPECIFICATION FOR ELECTRIC HEATER SKID, PY-51338
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
1 |  |  | Process Data Sheet (PDS) | PDS document is not availabe in tender MR. This is needed to design heater. Kindly provide this document. | 1. WORKING PRESSURE –35.8-41 kg/cm2(g) 2. INLET TEMP - 10 - 25 deg C 3. OUT LET TEMP- 85 deg C 4. PRESSURE DROP- 0.5 kg/cm2 5. DESIGN TEMP- 100 deg C 6. DESIGN PRESSURE - 49 kg/cm2(g) Please refer Annexure-1 for further detail
2 | 5 of 20 | 10.1 | ...site of 01 No. of Electric Heater Skid including…. | Our offer is for supply of heater and its control panel. Skid shall be in client scope. | Heater and its control panel horizontal flour mounting with saddle support is required.
3 | 8 of 20 | 2.2 | Any additional equipment, material, services etc., which are not specifically mentioned in this specification, but required to make the Gas Conditioning System complete in all respects…… | Noted, however our scope in complete system shall be limited to heater and its control panel. | Noted
4 | 9 of 20 | 2.14 | The successful bidder shall furnish design calculations(in native/original format) to BHEL during detailed engineering stage for approval along with the relevant pages of authentic supporting literature….. | No proprietary design calculations shall be submitted in DDE. All datasheets and drawings shall be submitted in PDF format. Any specific documentation shall be mutually discussed. | Noted
5 | 10 of 20 | 3.0.4 | Foundation bolts for skids along with shims (if required), are in the scope of bidder. | Only supports shall be in EXHEAT scope of supply. Foundation bolts along with skid shall be in others scope. | Foundation bolt along shims (if required) shall be in bidder's scope for saddle support.
6 | 11 of 20 | 3.0.8 | All the initial fills like consumable, lubricants, desiccants etc | Not applicable for our scope | Noted
7 | 11 of 20 | 3.0.14 | Training to Owner | Training shall be provided during commissioning activities. Separate classroom or manufacturers work's training is not required. | Noted.
8 | 11 of 20 | 3 | Vendor to limit the setting of thyristor so that maximum power output from it will be limited to 400 KW from each bank irrespective of voltage variation i.e. +- 10%. | Vendor -1 Reply: Noted for 3 banks of 400kW limit on thyristor. Thyristor shall be designed for 400kW at rated voltage. During under voltage thyristor shall be designed to compensate for the same. In such case, thyristor shall be capable to handle 493.82kW | Bidder to consider Multi-drive as per option 3.
Vendor -2 Reply: While considering the negative Voltage variation the Heater capacity will be around 1481KW however we have to design the Control Panel as per above requirement by limiting the current, In this regard we would like to clarify the following regarding availability of Power Control 1. Phase angle control:- In this option we have the feature of current limiting, but the harmonic generation are more than required limitation hence generally not recommended unless not specified.. 2. Integral cycle control :- In this option we have no option to control current limit, but harmonic less than 3%.also unity power factor. 3. Multi-drive is a Full digital and universal Thyristor unit based on a very powerful dedicated micro configurable via serial communication port for all inputs, firing modes, control modes and loads types.Suitable to drive resistive, inductive, transformer and complex loads requiring current limit and power control mode. According please advise further.
9 | 12 of 20 | 15 | Location | Heater shall be designed for Zone 2, II A, T3 Control panel shall be installed in safe area. Please confirm | Zone 2, Gas Group IIA, IIB & IIC, T3 area
10 | 13 of 20 | 20 | Each phase of bank shall be equipped with duplex type over-temperature thermocouple welded to the sheaths of heating elements | Temperarure sensors shall be firmly clamped to elements insuead of welding to avoid any cracks due to differential expansion. | Being minor in nature, it will be discussed during detail engineering.
11 | 14 of 20 | 24 | All sheaths (both heating elements & thermocouples) shall be strength welded to the heater flange. (Bite coupling or brazing or seal welding is not acceptable) | Strength welding is not possible due to spare constraints. All elements shall be seal welded to tubesheet as per standard industry practices. | Bidder to follow specification requiremenrt i.e. All sheaths (both heating elements & thermocouples) shall be strength welded to the heater flange. (Bite coupling or brazing or seal welding is not acceptable)
Document - SPECIFICATION FOR ELECTRIC HEATER (6-51-0059 Rev 1)
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
12A | 5 of 10 | 5.4 | All electronic power devices in heater panel ……… shall be rated under normal operating condition for approx 200% of max current carried by device.. | As per standard practice, All electronic power devices shall be rated for 125% of max current carried by device. | Bidder to follow specification requiremenrt
12B | 7 of 10 | 6.2 | Main terminal Box for Cable connection | if we are connecting the directly to pvc cablesaremoured alumimium cables overheating takes place and termianal is going to melt.So, we are regularly supplying and receomeneding the inetermaideate junction box to connect 10 mtrs long suiatblecopper cables.kindly confirm | Please note that cable size for each heater bank (400 KW) shall be 3 Runs of 3Cx240 sqmm Arm XLPE cable. Intermediate terminal box (junction Box), if recommended by bidder, shall be provided by the bidder for terminating BHEL's incoming cables from thyristor panel.Further, cables between intermediate TB & heater shall be supplied by bidder. Cables shall be PVC/XLPE insulated, Copper conductor, armoured cable. Bidder to note this additional clarification
13 | 9 of 10 | 7.2.2.1 | Burn-in test - 72 hours at 60Deg C at varied voltage. | All circuits shall be tested at designed temperatures for 8 hours as per OEM standard practices. Panels shall be tested at 45 Deg C for 8 hours with available voltage and current. | Being minor in nature, it will be discussed during detail engineering.
Document - JOB SPECIFICATION (EQUIPMENT DIVISION),
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
14 | 69 of 71 | 3.5 | AGITATOR | Not applicable for our scope | Noted
15 | 69 of 71 | 3.6 | VENT SILENCER | Not applicable for our scope | Noted
16 | 69 of 71 | 4 | Spares | We shall provide optional extra price for spares. Our base offer shall be for supplty of heater and its control panel. | Bidder to quote strictly as per Annexure-9 (Price Bid Format) including commissioning& mandatory spares.
Document - STANDARD SPECIFICATION FOR HEATER TUBE SKIN THERMOCOUPLE
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
17 | 5 of 8 | 1.2.5 | Spares - Welding rods | Not applicable as thermocouples are clamped to elements. | Noted
18 | 6 of 8 | 2.2 | MgO insulated sheather thermocouple elements….. | Thermocouple are not insulated with MgO. Heating elements are insulated with MgO. Clause not clear. | Bidder to follow specification requiremenrt
19 |  | 2.4.1 B | OD of sheath shall be 12.7mm and sheath wall thickness shall be min 3.18mm…… | All offered elements shall be of seamless construction as per tender specification. OD of sheath shall be 12.5mm and wall thickness shall be 1.24mm. | Being minor in nature, it will be discussed during detail engineering.
20 | 7 of 8 | 2.5.3 | Thermocouple | We have considered duplex, k type, grounded thermocouple. Please confirm | Being minor in nature, it will be discussed during detail engineering.
21 | 7 of 8 | 2.7 | Terminal head | As per P&ID, all transmitters are supplied by others. Hence terminal heads are not applicable for our scope of supply. All signals shall be terminated in Junction box placed adjacent to main terminal box | Please note that transmitters are supplied by BHEL. However temperature element shall be provided by bidder.
Document - STORAGE AND HANDLING OF MANDATORY SPARES
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
22 |  | 4 | Clearance for dispatch for ordered spares. | Spare parts ordered along with main enquipment shall be dispatched along with main equipment. Since quantity of spares is less, dispatch clearance for main equipment shall be treated as clearance for spares as well. | Being minor in nature, it will be discussed during detail engineering.
Document - ANNEXURE 14: MANDATORY SPARES LIST
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
23 |  | 1.A.IV | Copper links | Offered heater is with Ex d certification. Due to space constraints and considering design aspects, application of copper links cannot be confirmed at this stage. Hence copper links as spares cannot be offered. | Being minor in nature, it will be discussed during detail engineering.
24 |  | 1.B.I | Rectifier Control Module | Offered heaters are thyristor controlled. Rectifiers are not used in our system hence not applicable. | Noted
25 |  | 1.B.VIII | Blocker Diode | Not applicable | Noted
26 |  | 2.a | Instrument valves, tubes.. | Not applicable | Noted
Document - ANNEXURE 16: SUB VENDOR LIST
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
27 |  |  |  | Our manufacturing is in UK and list provided in tender is general list for all items with Indian vendors. Please refer seperately enclosed our approved vendor list for Exheat scope of supply. | AS per project phylosphy, customer vendor list is to be followed. However, considering constraint of bidders from outside India, it will be reviewed positively during detail engineering.
Document - SPECIFICATION FOR SURFACE PREPARATION & PROTECTIVE COATING
SR. No. | Page No. | Clause No. | Tender Specification | Clarification/Deviation requested | Resolution
28 | 27 of 46 | 6 | As per Table -7 of Annex-12 | We have noted detailed specification for painting ang surface preparation. However, no specific details on paint required on heater is provided in tender. As per standard practice one coat of primer and a coat of paint shall be offered. Kindly confirm | Please follow Table -6 of Annex-17