## MAIN SHEET
Main Price Shedule
NAME OF PROJECT: |  | 4X270 MW BHADRADRI FGD THERMAL POWER PROJECT
NAME OF PACKAGE: |  | HVAC FOR FGD
TECHNICAL SPECIFICATION No: |  | PE-TS-440-571-13000-A-A001
S. No. | DESCRIPTION |  |  | UNIT | QTY | Supply |  |  | Service |  | Taxes
|  |  | HSN / SAC CODE |  |  | Total Ex-Works (excluding GST) (INR) | Freight in % | Total Freight | Unit Price (INR) | Total Price (INR) | GST type | GST rate in % | GST amount in Rs. | Total Price Including Freight & GST (INR) | Total Price Including Freight & GST (INR) in words
1 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part, Services Part and Mandatory Spares comprising of design (i.e. preparation and submission of drawing /documents including “As Built” drawings and O&M manuals), engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables, mandatory spares along with spares for erection, start-up and commissioning as required, forwarding, proper packing, shipment and delivery at site, unloading, handling, storage at site, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. |  |  | Lot | 1
2 | MAJOR BREAK-UP OF PRICES GIVEN IN 1.0 ABOVE.
2.1 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part comprising of Design (i.e. Preparation and submission of drawing /documents including “As Built” drawings and O&M manuals), engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as per Appendix-A), fill of lubricants & consumables along with spares for erection (as per Appendix-B), start-up and commissioning spares as required, forwarding, proper packing, shipment and delivery at site for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  |  | Lot | 1
2.2 | Total lumpsum firm prices inclusive of all prevailing taxes, duties and other levies for Services comprising of service part for unloading, handling, transportation & storage at site, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client staff covering hands on experience of operation and maintenance of air conditioning and ventilation system and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  |  | Lot | 1
2.3 | Total lumpsum firm price for Mandatory Spares comprising of manufacture, fabrication, assembly, inspection / testing (as applicable) at vendor's & sub-vendor’s works, painting, forwarding, proper packing, shipment, delivery at site & guarantee as per tender technical specification above, amendment & agreements till placement of order. (Price break up of mandatory spares is to be furnished as per Annexure- II) |  |  | Lot | 1
2.4 | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for providing OPERATION AND MAINTENANCE SERVICE (24x7) including manpower, supervision, consumables etc. for operation & maintenance of HVAC System after commissioning of HVAC system & before final handing over to end customer in flawless condition for the scope defined as per technical specification. |  |  | Months* | 6
Note: 1.) Bidder to quote the Prices in ‘figures’ along with corresponding ‘words’. 2.) Lumpsum price quoted at Sl.no 1.0 shall be considered for evaluation. 3.) For detailed scope of Operation and Maintenance Services, Technical Specification (PE-TS-440-571-13000-A-A001) to be referred. Any variation in no. of months shall be exercised based on unit rate arrived from price quoted against Sl.no 2.4 above.

## Annexure-I
PRICE SCHEDULE ANNEXURE - I
NAME OF PROJECT: |  | 4X270 MW BHADRADRI FGD THERMAL POWER PROJECT
NAME OF PACKAGE: |  | HVAC FOR FGD
SL NO | DESCRIPTION | Qty | UNIT | SUPPLY |  | ERECTION & COMMISIONING
|  |  |  | Unit Price (Ex-works) | Total Price (Ex-Works) | Unit Price (Ex-works) | Total Price (Ex-Works)
A | AIR CONDITIONING SYSTEM
1* | Air-Cooled Precision Package AC of 15TR (Net) complete with all accessories as specified | 6 | NOS*
2 | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), dampers etc. | 1 | LOT
3* | AIR COOLED SPLIT UNITS consisting of outdoor unit (having compressor condenser coils with fan and motor), indoor unit (having evaporator coil, filter,fan with motor), interconnecting refrigerant piping as per site requirement & fittings with insulation, cordless remote, electrical power cord upto the nearest available point along with isolator / MCB, fixing frame for indoor and outdoor unit, Stablizer, etc.
a* | 5.0 TR capacity (ductable type, 415 V, 3 phase with isolation switch). | 2 | NO*
b* | 2.0 TR capacity (non-ductable type, 240 V, 1 phase) with isolation switch, i.e. MCB of suitable rating as specified, voltage stabilizer, cabling, all supporting structure and refrigerant piping to suite actual site condition, drain piping upto nearest drain etc. Split AC shall be of best rating as per latest BEE based on ISEER. | 22 | NO*
c* | 1.5 TR capacity (non-ductable type, 240 V, 1 phase) with isolation switch, i.e. MCB of suitable rating as specified, voltage stabilizer, cabling, all supporting structure and refrigerant piping to suite actual site condition, drain piping upto nearest drain etc. Split AC shall be of best rating as per latest BEE based on ISEER. | 15 | NO*
4* | Drain piping with and without insulation from various equipment upto nearest available drain point with necessary fittings like tees, reducers, expanders, elbows, flanges, valves with flanges, U trap etc as per specifications.
a)* | 50mm with insulation and cladding | 20 | Rmt*
b)* | 40mm with insulation and cladding | 10 | Rmt*
c)* | 50mm without insulation and cladding | 20 | Rmt*
d)* | 40mm without insulation and cladding | 10 | Rmt*
B | VENTILATION SYSTEM
1* | Sheet metal containarized type air washer unit with centrifugal fan (DIDW) with motor, pumps with motors, air washer internals, inlet air louvers, filters, piping as per IS:1239, Part-I (heavy class galvanised), valves, nozzles, back wash arrangement, galvanised drain piping, etc as per specification of capacity 1,10,000 CMH. Each air washer has 1 no centrifugal fan ( 1 x 100% duty) of capacity 1,10,000 CMH at min. 65 mm SP. | 1 | NO*
2* | Roof extractor units (axial flow type) with hood, disconnect switch and all accessories as specified. Following fan shall have 15 mmwc static pressure.
a)* | Capacity 20,000 CMH | 2 | Nos.*
3* | Axial flow supply fans with pre and fine filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3-phase supply). Following fan shall have 30 mmwc static pressure.
a)* | Capacity 10,000 CMH | 10 | Nos.*
b)* | Capacity 7,500 CMH | 6 | Nos.*
c)* | Capacity 6,000 CMH | 2 | Nos.*
d)* | Capacity 4,000 CMH | 2 | Nos.*
4* | Axial flow supply fans with pre filter (wall mounted) complete with casing, TEFC sq cage induction motors & mounting frame, MS rain protection cowl, bird screen and all other accessories (suitable for 415V/3-phase supply) as specified. Following fan shall have 20 mmwc static pressure.
a)* | Capacity 10,000 CMH | 3 | Nos.*
b)* | Capacity 7,500 CMH | 2 | Nos.*
c)* | Capacity 6,000 CMH | 1 | Nos.*
d)* | Capacity 4,000 CMH | 1 | Nos.*
5* | Axial flow exhaust fans (Bifurcated type, spark proof construction, wall mounted) complete with casing, flame proof motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3-phase supply) as specified. Following fan shall have 15 mmwc static pressure.
a)* | Capacity 15,000 CMH | 2 | Nos.*
b)* | Capacity 10,000 CMH | 2 | Nos.*
c)* | Capacity 7,500 CMH | 2 | Nos.*
d)* | Capacity 4,000 CMH | 1 | Nos.*
e)* | Capacity 2,000 CMH | 1 | Nos.*
6* | Axial flow exhaust fans (Wall mounted) complete with casing,TEFC sq cage induction motor & mounting frame, MS rain protection cowl, bird screen and all other accessories epoxy painted (suitable for 415V/3-phase supply) as specified.Following fan shall have 10 mmwc static pressure.
a)* | Capacity 15,000 CMH | 8 | Nos.*
b)* | Capacity 10,000 CMH | 4 | Nos.*
c)* | Capacity 7,500 CMH | 3 | Nos.*
d)* | Capacity 6,000 CMH | 3 | Nos.*
e)* | Capacity 4,000 CMH | 2 | Nos.*
f)* | Capacity 2,000 CMH | 2 | Nos.*
7* | Exhaust fan (propeller type) completes with induction motor & mounting frame MS rain protection cowl, bird screen and all other accessories as specified (suitable for 240V/ 1 phase). Following fan shall have 5 mmwc static pressure.
a)* | Capacity 1200 CMH | 10 | Nos.*
C | COMMON FOR AC AND VENTILATION SYSTEM
1* | GI ducting (finished), diffusers/ grills (with VCD & without VCD), supports (painted), volume control dampers etc. complete with all accessories as required to complete ducting system.
1.1* | Galvanised steel sheets (finished) having zinc coating of atleast 180 gms/ sqm ducting complete with accessories like flanges, bracings, nuts, bolts, washers, gasket, locknut, hilti, threaded hanging rods, supports (painted), vanes, splitter dampers, sealant, adhesive etc. required to make the installation complete in all respect.
a)* | 18 G | 230 | SQM*
b)* | 20 G | 290 | SQM*
c)* | 22 G | 560 | SQM*
d)* | 24 G | 450 | SQM*
1.2* | Thermal insulation along with finish as per specification for AC Supply & Return air and exposed Ventilation Supply air duct | 920 | SQM*
1.3* | Supply air Grill/diffuser with VCD (Extruded Aluminium) complete with fixing frames, nuts, bolts, gaskets, washers etc. | 16 | SQM*
1.4* | Return air Grill/diffuser without VCD (Extruded Aluminium) complete with fixing frames, nuts, bolts, gaskets, washers etc. | 10 | SQM*
1.5* | Supply air Grill/diffuser with VCD (MS, POWDER COATED) complete with fixing frames, nuts, bolts, gaskets, washers etc. | 8 | SQM*
1.6* | Return air Grill/diffuser without VCD (MS, POWDER COATED) complete with fixing frames, nuts, bolts, gaskets, washers etc. | 2 | SQM*
1.7* | Volume control damper in GI construction as per specification complete with fixing arrangement. | 11 | SQM*
1.8* | Wall mounted dampers (gravity operated) for different areas. | 30 | SQM*
1.9* | Inlet Louvres | 15 | SQM*
1.10* | MS Duct With Epoxy paint for battery room. | 7 | SQM*
2* | ACOUSTIC INSULATION (AS PER THE SPECIFICATION) | 250 | SQM*
3* | FIRE DAMPER
a)* | Fire damper | 10 | SQM*
b*) | Fusible Link type Fire Damper | 4 | SQM*
4* | Motorized Actuator with single phase power supply for the above Fire damper / Volume control damper etc with auto resetting, limit switches, indication lamps etc. | 16 | NOS*
5* | Handling arrangement for ventilation equipments
a)* | Manual trolley (Manually operated, platform trolley of 1.5 Ton capacity with base area 2m x 1.5m) | 1 | NO*
b)* | 1T Chain pulley block without travelling trolley with tripod arrangement | 1 | NO*
6 | Cable tray, condutes, junction box,lugs and glands, Local control panel and Field instruments like pressure gauge, temperature gauge, switches and transmitters for pressure, flow and temperature measurement, differential pressure switch across filters, flow meters, RH and Temperature sensor, cabling work as per Electrical scope sheet, and other required instruments as per specifications, including necessary control panel for hook up with main DDCIMS as per specifications | 1 | LOT
7* | Fibre optic Cable with its accessories | 100 | Meter*
8* | Providing full support during FAT of DDCIMS, preparation of control scheme, and commissining of DDCIMS as per relevent specification. | 20 | Mandays*
9 | Total lumpsum price for special tools & tackles for maintenance inclusive of packing forwarding, transportation up to site, etc. (Break up of to be furnished as per Appendix- A) | 1 | LOT
10 | Total lumpsum price for commissioning spares inclusive of packing forwarding, transportation up to site, etc. (Break up of to be furnished as per Appendix- B) | 1 | LOT
11 | Any other item not indicated above, but required to make the system complete in all respects. | 1 | LOT
TOTAL=
NOTES
1 | The bidder shall furnish unit rates for variable item (marked *) for necessary adjustment (plus or minus) variation during detailed engg. stage. The unit rates quoted above shall be considered and no separate unit rates shall be quoted. Unit rates shall be valid throughout the contract.
2 | Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price.
3 | Bidder to note that above BOQ for this tender has to be read in conjunction with tender specification. Any item, if not mentioned in above BOQ but indicated in tender specification and required for completion of the system shall deemed to be included in above price.

## APPENDIX-A
PRICE SCHEDULE APPENDIX - A Maintenance tools & tackles
NAME OF PROJECT: |  |  | 4X270 MW BHADRADRI FGD THERMAL POWER PROJECT
NAME OF PACKAGE: |  |  | HVAC FOR FGD
SL NO | DESCRIPTION | UNIT | Qty | Unit Price (Ex-works) | Total Price (Ex-Works)
1 | FLAT D WRENCH - 6 MM TO 32 MM (12 Pcs) | SET | 1
2 | BOX WRENCHES - 6 MM TO 22 MM (14 Pcs) | SET | 1
3 | RING SPANNER - 6 MM TO 32 MM (12 Pcs) | SET | 1
4 | ALLEN KEYS - 2 MM TO 10 MM | SET | 1
5 | CRESCENT SCREW SPANNER | NO. | 1
6 | SCREW DRIVER | NO. | 1
7 | OFFSET SCREW DRIVER | NO. | 1
8 | INSULATED PLIER | NO. | 1
9 | TORCH LIGHT ( SUITABLE FOR 2 CELL) | NO. | 1
10 | HAMMER 1 LB | NO. | 1
11 | OIL CAN | NO. | 1
12 | POCKET THERMOMETER - 0 TO 50 DEG. C | NO. | 1
13 | INSULATION TAPE ROLL | NO. | 1
14 | STEEL FOOT RULE - 12" | NO. | 1
15 | FEELER GAUGE 9 BLADES | NO. | 1
16 | PIPE WRENCH | NO. | 1
17 | FLARE NUT (1/4") | NOS. | 6
18 | FLARING TOOL | NO. | 1
19 | TUBE CUTTER | NO. | 1
20 | GAS CHARGING PIPE | NO. | 1
21 | NITROGEN CHARGING ADAPTER | NO. | 1
22 | PRESSURE GAUGE (2 1/2" DIA DIAL) 0 - 300 PSI | NO. | 1
23 | PRESSURE GAUGE (2 1/2" DIA DIAL) 0 - 500 PSI | NO. | 1
24 | COMPOUND GAUGE (2 1/2" DIA DIAL) (-)30” to 150 PSI | NO. | 1
25 | PSYCHRO METER | NO. | 1
26 | LOCK WITH KEY FOR TOOL BOX | NO. | 1
27 | RATCHET 1/4" | NO. | 1
28 | MS TOOL BOX | NO. | 1
29 | Measuring tape | NO | 1
30 | Tachometer | NO | 1
31 | Double ended spanner | SET | 1
32 | Gasket punch | NO. | 1
33 | Centre punch | NO. | 1
34 | Scissors for sheet metal cutting | NO. | 1
35 | Multimeter | NO. | 1
36 | Anemometer | NO. | 1
37 | Slide wrench 8” | NO. | 1
38 | Slide wrench 10” | NO. | 1
39 | Slide wrench 6” | NO. | 1
40 | Box spanner set | SET | 1
TOTAL=
NOTES
1 | ABOVE IS THE MINIMUM LIST. ANY OTHER TOOL / TACKEL REQUIRED FOR THE SYSTEM SHALL ALSO BE PROVIDED BY THE VENDOR WITHOUT ANY COST IMPLICATION.
2 | SUPPLY OF SPECIAL TOOLS AND TACKLE INCLUDING TOOLBOX REQUIRED FOR OPERATION, MAINTENANCE AND OVERHAULING OF THE SYSTEM IS IN THE SCOPE OF THE BIDDER.

## APPENDIX-B
PRICE SCHEDULE APPENDIX - B Commissioning spares
NAME OF PROJECT: |  | 4X270 MW BHADRADRI FGD THERMAL POWER PROJECT
NAME OF PACKAGE: |  | HVAC FOR FGD
SL NO | DESCRIPTION | UNIT | Qty | Unit Price (Ex-works) | Total Price (Ex-Works)
1 | FAN BELTS | SET | 1
2 | PRESSURE GAUGE | NO. | 1
3 | TEMPERATURE GAUGE | NO. | 1
4 | FILTER | SET | 1
5 | COMPRESSOR OIL | Lot | 1
6 | REFRIGERANT | Lot | 1
7 | LUBRICANT (EACH TYPE) | Lot | 1
TOTAL=
NOTES
1 | ABOVE IS THE MINIMUM LIST. ANY OTHER COMMISSIONING SPARE REQUIRED FOR THE SYSTEM SHALL ALSO BE PROVIDED BY THE VENDOR WITHOUT ANY COST IMPLICATION.

## Annexure-II
MANDATORY SPARES ANNEXURE - II
NAME OF PROJECT: |  | 4X270 MW BHADRADRI FGD THERMAL POWER PROJECT
NAME OF PACKAGE: |  | HVAC FOR FGD
SL NO | DESCRIPTION | Qty | Unit Price (Ex-works) | Total Price (Ex-Works)
A | AIR CONDITIONING
2.7 | Precision Air Conditioners / Package Air Conditioners
2.7.1a | Vibration Isolators | 2 sets for every category
2.7.1 | Filters | 2 set for each PAC unit
2.7.2 | Bearings | 2 set for each rating of PAC unit (both for condenser & Indoor Unit)
2.7.2a | Condenser fan impeller | 2 set for each rating of PAC unit
2.7.3 | Expansion valve | 2 set for each rating of PAC unit
2.7.3a | Any other spare parts recommanded by the manufacturer | 2 set for each rating of PAC unit
2.7a | Split Air Conditioners
1 | Fan-motor bearing for outdoor | 2 sets for each rating of SAC
2 | Vibration Isolators | 2 set each for outdoor unit & Indoor unit for each SAC unit
3 | Filter | 2 sets for each rating of SAC unit
4 | Expansion valve | 2 set for each rating of SAC unit
5 | Any other spare parts recommanded by the manufacturer | 2 set for each rating of SAC unit
2.12 | Mandatory Spares for Temperature Elements and Thermowells | As applicable
2.12.1 | Thermocouple / RTD elements (10% of each type, rating and immersion length. Minimum 5 nos..) | 10% of each type, rating and immersion length. Minimum 5 nos.
2.12.2 | Thermowells for each type of temperature sensors (10% of each type, rating and immersion length. Minimum 5 nos.) | 10% of each type, rating and immersion length. Minimum 5 nos.
2.13 | Mandatory Spares for Electronic Transmitters (for pressure, DP, Flow, level, Temperature) and Electrical Transducers.
2.13.1 | Transmitters and Electrical Transducers (10% of total or atleast two (whichever is higher) for each type along with accessories.) | 10% of total or atleast two (whichever is higher) for each type along with accessories.
2.14 | Mandatory spares for local gauges/switch (for Pressure, DP, Temperature, Flow, level , etc.)
2.14.1 | Local gauges/ Switch (for Pressure, DP, Temperature, Flow, level , etc.) (10% of total or atleast two (whichever is higher) for each type along with accessories.) | 10% of total or atleast two (whichever is higher) for each type along with accessories.
2.16 | Electrical Spares for Motors
2.16.2 | Motor bearing set for fresh air fan motor | 1 set for each type and rating of fan motor
B | VENTILATION SYSTEM
1.1 | Centrifugal fans
1.1.1 | Set of bearings for Air washer fans | 2 Set for each Type of Fan
1.1.3 | Impeller for the fan | 2 sets for each type of fan
1.1.4 | Vibration isolators | 2 sets for each type of fan
1.2 | Centrifugal pumps
1.2.1 | Set of bearings for Air washer pumps | 2 Set for each Type and rating of Pump
1.2.3 | Mechanical seal / gland packing as applicable, shaft sleeve & casing wearing rings and lantern rings for shaft and impeller | 2 Set for each Type and rating of Pump
1.2.4 | Complete Impeller Assembly | 2 Set for each application and ratings of Pumps
1.2.5 | Key for impeller | 1 No. for each application and ratings of Pumps
1.2.6 | Pump shaft | 1No. for each application and ratings of Pumps
1.2.7 | Coupling | 1 No. for each application and ratings of Pumps
1.3 | Spray Nozzles
1.3.1 | Spray nozzles for air washer unit | 2 set for each type
1.4 | SS Filters
1.4.1 | SS Filters for Air washer | 2 set for each type
1.4a | Flow Regulating Valve (Not there in BTPS and there in KTPS)
1.4a.1 | For Air washer | 20% or min. 1 no whichever higher
1.5 | Basket for POT Strainer
1.5.1 | Strainer Busket for Air Washer | 2 No. for each type and size
1.6 | Valves
1.6.1 | Gate valve for Air washer | 20% or Minimum 1No. Whichever is higher
1.6.2 | NR Valve for Air Washer | 20% or Minimum 1No. Whichever is higher
1.6.5 | Gate Valve for Make-up Drain of Air washer | 20% or Minimum 1No. Whichever is higher
1.6.7 | Other LP Piping valves & traps - Complete assembly | 5% or min. 1 no. (whichever is more) for each size, type & rating for total population
1.7 | Wall mounted supply/ Exhaust fan
1.7.1 | Fan-motor Bearing | 2 set for each rating of fan
1.7.2 | Vibration Isolators | 2 set for each fan
1.7a | Fan-Filter Units
1.7.a1 | Filters | 2 set for each rating of FFU
1.7.a2 | Vibration Isolators | 2 set for each FFU
1.7.a3 | Fan-motor bearing | 2 set for each rating of FFU
1.7.a4 | Back Draft Dampers | 2 set for each rating of FFU
1.7.a5 | Any other spare parts recommended by the Manufacturer | 1 no. of each size
1.8 | Electrical Spares for Motors
1.8.1 | Motor bearing set for Air washer fan motor | 2 set for each type of fan motor
1.8.3 | Motor bearing set for axial flow supply fan motor | 2 set for each rating of fan motor
1.8.4 | Motor bearing set for axial flow exhaust fan motor | 2 set for each rating of fan motor
1.8.4a | Terminal plates | 10 nos. each for small motors up to 30 kw and 4 nos. each for motors above 30 kw
1.8.4b | Heaters | 2 set for each motor of rating above 30 kw
1.8.4c | Greasing arrangement | 4 sets for each type of motors
1.8.4d | Motor for fans | 2 set for each rating of fan
1.8.4e | Bearing (DE & NDE) | 4 sets of each type and rating
1.9 | Mandatory Spares for Temperature Elements and Thermowells | As applicable
1.9.1 | Thermocouple / RTD elements (10% of each type, rating and immersion length. Minimum 5 nos..) | 10% of each type, rating and immersion length. Minimum 5 nos.
1.9.2 | Thermowells for each type of temperature sensors (10% of each type, rating and immersion length. Minimum 5 nos.) | 10% of each type, rating and immersion length. Minimum 5 nos.
1.1 | Mandatory Spares for Electronic Transmitters (for pressure, DP, Flow, level, Temperature) and Electrical Transducers. | As applicable
1.10.1 | Transmitters and Electrical Transducers (10% of total or atleast two (whichever is higher) for each type along with accessories.) | 10% of total or atleast two (whichever is higher) for each type along with accessories.
1.11 | Mandatory spares for local gauges/switch (for Pressure, DP, Temperature, Flow, level , etc.) | As applicable
1.11.1 | Local gauges/ Switch (for Pressure, DP, Temperature, Flow, level , etc.) (10% of total or atleast two (whichever is higher) for each type along with accessories..) | 10% of total or atleast two (whichever is higher) for each type along with accessories.
Total=
NOTES
1 | Mandatory spares listed above is bare minimum requirement. In case any additional mandatory spares requirement is covered elsewhere in the tender specification apart from specified above, same shall be deemed to have been covered in bidders scope of supply.
2 | Unless stated otherwise, a "set" or "Lot" means items required for complete replacement in one equipment of each type / size/ range.
3 | Wherever quantity has been specified as percentage (%), it shall mean percentage (%) of the population of the item required for one unit of 270 MW in the station (project), unless specified otherwise.
4 | In case of Bought Out items, itemised spares list may be vendor specific and may differ from the list of spares mentioned above. In such cases, The quoted price shall be considered for applicable items only without any change in the contract price.
5 | All Spares shall be supplied as per the requirement of the specifications. In case any spare indicated in the specification is “not applicable” for particular equipment, then suitable applicable alternate spare has been offered / shall be supplied by the bidder without any financial implication."
6 | Bidder to write “Quoted / Not Applicable” against all items. Any item which is quoted as “not applicable” by the bidder in the above list and is found to be “applicable” at a later date shall be supplied by the bidder without any commercial and delivery implication.
7 | For quantities indicated in percentage, fractions are to be rounded-off to next higher integer.
8 | Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price.
9 | Bidder to note that even though there may be some spares which are repetitive at various sl.no mentioned above, bidder to ensure that prices are quoted against each sl.no. In case any cell is left blank in the unpriced schedule shall be treated as "quoted" and included in total price.
10 | The list of mandatory spares given above shall be finalized during detailed engineering. Prices for any variation in quantity shall be adjusted based on unit rate deduced from total prices quoted by bidder against respective mandatory spares.

## ANNEXURE-III (hidden)
SUGGESTED PRICE FORMAT ANNEXURE-III: GUARANTEED POWER CONSUMPTION FORMAT |  |  |  |  | Doc No: | PE-PF-483-(571-13000-A)-A001
[5 empty] | Rev No: | 0
[5 empty] | Date of issue | 2021-06-19
NAME OF PROJECT: |  |  |  | 2X500 MW TUTICORIN TPP (FGD SYSTEM PACKAGE)
NAME OF PACKAGE: |  |  |  | HVAC FOR FGD
TECHNICAL SPECIFICATION No: |  |  |  | PE-TS-483-(571-13000-A)-A001
GUARANTEED POWER CONSUMPTION FORMAT
Sl.No. | Description / Item | Working | Standby | Power Consumption (KW) (at motor input terminal) | Duty Factor | Power Consumption (KW)
1 | 2 | 3 | 4 | 5 | 6 | 7 = 3 x 5 x 6
1 | AC SYSTEM
1.1 | AIR COOLED CONDENSING UNIT
1.1.1 | OUTDOOR UNIT | 1 | 1
1.1.2 | AHU FAN | 1 | 1 |  | 1
2 | VENTILATION SYSTEM
2.1 | UAF
2.1.1 | UAF FAN | 1 | 0 |  | 1
Total Guaranteed power (KW)
Notes
1 | Estimated power consumption (EPC) figure for the system (for working drives only) has been considered as 206 KW. So long bidder's quoted guaranteed power consumption (GPC) above remains within this EPC, there will be no technical loading of bid on power consumption for evaluation. However, if bidder's quoted GPC exceeds EPC, there shall be technical loading of bid for evaluation @ USD 2129 per KW of additional power over EPC. Bidder’s guaranteed power consumption at motor input terminals (not shaft power) as furnished in relevant schedule shall be demonstrated by the successful bidder during performance testing at works/ site. In case power consumption is noted higher than EPC / bidder's quoted GPC whichever is higher, during inspection/ PG test, penalty @ USD 2129 per KW shall be levied on vendor. USD conversion rate shall be taken as defined in NIT. Above guaranteed power consumption value shall be at 20 deg. C for centrifugal fans for AHUs and 30 deg. C for centrifugal fans of UAF units and at an elevation of RL of site for both AHUs and UAF centrifugal fans.
Particulars of bidder / authorised representative
Name | Designation |  |  | Signature | Date | Company Seal