## MAIN SHEET
PRICE FORMAT
NAME OF THE BIDDER
NAME OF PROJECT: |  | 2X 800 MW LARA TPP MAIN PLANT
NAME OF PACKAGE: |  | AC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-508-553-A001
[5 empty] | Supply |  |  | Service |  | Taxes
S. No. | DESCRIPTION |  | UNIT | QTY | Total Ex-Works (excluding GST) | Freight in % | Total Freight | Unit Price | Total Price | GST type | GST rate in % | GST amount | Total Price Including Freight & GST
1 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part, Services part and Mandatory spares comprising of design (i.e.preparation and submission of drawing /documents including “As Built” drawings and O&M manuals), engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable) fill of lubricants & consumables, mandatory spares alongwith spares for erection, startup and commissioning as required, forwarding, proper packing, shipment and delivery at site, unloading, handling, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff, Operation & Maintenance of AC System (24x7) before handing over after commissioning, and handover in flawless condition of the package to the end customer complete with all accessories, for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. |  | Lot | 1 | [8 empty] | 0
2 | MAJOR BREAK-UP OF PRICES GIVEN IN 1.0 ABOVE.
2.1* | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for Design (i.e. Preparation and submission of drawing /documents including “As Built” drawings and O&M manuals) and engineering as per tender technical specification above, amendment & agreements till placement of order. |  | LOT | 1 | NA |  |  |  | 0 |  |  | 0 | 0
2.2 | Total lump sum firm price inclusive of all prevailing taxes, duties and other levies for Supply part comprising of manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables along with spares for erection as required, start-up and commissioning spares as required, forwarding, proper packing, shipment and delivery at site for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | 0 |  | 0 | NA |  |  |  | 0 | 0
2.3 | Total lumpsum firm prices inclusive of all prevailing taxes, duties and other levies for Services part comprising for unloading, handling, transporation to site, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee / Functional / Demonstration tests at site (As applicable), training of customer/client O&M staff and handover in flawless condition of the package to the end customer complete with all accessories, for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | NA |  |  | 0 |  |  |  | 0 | 0
2.4 | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for Mandatory Spares comprising of manufacture, fabrication, assembly, inspection / testing (as applicable) at vendor's & sub-vendor’s works, painting, forwarding, proper packing, shipment, delivery at site & guarantee as per tender technical specification above, amendment & agreements till placement of order. (Price break up of mandatory spares is to be furnished as per Annexure- II) |  | Lot | 1 |  |  | 0 | NA |  |  |  | 0 | 0
2.5* | Total lumpsum firm price inclusive of all prevailing taxes, duties and other levies for providing Operation and Maintenance Service (24x7) including manpower, supervision, consumables etc. for operation & maintenance after commissioning of AC system before final handing over to end customer in flawless condition for the scope defined as per technical specification. |  | Months* | 12 | NA |  |  |  | 0 |  |  | 0 | 0
Note: 1) Please note that the complete engineering of the package is in the scope of bidder as per the tender requirement. However, for the payment purpose bidder to note that 50% of price as per sl. no. 2.1 shall be made against basic engineering (i.e. Preparation, submission & approval of basic drawing/ documents as indicated in tender specification) and the remaining payment shall be made for the balance engineering part on pro-rata basis. 2) For detailed scope of Operation and Maintenance Services, Technical Specification to be referred. Any variation in no. of months shall be exercised based on unit rate arrived from price quoted against Sl.no 2.5 above.

## ANNEXURE-I
ANNEXURE - I : PRICE BREAKUP FOR SUPPLY PART
NAME OF PROJECT: |  | 2X 800 MW LARA TPP MAIN PLANT
NAME OF PACKAGE: |  | AC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-508-553-A001
| ITEM DESCRIPTION | QTY. | UNIT | SUPPLY |  | E&C
|  |  |  | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR) | Unit E&C Price (INR) | Total E&C Price (INR)
BREAK-UP OF ITEMS MENTIONED AT S. NO. 2.2 OF MAIN SHEET
A | AC-Plant-1: CENTRAL CHILLED WATER SYSTEM FOR MAIN CR AREAS COMMON FOR UNIT-1&2
1* | Water cooled Chilling machine each of minimum 150 TR capacity (actual) consisting of (a) Screw refrigerant compressor complete with motors, control panel, multi drive set, controls and interlocks other accessories as specified; (b) Water cooled condenser adequately sized with suitable anti corrosive paint coating for tube and shell part coming in contact with soft water & other accessories and (c) Shell & tube type water chiller & other accessories, as specified. | 3 | NO*
2 | Sheet metal cabinet type air handling units (double skin as per specification) consisting of chilled water cooling coil, centrifugal blower, TEFC sq cage induction motor, non-return damper, motorised volume control damper,filters (pre filter), 3 way motorised mixing valve with thermostatic controls and other accessories to meet the AC load of the main CR areas of Unit I & II at 17.0m. Fine Filters and HEPA Filters for AHUs shall be included in individual discharge of AHU as per specification. | 4 | NO
3 | Sheet metal cabinet type air handling units (double skin as per specification) consisting of chilled water cooling coil, centrifugal blower, TEFC sq cage induction motor, non-return damper, motorised volume control damper,filters (pre filter), 3 way motorised mixing valve with thermostatic controls and other accessories to meet the AC load of the UPS, SWAS Room, Water Analysis Lab of Unit I & II at 8.5m & 0 .0m. Fine Filters and HEPA Filters in individual discharge of AHUs as per specification. | 3 | NO
4 | Fibreglass reinforced plastic (FRP) construction cooling towers complete with fan, motor, FRP basin, nozzles, make-up water & quick fill water connection, Instruments, drains, piping, valves, strainers, ladder, structural support & all accessories as specified. | 3 | NO
5 | Centrifugal pump sets for condenser water recirculation complete with TEFC motor & all accessories as specified. | 3 | NO
6 | Centrifugal pump sets for chilled water recirculation complete with TEFC motor set & all accessories, as specified. | 3 | NO
7 | Condenser water piping with necessary fittings, strainers, valves including piping from soft water storage tank to cooling tower, chiller, condenser water pumps, pan humidifiers of AHU room as specified. | 1 | LOT
8 | Chilled water piping within AC plant room, AHU rooms and from AC plant room to various AHU rooms, chilled water pumps, expansion tank complete with valves, supports, fittings, strainers,insulation with finish as per specification. | 1 | LOT
9 | Monsoon reheating/ winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat & humidistat/ sensors etc. | 1 | LOT
10 | Pan type humidifier for each AHU room. | 1 | LOT
11 | Fresh air fan (axial flow type), complete with motor,inlet cone, air filters (pre and fine), modulating dampers etc. as per specification for each AHU room. | 1 | LOT
12 | Soft water/Make-up MS /FRP Storage tank to cooling towers with instruments, valves and other accessories as required. Capacity of each tank min. 8 m3 . | 2 | NO
13 | MS/FRP Expansion Tank (insulated) spray galvanised from inside for chilled water with all accessories like instruments and valves as required, capacity min. 1 m3. | 1 | NO
14 | MS/FRP Make up Tank (Tanks shall be MS & inner surface spray galvanised. Make up water line with with all accessories like instruments and valves as required. Capacity of each tank min. 2 m3 . | 1 | Nos
15 | Skid mounted softening plant (2 x 100 % ) with associated piping,valves, instruments, soft water pumps & regeneration pumps, chemical dosing pump, reject transfer pump & tanks as applicable & as per tender requirement. | 1 | SET
16* | Pumps with motor set along with accessories for pumping of softening plant reject and cooling tower blow down to CMB. | 2 | Nos.*
B | AC Plant -2, (For ESP control room, FGD control room and Ash Handling Control Rooms, for Unit-1 &2
1* | Water cooled Chilling machine each of minimum 130 TR capacity (actual) consisting of (a) Screw refrigerant compressor complete with motors, control panel, multi drive set, controls and interlocks other accessories as specified; (b) Water cooled condenser adequately sized & other accessories and (c) Shell & tube type water chiller & other accessories, as specified. | 3 | Nos*
2 | Sheet metal cabinet type air handling units (double skin as per specification) consisting of chilled water cooling coil, centrifugal blower, TEFC sq cage induction motor, non return damper,filters (pre filter), 3 way motorised mixing valve with thermostatic controls and other accessories to meet the AC load of the ESP control room, FGD control room areas of Unit I. Fine Filters in discharge for individual AHUs shall also be included. | 4 | Nos*
3 | Sheet metal cabinet type air handling units (double skin as per specification) consisting of chilled water cooling coil, centrifugal blower, TEFC sq cage induction motor, non return damper,filters (pre filter), 3 way motorised mixing valve with thermostatic controls and other accessories to meet the AC load of the ESP control room, FGD control room areas of II . Fine Filters in discharge for individual AHUs shall also be included. | 4 | Nos*
4* | Sheet metal cabinet type air handling units (double skin as per specification) consisting of chilled water cooling coil, centrifugal blower, TEFC sq cage induction motor, non return damper,filters (pre filter), 3 way motorised mixing valve with thermostatic controls and other accessories to meet the AC load of the AHP MCC 1 near Bottom Ash U1 Area. Fine Filters in discharge for individual AHUs shall also be included. | 2 | Nos*
5* | Sheet metal cabinet type air handling units (double skin as per specification) consisting of chilled water cooling coil, centrifugal blower, TEFC sq cage induction motor, non return damper,filters (pre filter), 3 way motorised mixing valve with thermostatic controls and other accessories to meet the AC load of the AHP MCC 2 near Compressor House (DCS ROOM & Control Room). Fine Filters in discharge for individual AHUs shall also be included. | 2 | Nos*
6* | Sheet metal cabinet type air handling units (double skin as per specification) consisting of chilled water cooling coil, centrifugal blower, TEFC sq cage induction motor, non return damper,filters (pre filter), 3 way motorised mixing valve with thermostatic controls and other accessories to meet the AC load of the AHP MCC 3 near Silo area (DCS / VFD & HCSD Control Room). Fine Filters in discharge for individual AHUs shall also be included. | 2 | Nos*
7* | Fibreglass reinforced plastic (FRP) construction cooling towers complete with fan, motor, FRP basin, nozzles, make-up water & quick fill water connection, Instruments, drains, piping, valves, strainers, ladder, structural support & all accessories as specified. | 3 | NO*
8* | Centrifugal pump sets for condenser water recirculation complete with TEFC motor & all accessories as specified. | 3 | NO*
9* | Centrifugal pump sets for chilled water recirculation complete with TEFC motor set & all accessories, as specified. | 3 | NO*
10 | Condenser water piping with necessary fittings, strainers, valves including piping from soft water storage tank to cooling tower, chiller, condenser water pump, pan humidifiers of AHU room of Unit ESP as specified. | 1 | LOT
11 | Complete Insulated Chilled water piping within AC plant room, from AC Plant Room to AHU room ESP building Unit 1 and from AC plant room to ESP building Unit 2 AHU room, complete with valves supports, fittings, strainers, insulation with finish as per specification. | 1 | LOT
12* | Complete Insulated Chilled water piping from ESP building to AHP MCC 1 near Bottom Ash U1 Area complete with valves supports, fittings, strainers, insulation with finish as per specification. | 1 | LOT*
13* | Complete Insulated Chilled water piping from ESP building to AHP MCC 2 near Compressor House (DCS ROOM & Control Room) AHU room complete with valves supports, fittings, strainers, insulation with finish as per specification. | 1 | LOT*
14* | Complete Insulated Chilled water piping from ESP building to AHP MCC 3 near Silo area (DCS / VFD - Room & HCSD Room) complete with valves supports, fittings, strainers, insulation with finish as per specification. | 1 | LOT*
15 | Monsoon reheating/ winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat & humidistat/ sensors etc. for each ESP cum FGD control room and AHP control rooms. | 1 | LOT
16 | Pan type humidifier for each AHU room for each ESP cum FGD control room and AHP control rooms. | 1 | LOT
17 | Fresh air fan (axial flow type), complete with motor,inlet cone, air filters (pre and fine), modulating dampers etc. as per specification for each AHU room of ESP cum FGD control room Unit I & II and AHP control rooms. | 1 | LOT
18 | Soft water/Make-up MS /FRP Storage tank to cooling towers with isntruments, valves and other accessories as required. Capacity of each tank min. 4 m3 . | 2 | NO
19 | MS/FRP Expansion Tank (insulated) for chilled water with all accessories as required, capacity 1 m3. | 1 | No.
20 | MS/FRP Make up Tank 2m3 (Tanks shall be MS & inner surface spray galvanised. Make up water line with float valve & backup, quick fill line with ball valve, drain line with ball valve, overflow & vent line, level gauge shall be provided). | 1 | No
21 | Skid mounted softening plant (2 x 100 % ) with associated piping,valves, instruments, soft water pumps & regeneration pumps & tanks as applicable & as per tender requirement. | 1 | SET
22* | Pumps with motor set along with accessories for pumping of softening plant reject and cooling tower blow down to CMB. | 2 | Nos.
C | AC-Plant-3: DX TYPE AIR COOLED CONDENSING UNIT FOR OFFICE ROOM CCR, CER
1* | DX type, air cooled condensing unit of minimum 40 TR capacity (actual). The refrigerant compressor shall be Scroll, hermetic / Semi-hermetic type suitable for Refrigerant R-134a / R-407c / R-410a environment friendly HFC refrigerants with drive package, Suction and discharge valves, capacity control system, expansion valve, crank case heater etc. A control panel shall be provided to house all gauges and controls. The panel shall contain all necessary terminal strips to facilitate external wiring. The unit shall be complete with expansion valve, all necessary fittings, accessories, insulated refrigerent piping to and from AHUs, foundation bolts, nuts, washers etc complete in all respect. | 2 | Nos.*
2* | Sheet metal cabinet type air handling units (double skin as per specification) The draw through horizontal AHUs shall comprise of Dampers, pre filter, fine filters, DX- cooling coil, Fan section with fan & TEFC sq cage induction motor, condensate drain pan, thermostatic controls and other accessories, like ladder along with supporting structure for filter and plenum, etc. to meet the AC load of control room area as per specification. | 2 | NO
3* | Monsoon reheating / winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat etc. | 1 | LOT
4 | PAN type HUMIDIFIER for each AHU room complete with humidistat, geyserstat safety controls, make up water piping from make up tank / nearest source of water, valves fittings etc | 1 | LOT
5 | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), modulating dampers etc. as per specification for each AHU room. | 1 | LOT
D | AC-Plant-4: DX TYPE AIR COOLED CONDENSING UNIT FOR WATER SYSTEM CONTROL BUILIDNG
1* | DX type, air cooled condensing unit of minimum 30 TR capacity (actual). The refrigerant compressor shall be Scroll, hermetic / Semi-hermetic type suitable for Refrigerant R-134a / R-407c / R-410a environment friendly HFC refrigerants with drive package, Suction and discharge valves, capacity control system, expansion valve, crank case heater etc. A control panel shall be provided to house all gauges and controls. The panel shall contain all necessary terminal strips to facilitate external wiring. The unit shall be complete with expansion valve, all necessary fittings, accessories, insulated refrigerent piping to and from AHUs, foundation bolts, nuts, washers etc complete in all respect. | 2 | Nos.*
2* | Sheet metal cabinet type air handling units (double skin as per specification) The draw through horizontal AHUs shall comprise of , Dampers, pre filter, fine filters, DX- cooling coil, Electric heating coil, Electric steam humidifier and Fan section with fan & TEFC sq cage induction motor, drive set, condensate drain pan, thermostatic controls and other accessories, like ladder along with supporting structure for filter and plenum, etc. to meet the AC load of control room area as per specification. | 2 | Nos.*
3 | Monsoon reheating / winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat etc. | 1 | LOT
4 | PAN type HUMIDIFIER for each AHU room complete with humidistat, geyserstat safety controls, make up water piping from make up tank / nearest source of water, valves fittings etc | 1 | LOT
5 | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), modulating dampers etc. as per specification for each AHU room. | 1 | LOT
E | AC-Plant-5: DX TYPE AIR COOLED CONDENSING UNIT FOR CEP VFD BUILDING UNIT-1
1* | DX type, air cooled condensing unit of minimum 30TR capacity (actual). The refrigerant compressor shall be Scroll, hermetic / Semi-hermetic type suitable for Refrigerant R-134a / R-407c / R-410a environment friendly HFC refrigerants with drive package, Suction and discharge valves, capacity control system, expansion valve, crank case heater etc. A control panel shall be provided to house all gauges and controls. The panel shall contain all necessary terminal strips to facilitate external wiring. The unit shall be complete with expansion valve, all necessary fittings, accessories, insulated refrigerent piping to and from AHUs, foundation bolts, nuts, washers etc complete in all respect. | 2 | Nos.*
2* | Sheet metal cabinet type air handling units (double skin as per specification) The draw through horizontal AHUs (min. 60 mmWC SP) shall comprise of Dampers, pre filter, fine filters, DX- cooling coil, Fan section with fan & TEFC sq cage induction motor, condensate drain pan, thermostatic controls and other accessories, like ladder along with supporting structure for filter and plenum, etc. to meet the AC load of control room area as per specification. | 2 | Nos.*
3 | Monsoon reheating / winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat etc. | 1 | LOT
4 | PAN type HUMIDIFIER for each AHU room complete with humidistat, geyserstat safety controls, make up water piping from make up tank / nearest source of water, valves fittings etc | 1 | LOT
5 | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), modulating dampers etc. as per specification for each AHU room. | 1 | LOT
F | AC-Plant-6: DX TYPE AIR COOLED CONDENSING UNIT FOR CEP VFD BUILDING UNIT-2
1* | DX type, air cooled condensing unit of minimum 30TR capacity (actual). The refrigerant compressor shall be Scroll, hermetic / Semi-hermetic type suitable for Refrigerant R-134a / R-407c / R-410a environment friendly HFC refrigerants with drive package, Suction and discharge valves, capacity control system, expansion valve, crank case heater etc. A control panel shall be provided to house all gauges and controls. The panel shall contain all necessary terminal strips to facilitate external wiring. The unit shall be complete with expansion valve, all necessary fittings, accessories, insulated refrigerent piping to and from AHUs, foundation bolts, nuts, washers etc complete in all respect. | 2 | Nos.*
2* | Sheet metal cabinet type air handling units (double skin as per specification) The draw through horizontal AHUs (min. 60 mmWC SP) shall comprise of Dampers, pre filter, fine filters, DX- cooling coil, Fan section with fan & TEFC sq cage induction motor, condensate drain pan, thermostatic controls and other accessories, like ladder along with supporting structure for filter and plenum, etc. to meet the AC load of control room area as per specification. | 2 | Nos.*
3 | Monsoon reheating / winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat etc. | 1 | LOT
4 | PAN type HUMIDIFIER for each AHU room complete with humidistat, geyserstat safety controls, make up water piping from make up tank / nearest source of water, valves fittings etc | 1 | LOT
5 | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), modulating dampers etc. as per specification for each AHU room. | 1 | LOT
G | ITEMS COMMON TO ALL AC PLANTS
1* | GSS zinc coating 275 gms/ m2 ducting complete with hangers/ supports, etc.
(a)* | 18G. | 1850 | SQM*
(b)* | 20G. | 1850 | SQM*
(c)* | 22G. | 3200 | SQM*
(d)* | 24G. | 6200 | SQM*
2* | Fire damper.
(a)* | Fire damper with auto resetting, limit switches, indication lamps etc. | 35 | SQM*
(b)* | Motorized actuator with single phase power supply for the above fire damper. | 40 | NO*
3* | Supply air grill/diffuser with VCD (Extruded Aluminium). | 85 | SQM*
4* | Supply air grill/diffuser with VCD (Extruded Aluminium). | 120 | SQM*
6* | GI Volume control dampers for Duct. | 30 | SQM*
7* | Acoustic insulation of the first 6m of ducting from AHU outlets. | 1 | LOT
8* | Thermal insulation of supply air duct & return air duct with finish as specified. | 13125 | SQM*
9* | Drain piping with and without insulation from various equipment upto nearest available drain point with necessary fittings like tees, reducers, expanders, elbows, flanges, valves with flanges, U trap etc as per specifications.
a* | 50mm | 200 | Rmt*
b* | 40mm | 150 | Rmt*
10* | Make up Water piping without insulation from terminal point near building up to various equipment with necessary fittings like tees, reducers, expanders, elbows, flanges, valves with flanges, U trap etc as per specifications.
a* | 50mm | 200 | Rmt*
b* | 40mm | 150 | Rmt*
11* | HDPE Piping (3 " ) complying to IS 4984, PN 10, PE80 carbon black, UV rating along with valves for transferring softening plant reject and cooling tower blow down to CMB (ETP) | 1100 | mtrs.*
H | AC SYSTEM FOR AUX. BLDG FOR UNIT 1&2
1* | DX type, air cooled condensing unit of minimum 40 TR capacity (actual). The refrigerant compressor shall be Scroll, hermetic / Semi-hermetic type suitable for Refrigerant R-134a / R-407c / R-410a environment friendly HFC refrigerants with drive package, Suction and discharge valves, capacity control system, expansion valve, crank case heater etc. A control panel shall be provided to house all gauges and controls. The panel shall contain all necessary terminal strips to facilitate external wiring. The unit shall be complete with expansion valve, all necessary fittings, accessories, insulated refrigerent piping to and from AHUs, foundation bolts, nuts, washers etc complete in all respect. | 2 | No*
1.1* | Sheet metal cabinet type air handling units (double skin as per specification) The draw through horizontal AHUs (min. 60 mmWC SP) shall comprise of Dampers, pre filter, fine filters, DX- cooling coil, Fan section with fan & TEFC sq cage induction motor, condensate drain pan, thermostatic controls and other accessories, like ladder along with supporting structure for filter and plenum, etc. as per specification. | 2 | No*
1.2* | Monsoon reheating / winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat etc. for above condensing unit | 1 | SET*
1.3* | PAN type HUMIDIFIER for each AHU room complete with humidistat, safety controls, make up water piping from make up tank / nearest source of water, valves fittings etc for above condensing unit | 1 | SET*
1.4* | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), dampers etc. above condensing unit | 1 | SET*
2* | DX type, air cooled condensing unit of minimum 20 TR capacity (actual). The refrigerant compressor shall be Scroll, hermetic / Semi-hermetic type suitable for Refrigerant R-134a / R-407c / R-410a environment friendly HFC refrigerants with drive package, Suction and discharge valves, capacity control system, expansion valve, crank case heater etc. A control panel shall be provided to house all gauges and controls. The panel shall contain all necessary terminal strips to facilitate external wiring. The unit shall be complete with expansion valve, all necessary fittings, accessories, insulated refrigerent piping to and from AHUs, foundation bolts, nuts, washers etc complete in all respect. | 2 | No*
2.1* | Sheet metal cabinet type air handling units (double skin as per specification) The draw through horizontal AHUs (min. 60 mmWC SP) shall comprise of Dampers, pre filter, fine filters, DX- cooling coil, Fan section with fan & TEFC sq cage induction motor, condensate drain pan, thermostatic controls and other accessories, like ladder along with supporting structure for filter and plenum, etc. as per specification. | 2 | No*
2.2* | Monsoon reheating / winter heating kit comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat etc. for above condensing unit | 1 | SET*
2.3* | PAN type HUMIDIFIER for each AHU room complete with humidistat, safety controls, make up water piping from make up tank / nearest source of water, valves fittings etc for above condensing unit | 1 | SET*
2.4* | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), dampers etc. above condensing unit | 1 | SET*
3* | Air Cooled PAC-Unit complete with all accessories as specified The package unit shall be complete with all accessories like duct hetaers, pan humidifier, filters, acoustic insulation of duct for 5m from PU, drain piping with insulation upto nearest drain, required instrumentation etc.
3.1* | 10 TR net capacity | 1 | No*
3.2* | MONSOON REHEATING / WINTER HEATING KIT comprising strip heaters, safety controls, air-stat, contactors, frame work, thermostat & humidistat/ sensors etc. for above mentioned PAC. | 1 | SET*
3.3* | HUMIDIFIER for above mentioned PAC complete with humidistat, safety controls, make up water piping from make up tank /nearest source of water, valves fittings etc. for above mentioned PAC. | 1 | SET*
3.4* | Fresh air fan (axial flow type), complete with motor, inlet cone, air filters (pre and fine), dampers etc. along with support structure and other accessories for above mentioned package AC | 1 | SET*
4 | AIR COOLED SPLIT UNITS consisting of outdoor unit (having compressor condenser coils with fan and motor), indoor unit (having evaporator coil, filter,fan with motor), interconnecting refrigerant piping, drain piping as per site requirement & fittings with insulation, cordless remote, electrical power cord upto the nearest available point along with isolator / MCB, fixing frame for indoor and outdoor unit, Stablizer,etc. with best BEE Rating as per specification.
4.1* | 2.0 TR capacity (non-ductable type, 240 V, 1 phase ) with isolation switch , i.e MCB of suitable rating as specified, voltage stabilizer, cabling, all supporting structure, refrigerent piping to suite actual site condition, drain piping upto nearest drain etc. | 85 | NO*
4.2* | 1.5 TR capacity (non-ductable type, 240 V, 1 phase ) with isolation switch , i.e MCB of suitable rating as specified, voltage stabilizer, cabling, all supporting structure and refrigerent piping to suite actual site condition, drain piping upto nearest drain etc.. | 65 | NO*
5* | AIR COOLED CASSETTE SPLIT UNITS consisting of outdoor unit (having compressor condenser coils with fan and motor), indoor unit (having evaporator coil, filter,fan with motor), interconnecting refrigerant piping as per site requirement & fittings with insulation, cordless remote, electrical power cord upto the nearest available point along with isolator / MCB, fixing frame for indoor and outdoor unit, Stablizer,etc. with best BEE Rating as per specification.
5.1* | 4.0 TR CASSETTE AC capacity (non-ductable type, 240 V, 1 phase ) with isolation switch , i.e MCB of suitable rating as specified, voltage stabilizer, cabling, all supporting structure and refrigerent piping to suite actual site condition, drain piping upto nearest drain etc. | 6 | NO*
5.2* | 2.0 TR CASSETTE AC capacity (non-ductable type, 240 V, 1 phase ) with isolation switch , i.e MCB of suitable rating as specified, voltage stabilizer, cabling, all supporting structure and refrigerent piping to suite actual site condition, drain piping upto nearest drain etc. | 6 | NO*
6* | AIR COOLED DUCTABLE SPLIT AC consisting of outdoor unit (having compressor condenser coils with fan and motor), indoor unit (having evaporator coil, filter, fan with motor), interconnecting refrigerant piping, drain piping as per site requirement & fittings with insulation, cordless remote, electrical power cord upto the nearest available point along with isolator / MCB, fixing frame for indoor and outdoor unit, fresh air arrangement etc.
6.1* | 5.5 TR capacity (ductable type, 415 V, 3 phase with isolation switch). | 5 | NO*
I* | Field instruments like pressure gauge, temperature gauge, pressure switch,pressure sensor, pressure transmitters, differential pressure switch, differential pressure transmitters flow switch, flow transmitter, flow meter, temperature sensors, etc, including necessary control panel form hook up with main DDCMIS as per specifications | 1 | LOT
J* | Local Start/Stop control panel with Local/remote Selector Switch for local/ remote operation of each AHU | 27 | No*
K* | Fibre optic cable. | 50 | Rmt*
L | Total lumpsum price for special tools & tackles for maintenance inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up as per Appendix-A ). | 1 | LOT |  |  | NA | NA
M | Total lumpsum price for commissioning spares inclusive of packing forwarding, transportation up to site, etc. (Bidder shall submit item-wise price break-up as per Appendix-B). | 1 | LOT |  |  | NA | NA
N* | Providing full support during FAT of DDCMIS, preparation of control scheme, and commissining of DDCMIS as per relevent specification. | 21 | Mandays* | NA | NA
O | Any other item not indicated above, but required to make the system complete in all respects as per specification and system requirement. | 1 | LOT
Total |  |  |  |  | 0 |  | 0
NOTES
1 | The bidder shall furnish unit rates for variable item (marked *) for necessary adjustment (plus or minus) variation during detailed engg. stage. The unit rates quoted above shall be considered for adjustment and no separate unit rates shall be quoted. Unit rates shall be valid throughout the contract. Final qty. shall be paid as per actual measurment at site for erection for all the variable items.
2 | Price format shall not be changed by the bidder as the bidder may get disqualified by doing so.
3 | Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price.
4 | The BOQ mentioned above shall be read in conjunction with technical specification requirement. Any item required as per technical specification but not specifically indicated in above BOQ, shall deemed to be inculded in total prices quoted by bidder. No additional price shall be payable against such items.

## APPENDIX-A
APPENDIX-A Special tools & tackles for maintenance
NAME OF PROJECT: |  | 2X 800 MW LARA TPP MAIN PLANT
NAME OF PACKAGE: |  | AC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-508-553-A001
SL NO | DESCRIPTION | UNIT | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | FLAT D WRENCH - 6 MM TO 32 MM (12 Pcs) | SET | 1 |  | 0
2 | BOX WRENCHES - 6 MM TO 22 MM (14 Pcs) | SET | 1 |  | 0
3 | RING SPANNER - 6 MM TO 32 MM (12 Pcs) | SET | 1 |  | 0
4 | ALLEN KEYS - 2 MM TO 10 MM | SET | 1 |  | 0
5 | CRESCENT SCREW SPANNER | NO. | 1 |  | 0
6 | SCREW DRIVER | NO. | 1 |  | 0
7 | OFFSET SCREW DRIVER | NO. | 1 |  | 0
8 | INSULATED PLIER | NO. | 1 |  | 0
9 | TORCH LIGHT FOR 2 CELL | NO. | 1 |  | 0
10 | HAMMER 1 LB | NO. | 1 |  | 0
11 | OIL CAN | NO. | 1 |  | 0
12 | POCKET THERMOMETER - 0 TO 50 DEG. C) | NO. | 1 |  | 0
13 | INSULATION TAPE ROLL | NO. | 1 |  | 0
14 | STEEL FOOT RULE - 12" | NO. | 1 |  | 0
15 | FEELER GAUGE 9 BLADES | NO. | 1 |  | 0
16 | PIPE WRENCH | NO. | 1 |  | 0
17 | FLARE NUT (1/4") | NOS. | 6 |  | 0
18 | FLARING TOOL | NO. | 1 |  | 0
19 | TUBE CUTTER | NO. | 1 |  | 0
20 | GAS CHARGING PIPE | NO. | 1 |  | 0
21 | NITOGEN CHARGING ADAPTER | NO. | 1 |  | 0
22 | FREON PRESSURE GAUGE (2 1/2" DIA DIAL) ) 0 - 300 MM PSI | NO. | 1 |  | 0
23 | FREON PRESSURE GAUGE (2 1/2" DIA DIAL) ) 30 - 150 MM PSI | NO. | 1 |  | 0
24 | PSYCHRO METER | NO. | 1 |  | 0
25 | LOCK WITH KEY FOR TOOL BOX | NO. | 1 |  | 0
26 | RATCHET 1/4" | NO. | 1 |  | 0
27 | MS TOOL BOX | NO. | 1 |  | 0
Total |  |  |  |  | 0
NOTES
1 | Above is the minimum list. Any other Tools and tackles required for AC system w.r.t. Mechanical, Electrical and C&I part shall also be provided by the Bidder as per system / customer requirement without any commercial & Delivery implication to BHEL.
2 | Supply of special tools and tackle including tool box required for operation, maintenance and overhauling of the system is in the scope of the bidder.

## APPENDIX-B
APPENDIX-B Commissioning spares
NAME OF PROJECT: |  | 2X 800 MW LARA TPP MAIN PLANT
NAME OF PACKAGE: |  | AC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-508-553-A001
SL NO | DESCRIPTION | UNIT | Qty | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
1 | Fan Belts ( each type & size) | Set | 1 |  | 0
2 | Pressure Gauge (for each type and range) | No. | 1 |  | 0
3 | Temprature Gauge (for each type and range) | No. | 1 |  | 0
4 | Filter (each size) | Set | 1 |  | 0
5 | Compressor Oil | Ltr./Lot | 1 |  | 0
6 | Refrigerant gas of each type in a non-returnable cylinders | Kg/Lot | 1 |  | 0
Total |  |  |  |  | 0
NOTES
1 | Above is the minimum list. Any other commissioning spare required for AC system w.r.t. Mechanical, Electrical and C&I part shall also be provided by the Bidder as per system / customer requirement without any commercial & Delivery implication to BHEL.

## ANNEXURE-II
ANNEXURE - II LIST OF MANDATORY SPARES
NAME OF PROJECT: |  | 2X 800 MW LARA TPP MAIN PLANT
NAME OF PACKAGE: |  | AC SYSTEM
TECHNICAL SPECIFICATION No: |  | PE-TS-508-553-A001
S. No. | Description | QTY | Total Ex-Works Price (INR)
1.0 | Screw Compressor Chilling Machine for each type/rating/model
1.1 | Oil filter – O ring | 1 Set
1.2 | Refrigerant filter | 1 Set
1.3 | Master solenoid valve | 1 No.
1.4 | Master solenoid valve coil | 1 Set
2.0 | Pumps (for each model)
2.1 | Pump Bearing | 1 Set
2.2 | Pump Motor Bearing | 1 Set
2.3 | Shaft Sleeve | 2 set
2.4 | Screw compressor chilling unit motor | 1 no.
3.0 | Air handling unit (for each model)
3.1 | V-belts for AHU Blower | 2 Sets
3.2 | AHU Blower bearing | 1 Set
3.3 | Blower motor bearing | 1 Set
3.4 | Filters at suction and discharge of all AHUs | 25% of installed population for each type/rating
4.0 | Cooling Tower (for each model)
4.1 | Nozzles for cooling towers | 20 Nos.
4.2 | Float valve assembly | 1 No.
4.3 | Fan Bearings | 1 Set
4.4 | Motor bearings | 1 Set
5 | Electrical Actuators
5.1 | Actuators | 1 No. of each type, model and rating.
6 | Motor | 1 No of each rating
7 | Control & Instrumentation
7.1 | Electronic Transmitters
7.1.1 | Transmitters of all types and model no. (for the measurement of Pressure, differential pressure flow, level, temperature etc.) | 5 Nos. of each type and model
7.2 | Temperature elements
7.2.1 | RTD's* | 5 Nos.
7.2.2 | Thermo well (if applicable) * (With head assembly, terminal block and nipple) | 2 Nos.
7.3 | Process Actuated Switch Devices Includes all types of Pressure, differential pressure, flow, temperature, and differential temperature, level switch Devices. | 2 Nos. of each type and model
7.4 | Relative Humidity Sensors | 1 No.
7.5 | Geyserstat | 1 No.
7.6 | Local Humidity/Temperature indicators | 2 Nos. each
| TOTAL |  | 0
Notes:
a) | Mandatory spares listed in Price Schedule are bare minimum requirement. In case any additional mandatory spares requirement is covered elsewhere in the tender specification apart from specified above, same shall be deemed to have been covered in bidder’s scope of supply.
b) | Wherever "set" is indicated, it shall mean complete replacement for one main equipment of similar size & capacity.
c) | All Spares shall be supplied as per the requirement of the specifications. In case any spare indicated in the specification is “not applicable” for particular equipment, then suitable applicable alternate spare has been offered / shall be supplied by the bidder without any financial implication."
d) | Bidder to write “Quoted / Not Applicable” against all items. Any item which is quoted as “not applicable” by the bidder in the above list and is found to be “applicable” at a later date shall be supplied by the bidder without any commercial and delivery implication.
e) | For quantities indicated in percentage, fractions are to be rounded-off to next higher integer.
f) | Any cell left blank in the unpriced schedule shall be treated as “Quoted” and is included in total price.
g) | Bidder to note that even though there may be some spares which are repetitive at various sl.no mentioned above, bidder to ensure that prices are quoted against each sl.no. In case any cell is left blank in the unpriced schedule shall be treated as "quoted" and included in total price.
h) | List of above mandatory spares shall be finalized during detail engineering. In case of deletion/increase in quantity of any particular item during detail engineering, prices quoted by the bidder against such item shall be reduced/adjusted (wrt unit rate quoted by the bidder) from the overall prices quoted by the bidder.