## CAS
PRICE FORMAT
NAME OF PROJECT: |  | 2 X 800 MW SINGRAULI STAGE-III, STPP |  |  | Vendor Name
NAME OF PACKAGE: |  | COMPRESSED AIR SYSTEM |  |  | Enquiry No- 77/25/6030/SAN Date 25.05.2025
TECHNICAL SPECIFICATION: |  | PE-TS-512-555-A001 |  |  | Supply |  |  | Services |  | Total Scope
S. No. | Description |  | UNIT | QTY | Total Ex-Works Price (INR) | Freight % | Freight in INR | Unit Price (INR) | Total Price (INR) | Total Price Including Freight & excluding GST (INR)
1 | Total lump sum firm price for Supply part, Services part, Mandatory spares, Engineering Charges and AMC comprising of design (i.e. preparation and submission of drawing /documents including “As Built” drawings and O&M manuals), engineering, manufacture, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables, mandatory spares along with spares for erection (as required), start-up spares and commissioning spares (as required), operational spares (as specified), forwarding, proper packing, shipment and delivery at site, unloading, handling, transportation & storage at site, in-site transportation, assembly, erection & commissioning, final painting at site, minor civil work, trial run at site, carrying out Performance guarantee tests at site, training of BHEL & Customer O&M staff at project site and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendments & agreements till placement of order. |  | Lot | 1 | [5 empty] | 0
2 | MAJOR BREAK-UP OF PRICES GIVEN IN 1.0 ABOVE
2.1 | Total lump sum firm price for Supply part comprising of manufacturing, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables alongwith spares for erection as required, start-up and commissioning spares as required, operational spares (as specified), forwarding, proper packing, parts / spares required during warranty period (against defects in design, materials, construction and workmanship) shipment and delivery at site, for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendments & agreements till placement of order. (Break-up as per Annexure-I) |  | Lot | 1 | 0 |  | 0 |  |  | 0
2.2 | Total lumpsum firm prices for Services part comprising of unloading, handling, transportation & storage at site, in-site transportation, assembly, erection & commissioning, connectivity of CAS with DCS, final painting at site, minor civil work, trial run at site and carrying out Performance guarantee tests at site as specified, travelling, lodging, boarding & other charges of E&C personnel's, training of BHEL & Customer O&M staff at project site and handover in flawless condition of the package to the end customer complete with all accessories for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendments & agreements till placement of order. |  | Lot | 1 |  |  |  |  | 0 | 0
2.3 | Total lumpsum firm price for Mandatory spares comprising of manufacture, fabrication, assembly, inspection / testing (as applicable) at vendor's & sub-vendor’s works, painting, forwarding, proper packing, shipment, delivery at site & handover of MS to BHEL/End Customer, for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendments & agreements till placement of order. (Price break up of mandatory spares is to be furnished as per Annexure- II) |  | Lot | 1 | 0 |  | 0 |  |  | 0
2.4* | Total lumpsum firm price for Engineering Charges comprising of design (i.e Preparation & submission of drawings/documents including " AS-BUILT" drawings and O&M Manuals and engineering as per tender technical specification above, amendments & agreements till placement of order. |  | Lot | 1 |  |  |  |  | 0 | 0
2.5 | Total lumpsum firm price for AMC (Annual Maintenance Contract), for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendments & agreements till placement of order; Refer Annexure-B of Technical specification for detailed scope in AMC. (Break-up as per Annexure-III) |  | Lot | 1 |  |  |  | 0 | 0 | 0
Note: 1) * Engineering Charges (quoted against S. no. 2.4) shall not be more than 5% of supply price (excluding freight and GST) quoted at S. No. 2.1, failing which break-up shall be adjusted accordingly from supply price for ordering. 2) Please note that the complete engineering of the package is in the scope of bidder as per the tender requirement. However, for the payment purpose bidder to note that 50% of price as per S. no. 2.4 shall be made against basic engineering (i.e. Preparation, submission & approval of basic drawing/ documents as indicated in S.No. 11 of index (Documentation requirement) mentioned in tender specification and the remaining payment shall be made for the balance engineering part on pro-rata basis. 3) For Guaranteed Power Consumption for Compressed Air System package, refer Annexure-IV. Other performance guarantees parameters for the package shall be as specified in the Technical Specification, under the chapter, ''Performance Guarantees for Compressed Air System,'' including the specific categories under which each guarantee parameter falls.

## CAS-ANNEX.-I
ANNEXURE-I: BREAK-UP OF SUPPLY PRICES
NAME OF PROJECT: |  | 2 X 800 MW SINGRAULI STAGE-III, STPP
NAME OF PACKAGE: |  | COMPRESSED AIR SYSTEM
TECHNICAL SPECIFICATION: |  | PE-TS-512-555-A001
S. No. | DESCRIPTION |  | UNIT | QTY | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR)
BREAK-UP OF SUPPLY PRICES GIVEN IN 2.1 OF MAIN SHEET
2.1 | Total lump sum firm price for Supply part comprising of manufacturing, fabrication, assembly, inspection / testing at vendor's & sub-vendor’s works, painting, maintenance tools & tackles (as applicable), fill of lubricants & consumables alongwith spares for erection (as required), startup spares and commissioning spares (as required), operational spares (as specified), parts/spares required during warranty period (against defects in design, materials, construction and workmanship), forwarding, proper packing, shipment and delivery at site, for the total scope defined as per BHEL NIT & tender technical specification as specified above, amendment & agreements till placement of order. |  | Lot | 1
Break up prices for items covered in clause 2.1 above
2.1.1 | Instrument air Compressors Oil Free (Screw / Centrifugal type) each of minimum 55 NM3/Min capacity @ 8.0 kg/cm2 (min.) discharge pressure with suction filter with silencer, inter cooler and after cooler with moisture separators, automatic drain traps, instruments, control system, cable lugs, glands and other accessories (as required / as specified) but excluding electric motor drive. |  | Nos. | 4 |  | 0
2.1.2 | Air Drying Plants HOC type (Twin Tower / Rotary Drum) of minimum 55 NM3/min. capacity for Air Compressor with all instruments, control panels, including Electronic dew point meter and other accessories as specified. |  | Nos. | 4 |  | 0
2.1.3 | Service air Compressors Oil Free (Screw / Centrifugal type) each of minimum 55 NM3/Min capacity @ 8.0 kg/cm2 (min.) discharge pressure with suction filter with silencer, inter cooler and after cooler with moisture separators, automatic drain traps, instruments, control system, cable lugs, glands and other accessories (as required / as specified) but excluding electric motor drive. |  | Nos. | 3 |  | 0
2.1.4 | Air Receivers required for Compressed Air System of minimum 10 Cu.M capacity each with instruments, relief valve, isolation valve, drain connection with automatic trap stations (zero purge air loss type) and other accessories as specified. |  | Nos. | 12 |  | 0
2.1.5 | Air Receivers required for Compressed Air System of minimum 02 Cu.M capacity each with instruments, relief valve, isolation valve, drain connection with automatic trap stations (zero purge air loss type) and other accessories as specified. |  | No. | 1 |  | 0
2.1.6 | Inter connecting cooling water, drain piping and compressed air piping as specified including fittings and valves etc. for complete Compressed air system. |  | Lot | 1 |  | 0
2.1.7 | Instruments as specified. |  | Lot | 1 |  | 0
2.1.8 | Interface module(s), JB's for the overall control & monitoring of compressed air system through DDCMIS including common Sequencing Panel. |  | Lot | 1 |  | 0
2.1.9 | E-Learning Package: e-learning packages for each equipment & for complete compressed air system. |  | Lot | 1 |  | 0
2.1.10 | Operational spares for Compressed air system.
a | Lube oil (Qty. for 1 Lot in Ltr. shall be as per oil tank capacity for One Compressor) |  | Lot | 14 |  | 0
b | Lube oil filters including gearcase filter with seals |  | Lot | 21 |  | 0
c | Air filters (intake filter, gearcase filter, control panel filter) with gaskets including silencer |  | Lot | 21 |  | 0
d | Service kit including seals, washers and rings for inter cooler & after cooler |  | Lot | 14 |  | 0
e | Air intake valve kit, throttle valve kit/ Inlet guide vane kit |  | Lot | 7 |  | 0
f | Blow off valve kit |  | Lot | 7 |  | 0
g | Drain valve kit |  | Lot | 7 |  | 0
h | Solenoid valve/ control valve kit |  | Lot | 7 |  | 0
i | Check valve kit |  | Lot | 7 |  | 0
j | Drive coupling (main motor & oil pump motor) kit |  | Lot | 7 |  | 0
k | Air piping kit, lubrication piping kit, oil cooler kit, water piping kit inside compressor skid (O-ring, gasket, pipe coupling elements) |  | Lot | 7 |  | 0
l | Grease/ lubrication (main motor, oil pump motor, other components) |  | Lot | 21 |  | 0
m | Shaft seals |  | Lot | 7 |  | 0
n | Yearly maintenance kit for air compressor (excluding above) as per OEM recommendation |  | Lot | 7 |  | 0
o | Filters for Air Dryers (as applicable) |  | Lot | 8 |  | 0
p | Yearly maintenance kit for air dryer (excluding above) as per OEM recommendation |  | Lot | 4 |  | 0
q | Service kit for ADT of Air Receivers |  | Lot | 13 |  | 0
Total | [5 empty] | 0
Note: 1.) For Lot breakup supply of items under S. No. 2.1.10 above, refer "ANNEXURE-E: LIST OF OPERATIONAL SPARES REQUIRED DURING STORAGE & PREVENTIVE MAINTENANCE PERIOD". in the tech. spec. 2) Wherever "Lot" is mentioned under S.No. 2.1.10, one Lot of the spares of that item shall be for complete replacement of that particular item for one equipment.

## CAS-ANNEX.-II
ANNEXURE-II: LIST OF MANDATORY SPARES
NAME OF PROJECT: |  | 2 X 800 MW SINGRAULI STAGE-III, STPP
NAME OF PACKAGE: |  | COMPRESSED AIR SYSTEM
TECHNICAL SPECIFICATION: |  | PE-TS-512-555-A001
S. No. | DESCRIPTION | QTY | Total Ex-Works Price (INR)
1.00.00 | COMPRESSED AIR SYSTEM
1.01.00 | Oil free Screw Air Compressor (as applicable)
(i) | Complete HP Stage with HP element | 1 No.
(ii) | Complete LP stage with LP element | 1 No.
(iii) | Void | -
(iv) | LP stage Pinion | 1 No.
(v) | HP stage Pinion | 1 No.
(vi) | Air Oil Filter Kit | 4 Nos.
(vii) | After cooler Safety Valve (if applicable) | 1 No.
(viii) | Inter Cooler Safety Valve (if applicable) | 1 No.
(ix) | Oil Pump kit | 2 Nos.
(x) | After cooler drain valve kit (if applicable) | 1 No.
(xi) | Inter cooler drain valve kit (if applicable) | 1 No.
(xii) | Air receiver drain/moisture trap | 1 No.
(xiii) | ‘O’ Rings for oil cooler | 8 Nos.
(xiv) | Moisture separators for Aftercooler (if applicable) | 2 Nos.
(xv) | Moisture separators for Intercooler (if applicable) | 2 Nos.
1.02.00 | Centrifugal Compressor (as applicable)
1.02.01 | Pinion Shaft Journal Bearing Assembly | 2 Sets
1.02.02 | Thrust Bearing Assembly | 2 Sets
1.02.03 | Shaft Seals for Air-Oil (All stages) | 2 Sets
1.02.04 | Gasket / O rings | 3 Sets each type/size
1.02.05 | Air Filter Elements | 4 Sets each type/size
1.02.06 | Lub Oil System
1.02.06.1 | Main oil pump complete | 1 No.
1.02.06.2 | Aux. oil pump complete | 1 No.
1.02.06.3 | Complete coupling for Main & Aux. oil pump, spacer | 1 No.
1.02.06.4 | Cartridge filter elements with gaskets and seals | 4 Sets
1.02.06.5 | Motor Bearings | 2 Sets
1.02.07 | Drain / Moisture Trap | 2 Set of each type/size.
1.02.08 | Oil Cooler Gaskets & Seals | 2 sets
1.03.00 | AIR DRYING PLANT FOR IA SYSTEM (Twin tower Type) (As applicable)
1 | Pre filter element (Ceramic candle or as applicable) | 2 sets
2 | After filter element (Ceramic candle or as applicable) | 2 sets
3 | Heater element (if applicable) | 1 sets
4 | Blower bearing (if applicable) | 1 sets
5 | Blower motor bearing (if applicable) | 2 sets
6 | Valves & Valve Actuators (pneumatic/hydraulic) | 2 sets
7 | Heater coil for temperature stabilization (for HOC type) (as applicable) | 2 sets
8 | Desiccant for Air Dryer: one complete fill for both towers of one dryer | 1 Lot
1.04.00 | Valves (within the compressor house having actuators) along with actuator | 2 Nos. of each type / rating / size
1.05.00 | Void | -
1.06.00 | MEASURING INSTRUMENTS
1 | Electronic Transmitters
(i) | Transmitters of all types, ranges and model no. (for the measurement of Pressure, differential pressure flow, level, etc.) | 2 Nos. of each type and model
2 | Temperature elements
(i) | RTD’s* of each type and length | 2 Nos. of each type and length
(ii) | Thermocouples of each type like K-type, R-type, metal etc. and length * | 2 Nos. of each type and length
(iii) | Thermowell | 2 Nos. of each type and length
(iv) | Temperature transmitters (if applicable) | 2 Nos of each type
3 | Process Actuated Switch Devices Includes all types of Pressure, differential pressure, flow, temperature, differential temperature, level switch Devices | 2 Nos. of each type and model
4 | Dew Point meters | 1 No.
1.07.00 | MICROPROCESSOR BASED/PLC BASED CONTROL/ELECTRONIC BASED CONTRAL PANEL (IF APPLICABLE)
1 | Fully programmed controller of electronic modules of each type (as applicable) | 1 No.
2 | Power supply module (if applicable) | 1 No.
1.08.00 | Rotary drum type Air drying plant for Instrument Air system (As applicable)
1 | Drive assembly consisting of motor, gear boxes, drive shaft & coupling | 1 set
2 | Desiccant for Air Dryer: one complete fill of one dryer | 1 Lot
Total |  |  | 0
NOTE:
1 | Wherever set is mentioned, one set of the spares of that item shall be for complete replacement of that particular item for one equipment.
2 | Any fraction of a item shall mean the next higher integer.
3 | Wherever quantity has been specified as percentage (%), the quantity of mandatory spares to be provided by contractor shall be the specified percentage (%) of the total population of the plant. In case the quantity so calculated happens to be fraction, the same shall be rounded off to next higher whole number.
4 | Wherever the quantities have been indicated for each type, size, thickness, material, radius, range etc., these shall cover all the items supplied and installed and the breakup for these shall be furnished in the bid.
5 | In case spares indicated in the list are not applicable to the particular design offered by the bidder, the bidder should offer spares applicable to offered design with quantities generally in line with the approach followed in the above list.

## CAS-ANNEX.-III
ANNEXURE-III: BREAK-UP OF AMC
NAME OF PROJECT: |  | 2 X 800 MW SINGRAULI STAGE-III, STPP
NAME OF PACKAGE: |  | COMPRESSED AIR SYSTEM
TECHNICAL SPECIFICATION: |  | PE-TS-512-555-A001
S. No. | DESCRIPTION |  | UNIT | QTY | Unit Price (INR) | Total Price (INR)
BREAK-UP OF AMC PRICES GIVEN IN 2.5 OF MAIN SHEET
2.5 | Total lumpsum firm price for AMC (Annual Maintenance Contract) of Compressed Air System. |  | Lot | 1
Break up prices for items covered in clause 2.5 above
2.5.1 | Maintenance during storage period
(a) | Total lumpsum firm prices for visits (should include travel expenses to/ fro site, intermediary stay) for maintenance during storage period for the total scope defined as per BHEL NIT & tender technical specification, amendment & agreements till placement of order. |  | Nos. | 2 |  | 0
(b) | Total lump sum firm prices for Maintenance during storage period (in days) for the total scope defined as per BHEL NIT & tender technical specification, amendment & agreements till placement of order. |  | days | 6 |  | 0
2.5.2 | Preventive maintenance
(a) | Total lump sum firm prices for visits (should include travel expenses to/ fro site, intermediary stay) for Preventive maintenance period for the total scope defined as per BHEL NIT & tender technical specification, amendment & agreements till placement of order. |  | Nos. | 14 |  | 0
(b) | Total lump sum firm prices for Preventive maintenance period (in days) for the total scope defined as per BHEL NIT & tender technical specification, amendment & agreements till placement of order. |  | days | 42 |  | 0
Total | [5 empty] | 0
Note: 1.) No. of days at site defined at S.N. 2.5.1 (b) & 2.5.2 (b) above shall be calculated on the basis of presence at site (travel time is excluded). 2.) No. of visits and days for above storage & preventive maintenance may vary depending on site requirement. Any variation in no. of visits & no. of days shall be exercised based on unit rate arrived from S.N. 2.5.1(a & b) & 2.5.2 (a & b) as above respectively.

## CAS-ANNEX.-IV
ANNEXURE-IV: Guaranteed Power Consumption
NAME OF PROJECT: |  | 2 X 800 MW SINGRAULI STAGE-III, STPP
NAME OF PACKAGE: |  | COMPRESSED AIR SYSTEM
TECHNICAL SPECIFICATION: |  | PE-TS-512-555-A001
S.No. (1) | Description of Equipments (2) | Nos. of Equipments (3) |  | Total Guaranteed Power Consumption for Each Equipment at Motor Input Terminals & control Panel (4) | Duty Factor (5) | Total (KW) (6) = (3A)*(4)*(5)
|  | Working | Standby
|  | A | B
1 | Instrument air compressors (Oil free Screw / Centrifugal type) of capacity 55 NM3/Min. @ discharge pressure of 8.0 Kg/cm2(g). | 3 | 1 | To be filled by bidder | 0.66 | To be filled by bidder
2 | Service air compressors (Oil free Screw / Centrifugal type) of capacity 55 NM3/Min. @ discharge pressure of 8.0 Kg/cm2(g). | 2 | 1 | To be filled by bidder | 0.33 | To be filled by bidder
3 | Air Drying plant (Heaters) (if applicable) | 3 | 1 | To be filled by bidder | 0.5 | To be filled by bidder
4 | Air Drying plant (Blowers) (if applicable) | 3 | 1 | To be filled by bidder | 1 | To be filled by bidder
TOTAL
Note :
1 | Estimated Power Consumption Figure for the compressed air system (For Working Drives Only) considered is 1250 KW.
2 | Bidders Guaranteed power consumption at motor input terminals (Not Shaft Power) considering motor efficiency of 95.0% (at full load) including power for control panel as furnished in guranteed schedule shall be demonstrated by the successful bidder during performance testing at works/site.
3 | The price quoted by the bidder shall be loaded @ US $ 4350 (US Dollar Four Thousand Three Hundred Fifty only) for every additional kW increase in consumption from the base figure indicated at Note no. 1.0 above.
4 | In case the successful bidder fails to establish / prove the guaranteed values of power consumption ((base figure of auxiliary power consumption or the GPC quoted by bidder, whichever is higher) on actual performance testing at the manufacturing works / site, penalty @ US $ 4350 (US Dollar Four Thousand Three Hundred Fifty only) per kW increase in power consumption figure shall be levied.
5 | If the contract currency is other than US dollars, then the liquidated damages shall be in equivalent amount in contract currency based on Bill selling exchange rate of State Bank of India prevailing on 05.03.2024.