## Sheet1
Job | Tender enquiry of Cooling towers as per technical specification No.PE-TS-410-165-N001 (Rev.0) for 1 X 800 MW Kothagudam project
NIT no. | PE / PG / KG1 / E-4750 / 2014 dated 27.03.2015.
Sl # | Reference clause of tender document | Existing provision | Bidder's query | BHEL's clarifications
1 | e-PCT/TS/K/02/2014-15, VII-D:10, clause no.7.03.02 | Minimum weight of fill shall be 100 kg/sqm. | There seems to be some error in this value as none of the fill supplier's manufactures fill media with such a high value. Kindly clarify. | Shall be replied later.
2 | e-PCT/TS/K/02/2014-15, VII-D:24, clause no.9.02.04 d) | The minimum size of raker column section shall be 1200 mm diameter or more as per design. | The raker column size shall be based on the design of the bidder. Kindly confirm. | Shall be replied later.
3 | e-PCT/TS/K/02/2014-15, VII-D:34, clause no.9.09.00 i) | Painting of concrete surfaces | Kindly confirm if this clause holds good for painting of concrete surfaces. | Confirmed
4 | e-PCT/TS/K/02/2014-15, VII-D:44, sl.no.2 | Basin holding capacity: 6 minutes of design CT capacity | The basin depth, levels shall be as mentioned in Annexure -1 of datasheet A. Kindly confirm.
5 | e-PCT/TS/K/02/2014-15, VII-D:44, sl.no.3 | Drift loss : 0.002% | Generally, the drift loss is specified as 0.005% in most of the tenders whereas here it is indicated as 0.002%. Due to this we have to use high efficiency drift eliminators, manufactured outside India, which would ultimately increase the overall price. Moreover, we feel that this additional value of 0.003% doesn't have any significance unless the drift loss test is carried out. Therefore, kindly confirm if drift loss of 0.002% is to be followed strictly and if yes, also confirm if drift loss test is to be conducted to establish the same. | Shall be replied later.
6 | e-PCT/TS/K/02/2014-15, VII-D:45, sl.no. 3 | Design pressure for hot water distribution: 6.2 kg/sq.cm | This is too high as there is very minimal pressure required. Moreover,the availability of the PVC lateral pipes is with 4 or 6 kg/sq.cm pressure. Hence we request you to revise the same to 6 kg/sq.cm. | Design pressure for hot water distribution shall be 5.5 kg/cm2 (g). Technical amendment shall be issued shortly in this regard.
7 | Vol II B, datasheet A, sl.no.2.13 | Minimum basin diameter ; 140 M | The basin diameter shall be based on the design of the bidder. Kindly confirm. | Follow the specification requirements.
8 | -- | Mandatory spares | Kindly provide us the list for mechanical and electrical items as the specs contains only the C & I items. | Mandatory spares list is already enclosed in the technical specification. Refer Annexure-4 to datasheet-A of section-D, Vol-IIB.
9 | Vol: II B, Section - C, standard electrical scope between BHEL and vendor | SL.no.3: Power, control cables and screened control cables for one end equipment shall be supplied & erected by BHEL. But as per sl.no.11, it is indicated as "further wires, any other material required for lighting system shall also be considered by vendor in their scope." | Kindly confirm the following: 1. Kindly confirm which is referred to as "lighting system".? Under sl.no.11. 2. Sl.no.3 & 11 is contradictory as further cabling required for lighting system will be under BHEL's scope. | Please find below point wise reply : 1. Lighting system includes scope of lighting as per Section : XV (Technical Specification for Natural Draft Cooling Tower - Electrical Works) enclosed with technical specification. 2. Sl. no. 3 mentions Cables. However Sl. No. 11 mentions wires used for connetions for lighting fixtures, receptacles, juction boxes etc. required for lighting system which shall be in vendor's scope as per Scope sheet enclosed with technical specification.