## BOQ
Part of Corrigendum 06 with ref: BHE/PW/PUR/TLRPT-RESERVOIR/2651/Corg-06
Revised Excel Sheet For Calculation Purpose Only
For the convenience of bidders, BHEL has issued this excel sheet with all requisite formulae (break up of price). However this excel sheet shall not form part of contract.
Job: Construction of Earthen Raw Water Reservoir, Raw Water Pump House, Pipeline Excavation & Backfilling, Pipe line laying & encasing, etc. at 2x660MW NTPC Talcher TPS, Angul Dist. Odisha
Total Price to be quoted by Bidder on E-Portal
ST. NO | DESCRIPTION OF ITEM | UNIT | TOTAL | RATE | AMOUNT | Weightage(%)
EARTHERN RAW WATER RESERVOIR, Pipeline Excavation & backfilling, Pipe Encasing, Valve Pit.
1 | Earth work in stripping of top soil for minimum depth of 300 mm below ground level so as to exclude all debris, grass, vegetation, bushes, trees having girth upto 300mm including roots and organic materials etc including dressing to specified levels & grades and compacting the graded/stripped surface by manual/mechanical means, disposal of stripped materials within a lead upto 1km etc all complete as per specification, drawing and as directed by the engineer-in-charge. | Sq.m | 52800 | 0 | 0 | 0.92829
2 | Earth work in excavation upto any depth below ground level in all types of soil including moorum, ash which can be excavated by any means inside reservoir/ash pond area and for foundation of reservoir/ash pond embankment and cut-off trench including site clearance, setting out, levelling, dewatering (wherever required), shoring & strutting (wherever required), dressing the sides & bottom, levelling to grade, all lifts, ramming/compacting the excavated bottom, stacking/disposal of surplus excavated materials within a lead upto 1km, spreading/levelling of disposed materials etc all complete as per specification, drawing and as directed by the engineer-in-charge. | CUM | 94193 | 0 | 0 | 8.7318
3 | Earth work in excavation upto any depth below ground level in soft rock (rock without any recovery of exacavated materials in the form of hard stone/boulder) including weathered rock which can be excavated by means of crow bar, pick axe, pneumatic rock breaker attachment with excavator machine etc (but does not require chiselling or blasting) inside reservoir area and for foundation of reservoir embankment and cut-off trench including setting out, levelling, dewatering (wherever required), dressing the sides & bottom, all lifts, ramming/compacting the excavated bottom, stacking/disposal of surplus excavated materials within a lead upto 1km, spreading/levelling of disposed materials etc all complete as per specification, drawing and as directed by the engineer-in-charge. | CUM | 6784 | 0 | 0 | 1.0951
4 | Earth work in embankment filling/bed filling upto any level below/above ground level in layers not exceeding 300 mm compacted thickness with selected approved soil from compulsorily excavated soil available within a lead upto 1km and compacted so as to achieve atleast 98% of maximum dry density (Standard Proctor Test) as per IS:2720, Part-7 including setting out, re-excavation of stacked earth, sorting, handling, spreading, breaking clods, watering, ramming/compaction by manual/mechanical means, dressing, finishing to required lines, grades and slopes, tesing, dewatering if required, all lifts etc all complete as per specification, drawing and as directed by the engineer-in-charge. | CUM | 93751 | 0 | 0 | 7.9417
5 | Extra over ST No. 1, 2, 3 and 4 for carriage of soil/excavated materials for every 1 km or part thereof beyond an initial lead of 1km. | CUM | 12145 | 0 | 0 | 0.097057
8 | Supplying, stacking and laying sand of approved quality as sand blanket/cushion over base/bed and on slopes of embankment including screening, washing (wherever required), watering, compaction, dressing, necessary trimming if any including all leads and lifts etc all complete as per specification and as directed by the engineer-in-charge. | CUM | 7256 | 0 | 0 | 5.1376
9 | Supplying, stacking and laying sand filter of approved quality inside the body/ slope of embankment including screening, washing (wherever required), watering, compaction, dressing, necessary trimming if any including all leads and lifts etc all complete as per specification and as directed by the engineer-in-charge. | CUM | 10340 | 0 | 0 | 9.9159
A10 | Supplying, stacking and laying 300mm thick graded gravel filter of approved quality below/above rock-toe in slopes, on the embankment including screening, washing (wherever required), watering, compaction, dressing, necessary trimming if any including all leads and lifts etc all complete as per specification and as directed by the engineer-in-charge. | CUM | 470 | 0 | 0 | 1.0415
11 | Providing and placing approved quality of 1mm thick heavy duty high density polyethylene liner (HDPE) film manufactured from polyethylene resin in the base/bed of reservoir as well as on side slopes of embankment to prevent seepage including joining with approved method including testing, fixing at the edges in plain cement concrete by providing 400mm wide and 300mm thick plain cement concrete 1:2:4 on the top of embankment (the cost of plain cement concrete 1:2:4 shall be excluded and shall be payable separately) as shown in the drawing etc all complete as per specification and as directed by the engineer-in-charge. Minimum width of HDPE liner shall be 6m. | SQM | 40915 | 0 | 0 | 5.3624
A12 | Providing and laying 1000mmx1000mm size and 75mm thick cast-in-situ concrete panels of grade M-20 (with graded stone chips 12.5mm nominal size) over non-woven geotextile laid over HDPE liner at the bed/slope of reservoir etc all complete as per specification and as directed by the engineer-in-charge. The rate shall be inclusive of cement sand mortar as well. (Synthetic Polyester triangular fibre of length 12mm, effective diameter 10-40 microns and specific gravity of 1.34 to 1.40 shall be mixed in Plain Cement Concrete of grade by using 125gms of synthetic Polyester triangular fibre for 50 Kg cement used as per directions of Engineer.) (Cement shall be provided by BHEL free of cost) | SQM | 40915 | 0 | 0 | 19.7819
13 | Supplying, stacking and laying hand placed rock toe at the down stream side of embankment with approved quality of rock fragments including materials etc all complete as per specification, drawing and as directed by the engineer-in-charge. | CUM | 3047 | 0 | 0 | 9.4406
14 | Supplying, stacking and laying 300mm thick rip rap on the slopes of embankment with approved quality of rock fragments including materials etc all complete as per drawing, specification and as directed by the engineer-in-charge. | CUM | 1790 | 0 | 0 | 3.2315
15 | Providing and placing turfing with approved quality of grass on the outer slopes of embankment including materials, transportation, watering etc all complete as per drawing, specification and as directed by the engineer-in-charge. | SQM | 2983 | 0 | 0 | 0.16925
16 | Providing and laying of 900 mm diameter R.C.C hume pipes of class NP3 conforming to IS:458 with collars, jointing the pipes with 1cement : 1sand mortar and testing of joints etc all complete as per specification and as directed by the engineer-in-charge. (Cement for mortar shall be provided by BHEL free of cost) | RM | 150 | 0 | 0 | 0.66493
18 | Providing, mixing & laying 25 mm thick compacted Semi dense bituminous concrete (SDBC) in a single course composed of suitable small size aggregate premixed with bituminous binder using medium setting grade bitumen on a prepared base including mixing, applying, rolling etc all complete. | SQM | 4432 | 0 | 0 | 0.86421
19 | Providing, mixing & laying of dense bituminous macadam course of specified thickness using bitumen of grade 60/70 conforming to IS 73, aggregates and binder material including hot mixing, hot laying, rolling etc all complete for the following.
a | 75mm compacted thickness | SQM | 4155 | 0 | 0 | 1.8362
A20 | Providing & Laying Wet mix macadam (WMM) granular base using close graded material conforming to specification, mixing in a mechanical mix plant at OMC, carriage of mixed material to work site, for all leads & lifts, spreading in uniform layers of specified thickness on prepared surface and compacting with vibratory power roller to achieve the desired density, complete as per specifications and directions of Engineer-in-Charge. | CUM | 1250 | 0 | 0 | 2.4313
23 | Providing and laying compacted 50mm thick moorum over WBM base course including watering and compaction with road roller to make required line, slope and levels etc all complete as per drawing, specification and as directed by the engineer-in-charge. | CUM | 250 | 0 | 0 | 0.29409
24 | Providing and applying liquid seal coat comprising of an application of a layer of bituminous binder using medium setting grade bitumen at the rate of 9.8kg/10sqm followed by a cover of stone chips at the rate of 0.09 cum/10sqm including rolling etc all complete. | SQM | 4432 | 0 | 0 | 0.3046
25 | Providing & applying tack coat of low viscosity liquid bitumen of grade 80/100 confirming to IS 73, 217 or 454 as applicable @10 kg/ 10 sqm for untreated WBM surface including scraping, cleaning with compressed air etc all complete. | SQM | 8864 | 0 | 0 | 0.50294
Earth work In excavation for foundations, trenches, drains, pipelines, sumps, substructures etc, backfilling and disposal including necessary labour, materials, equipment, loading, transportation, unloading, dewatering etc as per specification, drawing and as directed by engineer- in-charge for the following.
28 | Earth work in excavation up to any depth in all types of soil including moorum, ash which can be excavated by any means including setting out, levelling, dewatering (but excluding special type of dewatering viz. well point method), shoring & strutting (wherever required), dressing the sides & bottom, all lifts, ramming/compacting the excavated bottom, stacking, disposal of surplus excavated materials within a lead upto 1km, spreading/levelling of disposed materials etc all complete. | CUM | 6223.5 | 0 | 0 | 0.57693
A28 | Earth work in excavation upto any depth below ground level in soft rock (rock without any recovery of exacavated materials in the form of hard stone/boulder) including weathered rock which can be excavated by means of crow bar, pick axe, pneumatic rock breaker attachment with excavator machine etc (but does not require chiselling or blasting) inside reservoir area and for foundation of reservoir embankment and cut-off trench including setting out, levelling, dewatering (wherever required), dressing the sides & bottom, all lifts, ramming/compacting the excavated bottom, stacking/disposal of surplus excavated materials within a lead upto 1km, spreading/levelling of disposed materials etc all complete as per specification, drawing and as directed by the engineer-in-charge. | CUM | 925.5 | 0 | 0 | 0.14937
29 | Back filling upto any depth below ground level around foundations, plinths, trenches, drains, pipe lines, sumps, substructures etc to proper grade and level in layers not exceeding 250 mm thickness with selected materials from compulsorily excavated soil available within a lead upto 1km and compacted so as to acheive at least 90% maximum dry density as per IS-2720 (Part-VII) including re-excavation of stacked earth, watering, ramming/compaction by manual/mechanical means, dressing etc all complete. | CUM | 2372 | 0 | 0 | 0.18008
30 | Extra over ST No. 28, A28 and 29 for carriage of excavated earth for every 1 km or part thereof beyond an initial lead of 1km. | CUM | 4777 | 0 | 0 | 0.038175
Providing and placing concrete work including cost of labour, materials and equipment for handling, transportation, batching, mixing, placing, vibrating and curing, (excluding cost of centering, shuttering and reinforcement) with mechanised equipments like batching plant, transit mixer, concrete pump etc. complete as per drawing, specifications and as per direction of engineer in charge for the following. (RMC shall be provided by BHEL free of cost)
31 | Concrete of grade M10 (1 part cement, 3 part sand, 6 parts of 40 mm graded aggregate by volume) as lean concrete/ levelling course/encasement, mud mat under and around foundations/floors, drains, pits, sumps etc at all levels complete. | CUM | 495 | 0 | 0 | 0.52335
32 | Concrete of grade M15 (1 part cement, 2 part sand, 4 parts of 40 mm graded aggregate by volume) as lean concrete, levelling course, mud mat under and around foundations/floors at any depth etc at all levels complete. | CUM | 38 | 0 | 0 | 0.040177
33 | Concrete of grade 1:2:4 (1 part cement, 2 part sand, 4 parts of 20mm graded aggregate by volume) as levelling course, pipe encasement and anchoring of HDPE liner etc at all levels complete. | CUM | 133 | 0 | 0 | 0.14062
34 | Providing and laying design mix cement concrete of grade M20 conforming to IS:456 & IS 10262-2009 for reinforced concrete works with coarse sand and graded hard stone aggregate of 20mm nominal size in foundations/ substructure, superstructures, drains, under floors, sumps, culverts etc at all levels including use of plasticizer/ superplasticizer conforming to IS:9103 (latest) to achieve required slump in concrete all complete. | CUM | 450 | 0 | 0 | 0.47577
35 | Providing and laying design mix cement concrete conforming to IS:456 & IS 10262-2009 for reinforced concrete works with coarse sand and graded hard stone aggregate of 20mm nominal size in foundations/ substructure, superstructures, drains, under floors, sumps, culverts etc at all levels including use of plasticizer/ superplasticizer conforming to IS:9103 (latest) to achieve required slump in concrete all complete.
a | M 25 Grade | CUM | 35.5 | 0 | 0 | 0.037534
b | M 30 Grade | CUM | 1135 | 0 | 0 | 1.2
A35 | Providing and laying Design Mix cement concrete of grade conforming to IS:456 & IS 10262-2009 for reinforced concrete works with coarse sand and graded hard stone aggregate of 20mm nominal size in superstructure at all level above finished floor level, any shape, position or thickness etc complete including use of plasticizer/ superplasticizer conforming to IS:9103 (latest) to achieve required slump in concrete all complete as per specification & drawing for the following.
a | M 25 Grade | CUM | 239 | 0 | 0 | 0.25269
b | M 30 Grade | CUM | 250 | 0 | 0 | 0.26432
B35 | Providing and laying Design Mix cement concrete as per IS:456, IS 3370 & IS 10262-2009 for reinforced concrete works using graded aggregate for Concrete in water retaining/conveying structures including addition of suitable plastisizer cum waterproofing cement additives confirming to IS 9103 latest to achieve a slump more than 125 mm in concrete as per manufacturers recommendation and conforming to limits of permeability as per IS 2545 and specification with 20 mm nominal size graded aggregate for following grades. Watertightness is to be ensured including structural grouting if required.
b | M 30 Grade | CUM | 375 | 0 | 0 | 0.43214
36 | Breaking/dismantling existing concrete work at any level including reinforced concrete, removing the rubbish materials and disposal of the same within a lead of 1 km including transportation, loading, unloading etc all complete. | CUM | 5 | 0 | 0 | 0.0061415
Providing, fixing and removing formwork at any elevation for all structures as per specification including labour, materials, scaffolding, centering, providing pockets etc. complete as per drawing, specification and as per directions of engineer in charge for the following.
37 | Fairface form work with good quality water proof ply wood of required thickness and smooth surface at any level/elevation for foundations, footings, base of columns, walls, columns, pilasters, beams, drains, sumps mass concrete, trenches etc for enexposed/exposed concrete works all complete. | SQM | 7774.5 | 0 | 0 | 4.2373
A37 | Providing, fixing and removing formwork in block-outs/pockets and openings (below 0.1 sqm plan area) at all elevations including cutting, formation of all shapes and all other operations required for making the required shape and size all complete as per specification, drawing and instruction of engineer in charge.
b | Pockets of depths more than 150mm and upto 300 mm depth | Each | 4 | 0 | 0 | 0.0012946
c | Pockets of depths more than 300mm and upto 600 mm depth | Each | 36 | 0 | 0 | 0.020858
d | Pockets of depths more than 600mm and upto 1000 mm depth | Each | 2 | 0 | 0 | 0.0018205
REINFORCEMENTS
38 | Providing, straightening, cutting, bending, placing in position at all levels, binding in position of mild steel reinforcements conforming to grade-1 of IS:432, Part-1 in concrete including cost of reinforcement, binding wire, labour etc all complete as per specification, drawing and as directed by the engineer-in-charge. | MT | 5 | 0 | 0 | 0.30363
39 | Transportation, straightening, cutting, bending, placing in position at all levels, binding in position of steel reinforcements of TMT steel of grade Fe-500D or 500EQR confirming to IS:1786 including cost of binding wire, labour etc all complete per specification, drawing and as directed by engineer-in-charge. (TMT shall be provided by BHEL free of cost) | MT | 270 | 0 | 0 | 2.1694
40 | Providing and fixing suitable under drainage system consisting of PVC pressure release valve of minimum dia 100mm in water retaining structure including 160mm dia housing pipe of minimum length 3.75m with perforation as per IS4558, nylon jali, perforated end plug, collar, graded filter, excavation, fixing in concrete slab/wall etc. all complete. | EACH | 492 | 0 | 0 | 4.0152
41 | Providing and laying of approved quality of non woven geotextile membrane including unrolling, cutting all complete as per specification and as directed by Engineer-in-charge. | SQM | 40915 | 0 | 0 | 2.485
Roof Treatment works: Roof treatment works including all labour, material (unless otherwise specified in BOQ/contract specification), equipment, transportation, handling, curing, sampling, testing etc at all level as per specification, drawings and as directed by engineer - in - charge. (Material used for rooftreatment shall be CFC & HCFC free. The contractor shall submit documentary proof to GRIHA consultant in support of same).
A41 | Providing and applying two coats of bitumen grade 85/25 as per IS 702 (@1.7kg/sqm)with 1% antistripping compound conforming to IS 6241 in foundation, wall, column etc on concrete surfaces exposed to soil / ash including surface preparation etc. all complete. | SQM | 106 | 0 | 0 | 0.012791
JOINTS AND FILLERS: Joints & fillers including all labour, material, equipment, transportation, handling etc at all level as per specification, drawings and as directed by engineer - in - charge.
601 | Supplying & installation of bitumen impregnated fibre board confirming to IS 1838 as joint filler at joints in concrete including nailing, coating of both faces with coal tar pitch/bitumin etc. all complete.
c | 25 mm wide joints | SQM | 40 | 0 | 0 | 0.033437
610 | Providing and fixing PVC water stops in joints conforming to IS 12200 & IS 15058 all complete for the following: (Bulb or Kicker type)
d | 230 mm wide and 6 mm thick | RM | 708 | 0 | 0 | 0.11542
700 | MS EMBEDMENTS: Embedments including all labour, material (unless otherwise specified in BOQ/contract specification), equipment, transportation, handling etc. at all level as per specification, drawings and as directed by engineer - in - charge.
701 | Supply, fabricating and fixing of mild steel embedments, inserts, pipe sleeves, angle pieces, rungs of various diameters, plates of dimensions as required etc. including welding, bolting, cutting, drilling, scaffolding, setting etc. all complete. | MT | 6 | 0 | 0 | 0.49004
BRICK WORK MASONRY INCLUDING SUPPLY OF MATERIAL, COST OF LABOUR ETC. COMPLETE AS PER SPECIFICATION
42 | Providing brick work in cement sand mortar 1:6 (1 part cement: 6 part coarse sand) in walls, chambers etc at all depths, places and positions below plinth including crest drains, slope drains, toe drains, connecting drains etc on embankment at all levels including raking out joints, curing, scaffolding etc all complete excluding plastering and painting using bricks of class designation 7.5 of nominal dimensions as per specification. | CUM | 200 | 0 | 0 | 0.8837
43 | Breaking existing brick work at any level including plastering, cutting of reinforcement, removing the rubbish within a lead of 1 km including transportation, loading, unloading etc all complete as directed by the Engineer-in-charge. | CUM | 10 | 0 | 0 | 0.013945
CEMENT MORTAR PLASTER INCLUDING ALL MATERIALS, SCAFFOLDING, CURING ETC COMPLETE AS PER SPECIFICATION
44 | Providing 12mm thick plaster in walls, drains/culverts with a paste of neat cement @ 1kg/sqm and rubbed smooth with trowel etc. all complete. | SQM | 1190 | 0 | 0 | 0.1398
45 | Handling at site stores / storage yard, transporting to site, inspection, preassembly, erection, alignment, welding, NDT, fixing of supports, water flushing, hydro testing, surface finish, supply & application of primer & finish paints/ Anti corrosive / Wrapping and coating as applicable including labelling & flow direction on the piping, pre-commissioning for piping and its associated items, etc. as directed by Engineer-in-Charge. | MT | 52 | 0 | 0 | 0.98633
| Total Amount (Rs.) |  |  |  | 0 | 100