REPLACEMENT OF EXISTING CONTROL PANELS WITH FULLY WIRED NEW CONTROL PANELS WITH COMPLETE ELECTRICS OF LATEST TECHNOLOGY (HARDWARE AND SOFTWARE) FOR ABB MAKE INDUCTION MELTING FURNACE ITM 5/2500KW, 600 Hz.

1	OBJECTIVE:

The objective is

1. Technological up gradation of the existing furnace by retrofitting the furnace with latest technologies with single track/dual track / twin power system.

2. “Replace the existing Static Frequency Converter Panel and all the auxiliary control panels that with new standard panels that consists of complete electrics of latest technology (like Teflon / silicon insulated wires / cables) of reputed make.”

3. Introduction of operational, diagnostic software etc., for optimal utilization of the furnace.

4. Electrical interfacing.

5. Installation, commissioning and prove out.

PRE-QUALIFICATION REQUIREMENTS:

All the following conditions are to be satisfied by the tenderer. Documentary proof is to be enclosed with techno-commercial bid satisfying all these conditions. In case the tenderer fails to enclose the same his offer will be rejected.

- The party must be a reputed medium frequency Furnace manufacturer / rebuilder or retrofitter of minimum capacity 1000 KW with at least 5 years experience in the last 7 years in this field. List of the customers along with respective contracting officer’s addresses (including phone no. and e-mail Id) for whom the furnaces were manufactured / rebuilt / modernized shall be enclosed to the offer.

- Average Annual financial turnover during the last 3 years, ending 31s March 2007 should be at least 50% of estimated cost.

3.         Purchase Order copy / commissioning report from the customers where the project is implemented.

2      BRIEF DESCRIPTION OF THE EXISTING FURNACE:

### It is a Medium frequency Induction melting furnace of capacity 2500 KW, 600Hz supplied by M/s ABB, SWEDEN and was commissioned in the year 1989 in 04 foundry shop.

| Specifications |  | Supplier’s confirmation | Deviations if any /Remarks |
| --- | --- | --- | --- |
| 3 SCOPE OF MATERIAL SUPPLY |  |  |  |
| 3.1 | The power source and control system: The power source and electronic control system of latest type and version with suitable hardware and software (operational & diagnostic) to the existing furnace. * Technical details should be provided with offer |  |  |
| 3.2 | The auxiliary control panel with latest control systems and devices of reputed make consisting of all the switchgear, pushbuttons, indication lamps, buzzer, and indication meters (volt, current, frequency etc), alarm indication etc shall be provided. Make and Type of systems that offer should be furnished with offer. |  |  |
| 3.3 | Control panels (details): Panels of reputed make equivalent to RITTAL with control system, power control devices like converter and inverter rectifiers, chokes, capacitors etc. Transformers like control transformers, pulse transformers, potential transformers, current transformers,etc., all the indication lamps, meters and push buttons etc. The panel shall be with min IP41 degree of protection. The panel shall be free standing floor mounting type and Suitable hooks shall be provided for lifting the panels Proper Fluroscent lighting for cubicle and 2 numbers of 5A, 3 pin plug socket with switch for 230v test lamp shall be provided. Suitable power terminals shall be provided for incoming power cables. Dimensional details shall be provided with offer. |  |  |
| 3.4 | Cables suitable to furnace environment: All the interfacing cables between the control panels and the furnace crucibles. MAKE: LAPP / equivalent to LAPP. Make of cable that offer should be mentioned along with offer. |  |  |
| 3.5 | Control power supply: 24 Volt DC regulated power supply of suitable capacity for Control system and PLC. – MAKE: Siemens /Nemic-lambda /Astec /Bull power systems/ ABB/equivalent. |  |  |
| 3.6 | Control devices and switchgear: All the power control devices and switchgear items must be of reputed make. Make and type that offer should be provided along with offer. |  |  |
| 3.7 | Fault Indicator System: - Low Pressure Indication & Tripping for Furnace Coil Cooling Water (Internal & External Cooling System, both separate indication & tripping.) - Low Pressure Indication & Tripping for Panel Cooling Water (Internal & External Cooling System, both separate indication & tripping.) - High Temperature Indication & Tripping for Furnace Coil (Internal & External Cooling System, both separate indication & tripping.) - High Temperature Indication & Tripping for Panel (Internal & External Cooling System, both separate indication & tripping.) - Flow Rate indicator / gauges for the Panel Cooling Water system. - Audible System like motor operated siren shall be incorporated to the operational CONTROL PANEL for any fault in the panel & furnace. - Ground Leak Detector System shall be incorporated with Digital Display Mode at following two locations. - Power Panel - Operating Control Panel |  |  |
| 3.8 | Any other item not mentioned above to keep the furnace in working Condition and to ensure completeness of electrics. |  |  |
| 4 SCOPE OF WORK |  |  |  |
| ELECTRICAL AND ELECTRONICS |  |  |  |
| 4.1 | Dismantling and removal of existing control panels and interconnected cables. |  |  |
| 4.2 | Modifications to existing furnace transformers, busbar connections, heatexchanger, cooling system, capacitor systems etc. |  |  |
| 4.3 | Installation of new control panels |  |  |
| 4.4 | Development of modified logic and interface drawings. |  |  |
| 4.5 | Modifications to the existing electrical wiring. |  |  |
| 4.6 | Interfacing of control panels, hydraulic system and furnace with suitable electrical modifications. |  |  |
| 4.7 | Modifications to existing heat exchanger system suitable to new control panels. |  |  |
| 4.8 | Modifications / replacement of existing capacitor bank and related electrical wiring. The material if required for completeness of the project shall be in supplier’s scope. |  |  |
| INSTALLAITON AND COMMISSIONING |  |  |  |
| 4.9 | Checking all the functions of the furnace. |  |  |
| 4.10 | Checking all the safety interlocks. |  |  |
| 4.11 | Installation, commissioning and job proveout. |  |  |
| 5 DOCUMENTATION |  |  |  |
| 5.1 | The supplier shall supply 3 sets of the following documents for before commencement of work at BHEL factory : |  |  |
|  | i. Operation manual |  |  |
|  | ii. Installation/commissioning manuals |  |  |
|  | iii. Maintenance &diagnostic manual |  |  |
|  | iv. Electrical drawings and complete bill of material |  |  |
|  | ix. The modified control logic (hardware and software) logic |  |  |
| 5.2 | The disgnostic and operational software for optimum utilization of the furnace. |  |  |
| 5.3 | Three sets of AS-built drawings of the general arrangement, electrical wiring and cabling shall be supplied within two weeks after completion of work. |  |  |
| 6 GENERAL POINTS |  |  |  |
| 6.1 | Supplier should arrange for training on operation,- free of cost for six personnel (Operator- 2No, Maintenance personnel- 4No, at Manufacturer’s training facility. |  |  |
| 6.2 | Supplier to quote separately for the material and for installation and commissioning charges. |  |  |
| 6.3 | Supplier to send his offers for commercial and technical bids in a separate sealed cover and for price bid in a separate sealed cover. |  |  |
| 6.4 | The supplier is required to study the furnace, the scope of supply and certify the completeness of the scope in order to execute the work. In case of any discrepancies in the scope of supply the supplier is required to highlight the same to BHEL before acceptance of the order. |  |  |
| 6.5 | Planning and laying of all necessary cables, busbars are in suppliers’ scope of work. |  |  |
| 6.6 | Before commencing manufacture of the panels, electrical and general arrangement drawings should be submitted to BHEL for approval. |  |  |
| 6.7 | Before dispatch of material the supplier should arrange for inspection/working of the system to BHEL personnel at his works. BHEL shall be intimated ten days in advance before calling for inspection. Material shall be dispatched only after written clearance from BHEL |  |  |
| 6.8 | Modified logic shall be in line with the existing logic and interface drawings. |  |  |
| 6.9 | Indication lamps wherever required to be provided. |  |  |
| 6.10 | Earthing: All non-current carrying metallic parts shall be earthed. All doors and movable parts shall be connected to the earth bus with flexible copper connections. |  |  |
| 6.11 | All the bought out items should be furnished with test chart results. |  |  |
| 6.12 | The vendor shall furnish Complete Bill Of Material (BOM) with makes and necessary catalogues. |  |  |
| 6.13 | Itemized breakup of spares used as per recommendation of the vendor for 2 years of trouble free operation in three shifts continuous running basis should be offered by the vendor (unit price of each item of spare should be offered) |  |  |
| 6.14 | Test and guarantee: The supplied equipment should be guaranteed for a period of 12 months from the date of commissioning/18 months from the from the date of supply whichever is later for any fault in material/workmanship. |  |  |
| 6.15 | The Furnace will be available for modifications for a duration of 3 to 4 weeks. |  |  |
| 6.16 | Following documents shall be furnished by the supplier along with his offer : - Point-wise clarifications to these specifications - Catalogs of Control system /power source - Estimated time of machine outage for modifications with bar chart. - Clear scope of supply and scope of work - Supply of any other material not mentioned above but required for trouble free functioning of the project and to ensure completeness in every respect shall be in vendor’ - Deviations, if any from these specifications In the absence of the above information, the offer will not be considered. |  |  |