## Sheet1
|  | BHARAT HEAVY ELECTRICAL LIMITED |  |  | Enquiry No. :
|  | UNIT'S ADDRESS |  |  | Due Date :
|  | UNIT'S PHONE NOS. |  |  | Supplier Qtn. No.:
|  | CONTACT PERSON'S NAME/DESIGN./PHONE NO. /E-MAIL (FROM PURCHASE DEPTT.) |  |  | Date :
SPECIFICATION CUM COMPLIANCE CERTIFICATION FOR
MOTOR OPERATED LOOP CONTROL VALVES FOR PUMP TEST PLANT
NOTE:-
1. Vendor must submit complete information against clause no. 11.0.0 The offer meeting this clause would only be processed.
2. The "Offered" Column and where applicable, the "Deviations" & "Remarks" Column of this format shall be filled in by the Vendor and submitted along with the offer. Inadequate / incomplete, ambiguous, or unsustainable information against any of the clauses of the specifications/requirements shall be treated as non-compliance.
3. The offer and all documents enclosed with offer should be in English language only.
ADDRESS OF THE SUPPLIER : |  |  |  | ADDRESS OF THE INDIAN AGENTS :
TELEPHONE NOS.: |  |  |  | TELEPHONE NOS.:
FAX NOS.: |  |  |  | FAX NOS.:
E-MAIL ADDRESS : |  |  |  | E-MAIL ADDRESS :
DESIGN, MANUFACTURE, TESTING, PACKING, DISPATCH OF MOTOR OPERATED LOOP CONTROL VALVES FOR PUMPS TEST PLANT
SNO |  | DESCRIPTION FOR BHEL REQUIREMENT |  | SPECIFIED / TO BE CONFIRMED BY | OFFERED | DEVIATIONS | REMARKS
1.0.0 |  | PURPOSE
1.1.0 |  | Purpose: (Operations/Jobs involved) |  | Required for Water / Air flow control of hot water test loop during testing of pumps
2.0.0 |  | SPECIFICATION:
2.1.0 |  | FLOW DATA:
2.1.0 |  | CONDITION :
2.1.1 |  | Fluid |  | River / Ground water
2.1.2 |  | Flow Rate |  | As per Annexure-C
2.1.3 |  | Inlet Pressure |  | As per Annexure-C
2.1.4 |  | Outlet Pressure |  | As per Annexure-C
2.1.5 |  | Fluid Temperature |  | As per Annexure-C
2.1.6 |  | Shut off Differential pressure |  | As per Annexure-C
2.2.0 |  | TECHNICAL SPECIFICATION
2.2.1.0 |  | VALVE ASSEMBLY
2.2.1 |  | Body Size |  | Supplise to specify
2.2.2 |  | Body Material |  | Carbon Steel
2.2.3 |  | Internal; Material |  | Stainless steel
2.2.4 |  | End connections |  | Flanged ends, ANSI 300, RF, Size as per Annexure-C
2.2.5 |  | Characteristic |  | Linear
2.2.6 |  | Gland Type |  | Bolted gland
2.2.7 |  | Configuration |  | Straight-through (i.e Inlet and outlet in-line)
2.2.8 |  | Mounting |  | Universal
2.2.9 |  | Leakage Class |  | Class - V (ANSI)
2.2.10 |  | Noise Level |  | Less than 90 dB
2.3.0 |  | ACTUATOR ASSEMBLY
2.3.1 |  | Type |  | Motor operated electrical actuator with external starter unit. (Starter unit under BHEL Scope).
2.3.2 |  | Make |  | AUMA
2.3.3 |  | Duty |  | Regulating / Modulating duty by remote inching operation
2.3.4 |  | Power Supply |  | 415 V, 3 Ph., 50Hz.
2.3.5 |  | Actuator Mounting |  | Minimum 4 nos. mounting bolts to be used for actuator mounting.
2.3.6 |  | Limit Switches |  | 2 set each for CLOSE / OPEN end positions, One set each for CLOSE / OPEN over tourque protection.
2.3.7 |  | Protection |  | Themoswitch
2.3.8 |  | Accessories |  | Hand wheel for local manual operation, Remote position indicator with matching potentiometer.
2.4.0
2.4.1
2.4.2
2.4.3
2.4.4
2.4.5
2.4.6
2.4.7
2.4.8
2.4.9
2.5.0 |  | Quantity |  | As per Annexure-C
2.6.0 |  | ENVIRONMENTAL PERFORMANCE OFVALVE :
The Valve should conform to following factors related to environment :
|  | 1. Noise level during operation of valve should not cross more than 90 dB throught its flow range. |  | Required
3.0.0 |  | ACCESSORIES:
|  | Supplier shall offer matching Counter Flanges for Valve Inlet and Outlet connections including sealing gaskets, Studs and Nuts seperately. |  | Vendor
4.0.0 |  | SPARES:
4.1.0 |  | Itemised breakup of mechanical & electrical spares used for the valve in sufficient quantity as per recommendation of Vendor for 2 years of trouble free operation. (Unit Price of each item of spare should be offered) |  | Vendor (For Indentor to identify spares to be procured along with the valve)
4.2.0 |  | All types of spares for valve should be available for atleast ten years after supply of the valve. If valve is likely to become obsolete in this period, the vendor should inform BHEL sufficiently in advance and provide drawings of parts / details of spares & suppliers to enable BHEL to procure these in advance, if required |  | Vendor to confirm
4.3.0 |  | Recommended set of spares are to be offered with details. |  | Vendor
4.4.0 |  | Vendor to confirm that complete list of spares for valve along with specification / type / model and name & address of the spare supplier shall be furnished along with documentation to be supplied with the valve. |  | Vendor
5.0.0 |  | DOCUMENTATION : |  | Vendor
5.1.0 |  | Five sets of following documents (Hard Copies) in English Language should be supplied along with the valve.
5.2.0 |  | Detailed valve sizing calculations, Technical details of valve, cross sectional drawing, Dimensional drawing, actuator details test procedure to be submitted along with the offer.
5.3.0 |  | Test & Guarantee Certificates to be supplied along with the valve.
5.4.0 |  | Operating & Maintanance Manuals of Valve.
5.5.0 |  | Electrical & Electronics circuits should be given.
5.6.0 |  | One additional set of all the above documentation on CD ROM, wherever possible.
6.0.0 |  | ERECTION & COMMISSIONING |  | BHEL SCOPE
7.0.0 |  | VALVE ACCEPTANCE: (Inspection and Testing) |  | Should be accepted & confirmed by Vendor
7.1.0 |  | Tests / Inspection to be carried out at supplier’s works on the Valve before dispatch : |  | Witnessed by BHEL
7.1.1 |  | Body Hydrostatic test |  | Witnessed by BHEL
7.1.2 |  | Seat Leakage test |  | Witnessed by BHEL
7.1.3 |  | Valve calibration with Actuator. |  | Witnessed by BHEL
8.0.0 |  | PACKING:
8.1.0 |  | Sea worthy & rigid packing for all items of complete valve, all Accessories and other supplied items to avoid any damage/loss in transit. When valve is despatched in containers, all small loose items shall be suitably packed in boxes |  | Vendor
9.0.0 |  | GUARANTEE :
9.1.0 |  | 12 months from the date of commissioning of the valve. |  | Vendor
10.0.0 |  | GENERAL :
10.1.0 |  | Operating Fluid is highly prone for scale formation. Vendor to take necessary care while selecting control element. |  | vendor to confirm
10.1.1 |  | Vendor to submit , along with offer, reference list of customers where similar machines have been supplied mentioning broad specifications of the supplied machine |  | vendor
11.0.0 |  | REFERENCE LIST / QUALIFYING CONDITIONS :
11.1.0 |  | Only those vendors, who have supplied and commissioned at least 2 such valves of same or higher capacity for similar applications in the past 2 years (On the Date of Opening of tender) and such valve is presently working satisfactorily for more than TWO year after commissioning (On the Date of Opening of tender), should quote. However, if such valve(s) has/had been supplied to BHEL, then such valve should be presently working satisfactorily for more than six months after its commissioning and acceptance (On the Date of Opening of tender) in BHEL, should quote. The following information should be submitted by the vendor about the companies where similar valves have been supplied. This is required from all the vendors for qualification of their offer. |  | Vendor
12.0.0 |  | 8. BHEL reserves the right to verify the information provided by vendor. In case the information provided by vendor is found to be false/incorrect, the offer shall be rejected.
ANNEXURE - C
DETAILS OF MOTOR OPERATED LOOP VALVES
Line Size | Flow | Inlet. Pressure | Outlet Pressure | Max. Shut off Diff. Pr. | Fluid Temp. | Application | Qty.
| m3/hr | kg/cm2 | kg/cm2 | kg/cm2 | 0C
20” | 2500 | 10 | 9 | 40 | 60 | Fine Control | 1
20” | 2000 | 20 | 19 | 40 | 200 | Fine Control | 2
16” | 1700 | 10 | 9 | 40 | 60 | Fine Control | 1
12” | 850 | 10 | 9 | 40 | 60 | Fine Control | 1
4” | 100 | 5 | 1 | 40 | 60 | ON-OFF | 2
3” | 20 | 20 | 19 | 40 | 200 | ON-OFF | 4
3” | 120 | 100 | 20 | 200 | 200 | Fine Control | 1
1” | 10 | 20 | 10 | 40 | 200 | Fine Control | 4