## clamping
| BHARAT HEAVY ELECTRICALS LIMITED |  | Due Date:
| Heavy Power Equipment Plant,Ramachandrapuram |  | Supplier Qtn.No.:
| Hyderabad-502032, INDIA |  | Date:
Phones :
Fax Nos.:
E-mail :
TENDER DOCUMENTS TO BE FILLED BY THE SUPPLIER FOR SUPPLY , ERECTION AND COMMISSIOING OF THE EXHAUST FAN FOR VENTILATION SYSTEM INCLUDING ID FAN, ELECTRICAL MOTOR AND DUCTING.
ADDRESS OF THE SUPPLIER :
TELEPHONE NOS.:
FAX NOS:
E-MAIL:
Technical Specifications
SL.NO. | Description for BHEL requirement Specifications | Qty | Offered | Deviations
1 | This specifications for the ventilation system covers design,manufacture,testing at manufacturer's works, packing and dispatch to our works along with all accessories and fittings,Erection & Commissioning of ID fan for ventilation system in the 250 MW test Bed.
2 | a) TESTBED PIT DIMENSIONS : Total length of the pit is 58 Mtrs. with two different breadths as mentioned below. Length x Breadth : (26 M x 15 M ) + ( 32 M x 12.5 M ) Depth : - 5.5 Mtr. ( Below the ground ) b) AIR INLET TO THE PIT : Atmospheric air shall flow into the pit through two staircases. c) EQUIPMENTS ERECTED IN THE PIT : (1) CO2 Gas Tank,(2) Lubrication Oil System,(3) Seal Oil System and (4) Jacking Oil System
3 | SCOPE OF SUPPLY :
a | ID FAN : General design features of the ID fan is as given below: Fan Type : Centrifugal Volume Flow : 43500 CUM/Hour No. of air changes per hour : 20 Gas handled : Clean ambient air Drive arrangement : Belt drive Static pressure : 35 mm WC Efficiency : 74% Fan speed : 504 RPM | 2 Nos.
Sound Level : 85 dba@1 mt distance from the fan casing Codes and Standards : Testing of Fan as per IS 4894 standards.
b | ELECTRICAL MOTOR : Design features of the motor are as given below : Rating : 15 HP Speed : 1500 RPM Voltage : 440 V,50 Hz.,3 Phase,Squirrel Cage,Induction Motor Make : Kirloskar / GEC/NGEF/Jyoti Starter / Control Pannel : Shall be provided by vendor | 1 No.
c | DUCTING : Supply,Erection & Testing of exhaust duct with the following specifications. The job includes fabrication of 90 Deg. Elbows / bends required for both the fans. Type of material : MS fabricated pipe duct,flange connected Dia. of the pipe : 1.12 Meters Thickness of the pipe : 2.5 mm Length of the duct required : 30 Meters ( for both the fans ) Suction :Single point at - 1.0 mt. height in the 1.0 mt. thick RCC wall. Delivery : at 4 Mtr. height in the existing bay. | 36 M
d | FABRICATION OF ELBOWS / BENDS : The contractor has to fabricate the elbows / bends from the above pipe. Only fabrication rate shall be quoted for elbow/bend. | 8 Nos.
e | PAINTING : Supply and painting of the system. One coat of red oxide paint and two coats of enamel light grey of shade 631 as per IS 5. | LS
4 | GUARANTEE : The equipment shall guarantee against manufacturing defects for 12 months from the date of commissioining.
5 | GENERAL : a) Vendor shall quote unit rate for MS pipe b) Vendor shall quote fabrication rate for each elbow / bend c) Necessary civil foundations shall be provided by BHEL d) Necessary power & control cabling shall Laid & Terminated by BHEL e) Starter / control panel supply & erection is in the scope of vendor f) Supply & erection of base frame is in the scope of vendor g) BHEL will arrange raw material required for duct supports. Execution shall be carried out by the vendor. h) Welding electrodes,equipments & tools are in the contractor's scope. i) The tentative sketch for ducting layout alongwith fan & motor is enclosed.
i) The tentative sketch for ducting layout alongwith fan & motor is enclosed. However the final layout drawing shall be submitted by the vendor.
6 | INSPECTION : Item No. (3.a) and (3.b) will be inspected at supplier's works before despatch.