## Sheet2
ANNEXURE NO. - 1A-C
ITEM | DESIGNATION | DESCRIPTION | TYPE MAKE | QTY | REMARK
1 | ACB | AIR CKT. BREAKER(ACB), 1000A, 415V AC, BREAKING CAPACITY - 50 K.A. 3 POLE, 240 VAC MOTORCONTROL, DRAWOUT WITH CRADLE SH. REL EA1-240V AC, CT'S 800A6NO+6NC AUX. CONTACTS, 24 WAY SIC SERVICE POS. MICROSWITCH, EQUIPPED WITH REL.SR21 SHUTTERASSY.,DOOR INTERLOCKING RACKING INTERLOCK KIT TYPE CN-CS 1000C | CN-CS1000C G E POWER MAKE OR EQUIVALENT OF SIEMENS,ABB,C&S OR L& T MAKE | 1 | NOT APPLICABLE IN PDB 5 ST
2 | CT1 TO CT3 | C T 800/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3
3 | F1 TO F6 | HRC FUSE LINKS 2 A | NS2 GE
4 |  | FUSE BASE 20 A | NSH GE
5 | MCB | MINIATURE CIRCUIT BREAKER 10 A 2 POLE 240 V AC COMBINED RELEASE | SIEMENS OR HAGER
6 | PB | PUSH BUTTON UNSHROUD ACTUATOR GREEN RED | 3SB1200-OAE01 SIEMENS
7 |  | CONTACT BLOCK 1 NO + 1 NC FOR PUSH BUTTON | 3SB1400-OA SIEMENS
8 | V | DIGITAL VOLTMETER, TYPE 3 1/2 DIGITS,OPERATING VOLT. 415V ACRESOLUTION 10V RANGE, AUX. SUPPLY 240V AC, INSCRIPTIONS RY, YB, RB ENGRAVED ON INDICATING PLATE,MODEL VSS 96D IS :1248 | VSS 96 D A.E. MAKE
9 | ACB | DIGITAL AMMETER, TYPE 4 1/2 DIGITS, OPERATING CURRENT 5A, DULY CALIBRATED FOR CTR 800/5,RESOLUTION 10A RANGE, AUX. SUPPLY 240V AC, MODEL ASS 96D IS :1248 | ASS 96 D A.E. MAKE |  | RATINGS AS PER FEEDER DETAILS
10 | R,Y, B | LED PILOT LIGHT, RED,YELLOW , BLUE VOLTAGE SUITABLE FOR 42-240V AC AND 42-220V DC.TYPE 3SB14 01-2WZ3 | 3 SB 1401-2W23 SIEMENS
11 | SFU | SWITCH DISCONNECTOR FUSE UNIT TPN, 400A, OPEN EXECUTION, (INTERIOR) WITH DIN TYPE FUSE LINKS WITH DOOR INTERLOCKING, WITH 1 NO + 1NC AUX CONTACTS TYPE FN 400 IS : 13942-3 | FN 400 L&T OR SIEMENS,ABB,C&S,GE MAKES |  | RATING MENTIONED IS FOR 400A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER FEEDER
12 |  | HRC FUSE LINKS AMP RATING AS PER FEEDER
13 | CT1 TO CT3 | C T 100/5 A 5 VA WITH MOUNTING BRACKETS | A.E. | 3 | RATING MENTIONED IS FOR 100A FEEDER ONLY . FOR OTHER FEEDERS RATING AS PER FEEDER
SHEET 11 OF 11