## Sheet1
| Bharat Heavy Electricals Limited |  | Date:
| Heavy Power Equipment Plant, Ramachandrapuram |  | Due Date:
| Hyderabad-502 032, INDIA |  | Supplier Qtn No.
| Phones: 23182208 |  | Date :
Fax Nos:040-23021910 & 23021954
E-mail: surya@bhelhyd.co.in
TENDER DOCUMENTS TO BE FILLD BY THE SUPPLIER FOR SUPPLY OF 4 ZONE PROGRAMMABLE TEMPERATURE PID CONTROLLERS QUANTITY: 4 Nos.
ADDRESS OF THE SUPPLIER:
TELEPHONE NOS: |  | FAX NOS: | E-MAIL ADDRESS
Sl No | Specification | Specified | Vendor offered
1 | Purpose: 4 ZONE PROGRAMMABLE TEMPERATURE PID CONTROLLERS are required to monitor the temperature in the furnaces and during Local stress releiving.
1.1 | No.Of Zones/Channels | Minimum Four programmable independently.
1.2 | Display | Digital
1.3 | Power supply | AC 100 to 240 Volts , 45 to 65 Hz both automatically adjusted
1.4 | Mounting | Flush Panel mounting (Vertical)
1.5 | Front panel | Water and dust proof to IEC529-IP65
1.6 | Dimensions | Easily carriable
1.7 | Ambient Temperature | 0 to 50°C
1.8 | Panel Key-lock | With actual key : Panel keys assigning selection should be provided.
1.9 | Audio visual alarm | Fault in thermocouples and program
2 | INPUT
2.1 | Number of patterns/programmes | Minimum Four
2.2 | No of segments | Minimum Eight consists of ramp/soak/cool .
2.3 | Measurement intervals | 2.5 second max
2.4 | Measurement range (user selectable) | DC Volts : 20 mV to 20 V, Thermocouple : R, S, J, K & RTD : Pt 100
2.5 | Thermo-emf in case of thermocouples | As per standard IEC 584/ASTM 230-96
2.6 | Linear scaling | DC Volts, TC and RTD to be scaleable
3 | DISPLAY FUNCTION
3.1 | Display language | English
3.2 | Program monitor | LED yellowish green and front panel user friendly membrane key pad
3.3 | Set point/parameter display | 3 digits+4digits,7segment LEDs red
3.4 | Display contents | Process variable(PV) Set point/Parameters
3.5 | Process variable display | 4 digits, 7 segments LEDs red
3.6 | Other display information | Ramp, soaking and cooling cycle
3.7 | Look back facility | Programmed profile
3.8 | Scanner/Logger | Continuously scans and logs the temperature at predefined intervals.
3.9 | Power up mode | Retain the position in the running program at the time of power failure and resumes the program automatically on availability of power.
4 | CONTROL SPECIFICATIONS
4.1 | Uni start | 4 zone control of a single Furnace/system to ensure temperature uniformity, 4 zones are independently wired.
4.2 | Time proportional PID | Voltage pulse out put for driving external SSR
4.3 | Voltage pulse out put | ON voltage approx. 12 V DC
OFF voltage 0.1 V DC or less
Load resistance 1 kilo ohm
4.4 | Out put action selectable | Direct / reverse selectable
4.5 | Cycle time | 1 to 100 seconds, voltage pulse out put
4.6 | Other functions | Auto tuning, Multi PID, Key lock, Input Burn out detection, Measuring input and control out put circuits isolated from each other.
5 | ACCURACY
5.1 | Measurement and display accuracy
| · DC Voltage range | · ± (0.3 % reading + 2 digits)
| · Thermocouple (R/S) | · ± (0.3% of reading + 1°C)
| · Thermocouple J/K | · ±( 0.3% of reading + 0.7°C)
| · RTD Pt-100 | · ± (0.3% of reading + 0.3°C)
or better
5.2 | Reference junction compensation | Internal (automatic)
5.3 | RJC accuracy | ± 1°C max
6 | Spares: Spares required for 2 years normal operation shall be quoted with item wise break up as optional. | Vendor.
7 | Operating & Maintenance, installation and communication manuals of the Multi channel programmable temperature controller. | Three sets to be supplied with the each instrument.
8 | Catalogues with details shall be submitted along with offer for the offered model. | Vendor
9 | Preinspection of the equipment at suppliers works before despatch by BHEL engineers. During pre-inspection vendor shall explain all features af the equipment as per specifications. | Specify
10 | Customers reference list shall be furnished along with offer for similar item. | Specify
11 | Commssioning and prove out of the items at BHEL works is suppliers responsibility. | Specify
12 | The itmes shall be guaranteed for the satisfactory performance for a period of 18months from the date of commissioning. | Specify
13 | Two bid system shall be followed. | Vendor
14 | The quotation shall contain point to point detail explanation for every point mentioned in this specification clearly. In absence of this offer will not be evaluated technically. | Vendor
15 | Delivery Period. | Specify