Encl to MPR No ERN/6330/

Specification No.- PDB 1 ST -S-01

The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

- The Power distribution board shall be comprising of one incomer panel and the outgoing module feeder panels  4 nos approx. with hinged type doors at front  for each feeder module. The incomer panel approx.  dimension shall be W X H X D = 800 X2390X1300 mm and each  outgoings panel approx. dims shall be W X H X D = 800 X2390X560 mm .

- The incomer ACB shall be draw-out type and outgoings shall be fixed type.

- The details of various feeders rating with their components are as per

annexure  : 1ST-F.

- The details /specifications of equipments/components for various feeders are as per annexure  : 1A-C.

- The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

- The incomer ACB panel for PDB1ST shall be on right end .

- The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons , front of ACB etc shall be on the front door of the respective feeder modules.

- The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

- The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

- The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

- The thickness of the M.S sheet  C/R  for  mounting of components  shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

- The hinged doors of the panels shall be properly earthed using flexible wires .

- The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

- The structure of the panels shall be chemically pretreated before painting.

- The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

- The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

- The vendor shall get approved the mechanical drgs. , electrical drg., component details  of the panels before mfg. the same within one month of placement of the P.O. .

- Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint manuals of the various equipments/ components used shall be required with delivery.

- The T.C. and G.C. for one year after installation /commissioning shall be required.

.

Specification No.- PDB 2ST-S-01

The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

- The Power distribution board shall be comprising of incomer panel one no. and the outgoing module feeder panels 4 nos approx. with hinged type doors at front  for each feeder module. The incomer panel approx. dimension shall be W X H X D = 800 X2390X1300 mm and each  outgoings panel approx. dims shall be W X H X D = 800 X2390X560 mm .

- The incomer ACB shall be draw-out type and outgoings shall be fixed type.

- The details of various feeders rating with their components are as per

annexure: 2 ST-F.

- The details /specifications of equipments/components for various feeders are as per annexure  : 1A-C.

- The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

- The incomer ACB panel for PDB2ST shall be on left  end .

- The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons , front of ACB etc shall be on the front door of the respective feeder modules.

- The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

- The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

- The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

- The thickness of the M.S sheet  C/R  for component mounting plate  shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

- The hinged doors of the panels shall be properly earthed using flexible wires .

- The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

- The structure of the panels shall be chemically pretreated before painting.

- The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

- The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

- The vendor shall get approved the mechanical drgs. , electrical drg., components details  of the panels before mfg. the same within one month of placement of the P.O. .

- Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint.  manuals of the various equipments/ components used shall be required with delivery.

- The T.C. and G.C. for one year after installation /commissioning shall be required.

Encl to INDENT No .

Specification No.- PDB 3ST-S-01

The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

- The Power distribution board shall be comprising of incomer panel one no. and the outgoing module feeder panels 4 nos approx. with hinged type doors at front  for each feeder module. The incomer panel approx. dimension shall be W X H X D = 800 X2390X1300 mm and each  outgoings panel approx. dims shall be W X H X D = 800 X2390X560 mm .

- The incomer ACB shall be draw-out type and outgoings shall be fixed type.

- The details of various feeders rating with their components are as per

  - annexure: 3ST-F.

- The details /specifications of equipments/components for various feeders are as per annexure  : 1A-C.

- The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

- The incomer ACB panel for PDB3ST shall be on left  end .

- The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons , front of ACB etc shall be on the front door of the respective feeder modules.

- The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

- The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

- The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

- The thickness of the M.S sheet  C/R  for component mounting plate  shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

- The hinged doors of the panels shall be properly earthed using flexible wires .

- The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

- The structure of the panels shall be chemically pretreated before painting.

- The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

- The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

- The vendor shall get approved the mechanical drgs. , electrical drg., components details  of the panels before mfg. the same within one month of placement of the P.O. .

- Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint.  manuals of the various equipments/ components used shall be required with delivery.

- The T.C. and G.C. for one year after installation /commissioning shall be required.

Encl to INDENT No .

Specification No.- PDB 4ST-S-01

The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

- The Power distribution board shall be comprising of incomer panel one no. and the outgoing module feeder panels 4 nos approx. with hinged type doors at front  for each feeder module. The incomer panel approx. dimension shall be W X H X D = 800 X2390X1300 mm and each  outgoings panel approx. dims shall be W X H X D = 800 X2390X560 mm .

- The incomer ACB shall be draw-out type and outgoings shall be fixed type.

- The details of various feeders rating with their components are as per

  - annexure: 4 ST-F.

- The details /specifications of equipments/components for various feeders are as per annexure  : 1A-C.

- The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

- The incomer ACB panel for PDB4ST shall be on left  end .

- The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons , front of ACB etc shall be on the front door of the respective feeder modules.

- The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

- The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

- The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

- The thickness of the M.S sheet  C/R  for component mounting plate  shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

- The hinged doors of the panels shall be properly earthed using flexible wires .

- The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

- The structure of the panels shall be chemically pretreated before painting.

- The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

- The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

- The vendor shall get approved the mechanical drgs. , electrical drg., components details  of the panels before mfg. the same within one month of placement of the P.O. .

- Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint.  manuals of the various equipments/ components used shall be required with delivery.

- The T.C. and G.C. for one year after installation /commissioning shall be required.

Encl to INDENT No .

Specification No.- PDB  5 ST-S-01

The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

- The Power distribution board shall be comprising of incomer panel one no. and the outgoing module feeder panels 2 nos approx. with hinged type doors at front  for each feeder module. The incomer panel approx. dimension shall be W X H X D = 800 X2390X1300 mm and each  outgoings panel approx. dims shall be W X H X D = 800 X2390X560 mm .

- The incomer ACB shall be draw-out type and outgoings shall be fixed type.

- The details of various feeders rating with their components are as per

annexure  : 5ST-F.

- The details /specifications of equipments/components for various feeders are as per annexure  : 1A-C.

- The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

- The incomer  panel for PDB5ST shall be on right end .

- The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons etc shall be on the front door of the respective feeder modules.

- The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

- The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

- The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

- The thickness of the M.S sheet  C/R  for components mounting plate  shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

- The hinged doors of the panels shall be properly earthed using flexible wires .

- The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

- The structure of the panels shall be chemically pretreated before painting.

- The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

- The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

- The vendor shall get approved the mechanical drgs. , electrical drg.,component details  of the panels before mfg. the same within one month of placement of the P.O. .

- Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint manuals of the various equipments/ components used shall be required with delivery.

- The T.C. and G.C. for one year after installation /commissioning shall be required.