|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
| --- | --- | --- |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 1 OF 9 |
| - Scope of Supply : The specification includes complete design and manufacture assembly, testing at manufacturer’s worksand delivery to site of CODE: CG390 0250 1__ the UPS system complete in all respects. - Ambient conditions : Design ambient temperature : 50º C Humidity at design Min / Max temp : 85 % at 46º C 3.0 Application of UPS: To feed electronic instruments, Computers, Printers etc.. 4.0 Applicable standards: 4.1 The item supplied against this specification shall be in compliance with relevant latest IEC/IEEE/IS Standards 4.2 Items supplied against this specification shall confirm to the latest applicable Indian Standards except where modified or supplemented by this specification. IS-3700 Essential ratings and characteristics of semiconductor devices. IS-5467 Code of practice for the use of semiconductor junction devices. IS-4237 General requirements for switchgear and control gear 4.3 Equipments confirming to any other standard which ensures equal of better quality may be accepted. In such case, copies of the English version of Standard adopted must be submitted with the bid. 5.0 Features of the system: 5.1 The system offered shall comply with the following requirements/features and block diagrams as per enclosed Annexure I and shall have surge with stand capability. 5.2 The system consists of the following. a). 2 x 100% Static Chargers b). 2 x 100% Static Invertors c). 1 X 100% Static Bypass Voltage Stabiliser.d).Static switches. e).Manual bypass switch, f). Back up Battery bank. g). Battery Bank Isolators. h). Input/Output Isolators. 5.3 The system shall operate in parallel redundant mode under normal conditions and each bank sharing 50% load. Incase of troublein any of the invertor sections, the other invertor will continue to feed the load while the faulty section shall be isolated without any interruption in the out put. When both the invertor sections are faulty, a static switch shall automatically transfer the load to an alternate source of AC power with zero breaks. The return to normal i.e. invertor mode shall be automatic for externally caused transfers such as over loads, but it shall be manual in all other cases. Manual transfer shall be initiated by actuation of push button. 5.4 All manual and automatic transfer/retransfer shall be effected only after the synchronism of the outputs are established and suitable equipment for maintaining automatic synchronisations of the invertors and static stabiliser shall be provided |  |  |
| Date 05-04-05 | Prepared By : | Approved By : |

|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
| --- | --- | --- |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 2 OF 9 |
| - On mains failure or sustained undervoltages, the invertor unit (s) shall be connected to +ve output of the full batteryto furnish an uninterrupted source of power of specified viltage for a duration 30 minutes unless other wise mentioned in specified design requirements. - A normal bypass switch (make before break) shall be provided to isolate the invertor and static switch for maintenance. - Battery Bank:Sealed VRLA 12 volts x 32 cells (384 Volts), 100 AH (CG390 0250 1__) - Battery stands as per manufacturers approved drawings. - Terminations, interconnecting cables etc. - The following factors shall be considered while sizing the battery. Minimum Call voltage-90% of the normal cell at the end of discharge-Voltage. Design margin: 10% above the nominal requirement. Aging factor 10%. Temperature correction factor: As per the relevant standards. 6.0 Charger 6.1 Each charger unit shall be solid state full wave half controlled type, with boost and float charging facility. 6.2 Input supply : 380 V / 400 V / 415 Volts + 10% / - 15%, 50 Hz +/- 5%, 3, N (4 wire system), P.F.: 0.81 at 400 Volts 6.3 + /- 0.5% of nominal voltage for load variations of 0-100 %. 6.4 Ripple content: Not greater than 1 %. 6.5 Output current adjustable range: 80 to 125%. 6.6 Each charger unit shall be sized to feed the UPS system output load plus battery float charging current under normal condition and total UPS system output load plus battery boost charge current when the battery is in fully discharged conditions. 6.7 Output voltage: Float mode : Variable :384 volts +/- 10% Boost Mode: Variable : 415 Volts +/- 10% - The unit shall be designed to boost charge the completely discharged battery in 8 hours. - Necessary smoothing filters shall be provided in the output circuit. - Necessary blocking diodes shall be provided to prevent power feed backfrom the battery or other charger. - Necessary current limiting features shall be provided to prevent damage of the charger. - Invertoers Each inverter shall meet the following requirements 7.1 The invertor unit shall be designed to operate from the rectifier output without the use of battery smoothing effect. 7.2 With the battery connected to the UPS system, a filter shall be provided at the input of inverter unit to reduce the AC feed back from the battery to a maximum of 2% of battery AH capacity. |  |  |

|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
| --- | --- | --- |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 3 OF 9 |
| - The inverter unit shall be designed to operate with 344 volts to 456 volts DC at terminals. (3, N & 4 wire system) - Output Voltage regulation at the outgoing terminals of UPS system from where the load are fed: a. Steady state ( 0 – 100%) : +/- 1% at all input voltage variations and power factors. b .Dynamic response: i. For 100% step load change: +/- 8%. ii. For 50% step load change: +/- 6%. iii. Recovery time: +/- 5% within 5 milli sec. and +/- 1% with in 30 milli sec. - Output regulation at all loads: 50 Hz +/-0.5% - Total harmonic distortion: 4 % max. - Harmonic content of any single harmonic: 25 % max. - Short time over load: 300 % for 4 m.sec./ 200 % for 10 sec. / 125 % for 10 min. - Temp. rise over 50º C: Solid state element: 20º C / Wound elements: 30º C - Synchronisation limits for maintenance and synchronism between inverter and standby A.C source: +/- 5% - Field adjustment range for above: 50 +/- 0.5 Hz to 50 +/- 2.5 Hz. - Necessary current, limiting features shall be provided to prevent damageof inverter under short circuit conditions and overloads. - Static Switches: Capacity: 125% of continuous nominal ratingof UPS system. 100% of continuous rating for 5 cycles (peak). Transfer time: 1/4 cycle. Type of transition: Make before break. - Standby A.C source (By-pass): 9.1 Input supply: 415 Volts =/- 10%, 50 Hz +/- 3%, 3-N 4 Wire 9.2 Transient output voltage: +/- 1 % within 50 ms. Regulation within 100 % load charge. 9.3 Type of stabilizer: Static 9.4 Type of input transformer: 2 winding Dry type. 9.5 Rating of input transformer: 125% of nominal UPS capacity. 10.0 Instruments, indicators and annunciators: Following instruments shall be provided. 10.1 Charger Panel: AC Line voltage with selector switch / AC Line current with selector switch / Charger output voltage / Charger output current and Battery current 10.2 Inverter Panel: DC input current / UPS output voltage / UPS output current / P.F meter / Freqency meter 10.3 Following indicating lamps shall be provided along with mimic diagram or the system charger panel. AC mains ON 3 lamps / Battery on float / Freqency on boost. On Inverter panel: Battery output ON / Inverter -1 feeding / Inverter-2 feeding / Standby supply ON / Load on bypass / Main synchronized. 10.4 Audio visual alarm shall be provided for the following complete with accept, reset and test facilities. A. Charger Panel: Main under voltage / single phasing / Charger failures / SCR fuse failure / Reverse polarity on DC bus / Cooling fan tripped / Battery – Discharges / DC over-Voltage / Battery ground fault. |  |  |
|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 4 OF 9 |
| - B. Inverter panel: DC voltage to the inverter low-high / DC current to the inverter low – high / Inverter –I trouble / Inverter II trouble / Inverter output voltage high / load on bypass / Inverter output voltage – low / cooling fan tripped / Inverter out put voltage –high. - Potential free NO contacts for remote annunciation for all the above alarms shall be provided.. - Construction of UPS panel: 11.1 Charger and inverter section shall be housed in the same panel or separately with all interconnections and shall be complete in all respects. 11.2 Sheet steel (CRCA) 1.6 / 2 mm thick 11.3 Enclosure Protection IP 40 11.4 Top / Bottom Cable entry (As per the approved drawing) 11.5 Space heater with cubicleand lighting lamp and a 15 Amps /240 recepticle shall be provided. 11.6 External / Internal paint shall be decided on drawing approval. 12.0 Noice level Noice level should not be more than 65 db at 1 meter distance from the UPS panel. 13.0 Forced ventilation if required shall be providedto give the retested load for half an hour at reduced load (75%) continuously. 14.0 Testing 14.1 The follwing tests shall be carried out at vendor works in the presence of the Testing Engineer. 3 weeks advance information shall be given after internal tests. Scope of testing etc shall be furnished. 14.2 Test shall be conducted using the unit battery supply. Battery is also in vendors scope. - System shall run under rated power factor for a minimum continuous period of 100 hours. Total load shall be removed and reapplied once each hour for first four and last four hours of test. Record ouput voltage, current, frequency and critical temperatures for the above tests. The temperature shall be measured with all the panel doors closed. Load the system and switch off the blowers (if provided) and the system shall be capable of delivering the load as per clause 13.0 of this spec. Record noice level at various operations. - Transient response: Record output voltage, output current, and utility voltage with oscillogram under the following conditions: - Simulate an input a-c power failure to the rectifier. - Simulate a battery charger (rectifier) failure. - Simulate a battery failure. - Simulate an inverter failure, which would cause the full rated load to the other inverter. - Simulate both inverters failurewhich would cause the full rated load at rated power factor to transfer from invertes to bypass. - Manual return the full rated power factor from bypass to inverter output. |  |  |
|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 5 OF 9 |
| 14.7 Short circuit tests:. Record output voltage, output current and utility voltage with oscillogram under the following conditions - Short circuit the output bus to record the current limiting effect of the inverter. - Apply 150% rated load at rated power factor and measure time required for inverter protective devices to operate. - Control, Alarm, Instrumentation Tests: - Functionally test all controls alarm for correct setting and operation. - Test and calibrate all indicating instruments. - Documentation Schedule: 15.1 Bidder should furnish 2 sets of the following along with the bid. a. Filled in data sheets for each system b. Layout of battery banks with dimensions c. Dimensional drawing and foundations details of the battery charger and UPS panels. d. Schematics of battery chargers & UPS system. e. Ventilation requirements for the battery room. f. Any airconditioned atmosphere requirement for charger & UPS panels. g. Bill of material h. Relevent catalogues and literatures. i. Single line diagram with functional write ups. j. List of clause wise deviations, if any. k. Sizing caluculations for batteries and chargers. 15.2 The supplier shouldf furnish 3 sets of the following with 10 days of LOI for our approval. a.. Final dimensional drawing, foundation details. b. Control scheme and bill of material. c. Final layout of battery banks. d. Technical details of each item. 15.3 The supplier should furnish the follwing in 5 copies of hand bound folders immediately after testing. a. All documents listed in 15.2 b. O & Manual (5 sets) c. Commissioning instructions & Test reports. 2 CD’s with auto-cad drawings shall be furnished. 16.0 The price format should contain the the following: a. Unit price of each equipment of each rating. b. Unit price for 2 years operational spares. 17.0 Gaurentee: The equipment supplied shall be garenteed for a period of 18 months from the date of commissioning. Any defects noticed during this period shall be replaced free of cost at site. |  |  |

|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
| --- | --- | --- |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 6 OF 9 |
| Technical Details of UPS System To be filled by bidder Description : Battery Type : Make : Nominal Capacity of the Battery : 10 Hrs discharge basis) A.H : Capacity of the battery 60 / 90 min: Type of Positive cell : Type of Negative cell : No. of Cells : Float charging current amps : Float voltage V/Cell : Boost charging voltage V/cell : Voltage at the ---of discharge : 10 hours discharge V/cell : 60 min. discharge basis V/cell : 30 min. discharge basis V/cell : Maximum charging current (amps): Internal resistance of one cell Ohm: Short circuit current : Applicable standard : Battery layout furnished Yes/No : Battery Charger 1. Type : 2. Make : 3. Service : 4. A.C.Input ratings : a. Input voltage : b. Voltage range : c. 3, 3 wire / 3, 4 wire : d. Freqency with variation : e. Maximum KVA input : f. Input current amps full rated load : g. Input current amps full rated load : plus battery charging. h. Input power factor : 5. D.C.Output ratings : a.: Output voltage range : b. Voltage during float charging : c. Voltage during boost charging : d. Voltage during charging : e. Voltage regulation : f. Max. ripple content : g. Output current full rated load : plus battery charging 6. Efficiency a. At rated output % : b. at 75 % rated output % : c. at 50 % rated output % : d. at 25 % rated output % : e. Max. efficiency and the corresponding output: |  |  |

|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
| --- | --- | --- |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 7 OF 9 |
| Technical Details of UPS System To be filled by bidder Description 7. Temp. rise above ambient a. Solid state element : º C above º C amb. b. Woulnd element : º C above º C amb 8. Instruments provided (List of Instruments) : : 9. Controls Provided (Furnish schematics & write up) : 10. Provision of mimic buss : 11. Indication lights / lamps provision : 12. Alarm Indication Provided : 13. Overall dimension of the panel : (Give write up on general construction of the panel) : 14. Length x Breadth x Height : 15. Weight of the panel : 16. Standards applicable / Conforms to : Inverter: 1. Type : 2. Make : 3. Service : 4. Whether suitable to parallel operation : 5. Rated output Voltage : 6. Nominal voltage : 7. Maximum voltage : 8. Minimum Voltage : 9. Rated output kVA : 10. Rated output voltage : 11. No. of phases : 12. Voltage regulation : At unity P.F % : At 0.8 P.F : 13. Frequency : 14. Output voltage adjustment : 15. Freqency variation : 16. Output frequency adjustment : 17. Reated power factor : 18. Power factor range : 19. Total harmonics : 20. Overload duration 200 % / 125 % : 21 Short circuit current ratings : 22. Dynamic response measured at the outgoing : load terminals of UPS. 100 % step load change/recovery time to 5% & 1%: 50 % step load change/recovery time to 5% & 1%: 23. Noise level : 24. Electromagnetic interference : 25. Minimum voltage required to start the inverter : |  |  |
|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 8 OF 9 |
| Technical Details of UPS System To be filled by bidder Description 26. Efficiency : Full load output : 75% of Full load output : 50% of Full load output : 25% of Full load output : 27 Load at which maximum efficiency occurs : 28. Maximum efficiency : 29. Temerature rise above ambient : a. Solid state element : º C above º C amb. b. Woulnd element : º C above º C amb. 30. Instruments provided (enclose the list of insts). : 31. Controls provided (Furnish schematics with wite up): 32. Mimic provided or not : 33. Alarm Indicators provided : 34. Light/lamp indicators provided : 35. Overall dimension of the panel (Give a write up : on general construction of the panel) Length x Breadth x Height : 36. Weight of the inverter panel : 37. Standards applicable / Conforms to : 3  Transformer / 1 Transformer in bypass : 1. Type & Make : 2. Core construction (core/shell type) : 3. Rated output : 4. Winding connection : 5. Voltage ratio at no load : 6. Freqency : 7. Type of cooling : 8. Winding insulation class : 9. Tapping on 415 volts side or not : 10. Number of taps and % variation per step : 11. Switch off, circuit type : 12 Dimension of the panel housing the transformer : Length x Breadth x Height : Weight of the transformer : Applicable standards : Voltage Stabiliser : 1. Type : 2. Make : 3. Service : 4 Rated output kVA : 5. Rated output Voltage : 6. No of Phases : 7. Voltage regulation : At unity P.F % : At 0.8 P.F : |  |  |

|  | TECHNICAL SPECIFICATION | Ref.: GT/ TEST/SPEC250 |
| --- | --- | --- |
|  | FOR | Rev : 00 |
|  | 25 kVA, 6 pulse UPS SYSTEM | Page 9 OF 9 |
| Technical Details of UPS System To be filled by bidder Description 8. Output Voltage adjustment : 9. Frequency : 10. Total harmonics : 11. Over load capacity : 12. Short circuit rating : 13. Temerature rise above ambient : a. Solid state element : º C above º C amb. b. Woulnd element : º C above º C amb. 14. Instruments provided (enclose the list of insts). : 15. Contacts provided (furnish schematics with write up): 16. Transient response and time : for 100 % step load change : for 50 % step load change : 17. Light / lamp indicators provided : 18. Alarm indicators provided : 19. Overall dimensions of the stabiliser : Length x Breadth x Height : Weight : 20. Standards applicable / conforms to : GENERAL 1. Possible overloading of UPS if room temp is : maintained to AC 25º C to 30º C 2. Overall efficiency of each UPS unit At 100 % laod : (i.e. AC output to AC input) At 50 % laod : 3. Overall dimension of complete UPS systemoffered : 4. Transfer time to bypass the transformer when : Operating in synchronous & unsynchnonous modes. 5. Operating performance factor for the UPS at various : power factors (i.e 0.5 to unity pf) 6. Can inverter be operated with battery isolated and : for how much duration. 7. Accessories includes (the following meters are essential) Digital Multimeter true RMS fluke model 787 Qty. 1 no Digital clamp meter Fluke model 337 600 V/1000amps Qty. 1 no. Digital Meghaohmmeter Fluke model 1520 250V/500V/1000V. Qty. 1no. |  |  |