## Sheet1
| BHARAT HEAVY ELECTRICALS LIMITED |  | Date:
| Heavy Power Equipment Plant, Ramachandrapuram |  | Due Date:
| Hyderabad-502 032, INDIA |  | Supplier Qtn No.
| Phones: 23182250, Fax No:040-23186173 |  | Date :
E-mail: burre@bhelhyd.co.in
Tender Documents to be filled by the supplier for Supply of
Portable Oil Mist Fume Extraction System.
ADDRESS OF THE SUPPLIER:
TELEPHONE NOS:
FAX NOS:
E-MAIL ADDRESS :
Sl. No. | Description for BHEL Requirement |  | Vendor | Remarks
1 | UTILITY :
The equipment is required for extracting oil and coolant mist fumes generated during machining of various components in 5 - axis machining centre located in Air conditioned room in TCGT shop.
2
2 | Specification of exhaust system (LEV) for the machine:
2.1 | Exhaust Fan capacity | 5000 cfm
2.2 | Quantity | 1 No
2.3 | St. Pressure | 50 mmwc
2.4 | Temperature | Varying between 20 to 35 deg C
2.5 | Speed | Vendor to specify
2.6 | Motor with suitable rating | Vendor to specify
2.7 | Suitable Drive | Vendor to specify
2.1 | Variable pitch type of impeller shall be provided. | Vendor to submit details.
3 | Duct 75 sq. M approx., ducting material shall be Mild Steel or equivalent to prevent rust.Layout of ducting to suit machine and exhaust standards as per APPCB. Protection from rain entering ducting system, supports for ducting on walls shall be clearly shown in schematic drg. -- 1 Set | Vendor to visit bhel & offer correctly to ensure no aesthetics disturbance. vendor to submit complete details along with offer only after study at location of machine
4 | Suction Hood -(MS) -- 2 Nos. | Size to suit machine
5 | Platform with Monkey Ladder -- 1 No | As per BHEL requirement / Pre - Visit study
6 | Outlet Duct with tie rope & Cowl - (MS) as per requirement. | Vendor to submit complete details along with offer only after study at location of machine.
7 | Support Structure-(MS) - 1 No. | As per BHEL requirement / Pre - Visit study
8 | Electrical & Instrumentation - 1 set | Vendor
9 | Installation ,Trial Run & Commissioning of the above | Vendor
9.1 | Civil Work | M/s.BHEL scope
10 | Specification for Supply air system for the Room:
10.1 | Supply Air Fan ( Make & Model ) | Vendor
10.2 | Quantity | 1 No.
10.3 | Capacity: | 5000 Cfm
10.4 | St. Pressure | 65 mmwc
10.5 | Temperature | Varying between 20 to 35 deg C
10.6 | Speed | Vendor
10.7 | Motor with suitable rating | Vendor
10.8 | Suitable Drive | Vendor
11 | Duct 60sq. M approx.-only for idea, ducting material shall be galvanised iron or equivalent to prevent rust Layout of ducting to suit machine and exhaust standards as per APPCB. Protection from rain entering ducting system, supports for ducting on walls shall be clearly shown in schematic drg. - 1 Set. | Vendor to visit BHEL & offer correctly to ensure no aesthetics disturbance. Vendor to submit complete details along with offer only after study of conditions at BHEL.
12 | Supply Air Grilles - 8 Nos. | Vendor to specify Make & Model
13 | Pre Filter (20microns) - 4 Nos. | Vendor to specify Make & Model
14 | Fine Filter(5 microns) - 4 Nos. | Vendor to specify Make & Model
15 | General:
15.1 | In put Power supply: | By BHEL
15.2 | Sound Level | Less than 75dBA @ 1Mt.Distance
15.3 | Provision for Lifting arrangement (like hooks, lugs etc) at suitable location shall be provided by vendor for easy handling of the equipment. | Vendor
15.4 | Fan Casing Material | IS-2062 - 2.5 MM.
15.5 | Impeller Material | IS-2062 - 2.5 MM.
16 | Civil Works: Vendor shall explain in detail civil works required by BHEL during Erection & Commissioning. | Vendor
17 | Individual Starter for Fan Motors of Reputed make. | ABB / DOL / L&T / Siemens.
18 | Accessories required for 2 years normal operation shall be furnished item wise along with offer. (as optional). | Vendor
19 | Detailed catalogues shall be furnished for the offered equipment along with offer. | Vendor
20 | BHEL engineers will inspect the equipment at suppliers works before despatch. | Vendor
21 | Five sets of operation and maintenance manuals shall be furnished along with equipment with detailed drgs. | Vendor
22 | Customers reference list with phone no., email address and contact person name shall be furnished along with offer for similar equipment. | Vendor
23 | Commssioning and prove out of the equipment at BHEL works is suppliers responsibility. | Note: Payment will be made only after successful commissioning & prove out.
24 | System shall be Guaranteed for satisfactory performance for 18 months from the date of commissioning. | Vendor
25 | All bought out items shall be reputed make considering noise/sound standards as per AP factory act. | Vendor
26 | Delivery time: | Vendor