## Main qty.
Bill of Quantites for ETC Works Rev 01
Project : 132 kV SWITCHYARD FOR 100 MW MONARCHAK GAS BASED COMBINED CYCLE POWER PROJECT
Customer : North Eastern Electric Power Corporation Ltd.(NEEPCO)
S.No. | Description | Unit | Quantity | Comments | Unit Price | Total Price
MAIN EQUIPMENTS
1 | 132 KV, 1600 A, 40.0 kA for 1 sec SF6 Circuit Breakers( 3 Phase ) with lattice type GS supporting structure, with ACSR Moose terminal connector, Breaker Control Cabinets and interpole cabling. | nos. | 9 | Mandatory Spares are included in separate Annexure-F (MANDATORY SPARES TO BE HANDLED & STORED). |  | 0
2 | 132KV, Current Transformer, 1 Phase, 5 core complete with terminal connectors for ACSR Moose | nos. | 27 | 0 |  | 0
3 | 132KV , CVT, 1 Phase, complete with ACSR Moose terminal connector | nos. | 12 | 0 |  | 0
4 | 132KV , EMVT, 1 Phase, complete with ACSR Moose terminal connector | nos. | 6 | 0 |  | 0
5 | 132kV, 1600A , Horizontal Center Break (HCB), motor operated mechanically ganged isolator complete with support insulators, operating mechanism boxes, terminal connectors for ACSR Moose, etc.
5.1 | - with two earth switch | nos. | 10 | 0 |  | 0
5.2 | - with one earth switch | nos. | 10 | 0 |  | 0
5.3 | - without earth switch | nos. | 8 | 0 |  | 0
6 | 120KV, 1 Phase, Gapless Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable, Line terminal connector for single ACSR Moose conductor. | nos. | 24 | 0 |  | 0
7 | 132KV, 1 phase pedastal mounted Wave Trap complete with 3 nos support insulators per WT, terminal connectors for ACSR Moose | nos. | 8 | 0 |  | 0
8 | 132kV Post Insulators for Bus support with terminal connector for ACSR Moose. | nos. | 18 | 0 |  | 0
| 400kV Post Insulators for Bus support complete with corona ring, terminal connector and lattice type GS supporting Structure. | nos. | 177 | 0 |  | 0
9 | 400kV Post Insulators for Bus support complete with corona ring, terminal connector and lattice type GS supporting Structure. | nos. | 178 | 0 |  | 0
10 | 400kV Post Insulators for Bus support complete with corona ring, terminal connector and lattice type GS supporting Structure. | nos. | 179 | 0 |  | 0
11 | 400kV Post Insulators for Bus support complete with corona ring, terminal connector and lattice type GS supporting Structure. | nos. | 180 | 0 |  | 0
9 | BUS BAR MATERIALS
9.1.1 | 132kV double tension double anchoring 120 kN disc string insulator each string comprising 2 x 10 discs complete with hardware suitable for twin "moose" conductor with sub conductor spacing of 250 mm with turn-buckle | Set | 27 | 0 |  | 0
9.1.2 | Same as 10.1.1 above but without turn-buckle | Set | 27 | 0 |  | 0
9.1.3 | 132kV single tension single anchoring 120 kN disc string insulator each string comprising 1 x 10 discs complete with hardware suitable for single "moose" conductor with turn-buckle | Set | 36 | 0 |  | 0
9.1.4 | Same as 10.1.3 above but without turn-buckle | Set | 36 | 0 |  | 0
9.1.5 | 132kV single suspension 120 kN disc string insulator each string comprising 1 x 10 discs complete with hardwares with drop clamps suitable for twin "moose" conductor with sub conductor spacing of 250mm | Set | 6 | 0 |  | 0
9.1.6 | 132kV single suspension 120 kN disc string insulator each string comprising 1 x 10 discs complete with hardwares with straight clamps suitable for twin "moose" conductor with sub conductor spacing of 250mm | Set | 18 | 0 |  | 0
9.1.7 | 132kV single suspension 120 kN disc string insulator each string comprising 1 x 10 discs complete with hardwares with drop clamps suitable for single "moose" conductor | Set | 42 | 0 |  | 0
10 | GS Stranded Shield wire, 7/9 SWG, 10.98 mm dia including tension clamp, PG clamp and clamping on structure for down conductor, fixing/bolting with earth strip etc to complete. | m | 1300 | 0 |  | 0
11 | ACSR "Moose" conductor complete with Tee connectors,PG clamps,etc. for droppers to equipment connections, Twin bundle spacers etc to complete. | m | 6200 | 0 |  | 0
12 | Bay and Equipment Identification label | LOT | 1 | 0 |  | 0
12.1 | Supply & Mounting of Phase color disc alongwith associated hardware as per attached Technical Specification TB-331-316-040 : ANNEXURE-B. | sets | 39 |  |  | 0
12.2 | Supply & Mounting of Danger Labels alongwith associated hardware as per attached Technical Specification TB-331-316-040 : ANNEXURE-B. | nos. | 10 |  |  | 0
13 | Erection of terminal connectors/clamps of:
13.1 | Generator Transformer | nos. | 6 | 0 |  | 0
13.2 | Station Transformer | nos. | 6 | 0 |  | 0
YARD WORK INCLUDING CABLING, TRENCH & EARTHING.
14 | Cabling including laying, dressing, tagging,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates - laying can be either on trays, supports, underground, over ground, through wall etc. All erection materials viz. cable glands, ferrules, copper lugs, cable ties / straps, Al. tags, markers will be supplied by bidder.
14.1 | Control cables- Armoured, PVC insulated , Copper conductor. FRLS Type
14.1.1 | 19Cx2.5 sqmm(In Trench) | m | 14500 | 0 |  | 0
14.1.2 | 14Cx2.5 sqmm(In Trench) | m | 7500 | 0 |  | 0
14.1.3 | 10Cx2.5 sqmm(In Trench) | m | 27500 | 0 |  | 0
14.1.4 | 7Cx2.5 sqmm(In Trench) | m | 1500 | 0 |  | 0
14.1.5 | 5Cx2.5 sqmm(In Trench) | m | 13500 | 0 |  | 0
14.2 | Auxiliary Power cables, Armoured, PVC insulated, Al conductor, FRLS Type
14.2.1 | 3.5CX 300 sq. mm XLPE ( In Trench) | m | 100 | 0 |  | 0
14.2.2 | 3.5C x 70 Sq.mm(In Trench) | m | 2000 | 0 |  | 0
14.2.3 | 3.5C x 35 Sq.mm ( In Trench) | m | 4500 | 0 |  | 0
14.2.4 | 1C x 150 Sq.mm(In Trench) | m | 300 | 0 |  | 0
14.2.5 | 4Cx6 sq.mm(In Trench) | m | 1500 | 0 |  | 0
14.2.6 | 4Cx10 sq.mm(In Trench/on Lightning Mast) | m | 1500 | 0 |  | 0
14.2.7 | 2C x 2.5 Sq.mm ( In Trench/on Lightning Mast) | m | 400 | 0 |  | 0
14.2.8 | 2C x 6 Sq.mm ( In Trench) | m | 2200 | 0 |  | 0
15 | GI Pipes (including bends) laying,excavation, back filling,repair of trench wall, etc., as per the drawing No. TB-0-331-316-104 : ANNEXURE-C.
15.1 | 50 mm | m | 400 | 0 |  | 0
15.2 | 110mm | m | 500 | 0 |  | 0
16 | Marshalling Kiosks & CT / CVT Junction Boxes
16.1 | Bay Marshalling Kiosks ( Outdoor) | nos. | 9 | 0 |  | 0
21.2 | 63 A , 220 V Outdoor type Welding sockets. | nos.
16.2 | CT JB | nos. | 9 | 0 |  | 0
16.3 | CVT/EMVT JB | nos. | 6 | 0 |  | 0
17 | Cable trench material (welded type) as per the drawing No. TB-0-331-316-104 : ANNEXURE-C. |  |  | Welded type Cable Rack/Tray material shall be free issued by BHEL.
17.1 | Cable racks 3 tier assembly | Nos. | 58 | 0 |  | 0
17.2 | Cable racks 1 1/2 tier assembly | Nos. | 155 | 0 |  | 0
17.3 | 2.5 mtr, 750,600,450,400,200 and 150mm wide Cable Trays | Nos. | 435 | 0 |  | 0
18 | Earthing material- GS strip including cutting, bending, welding with 40 mm dia MS rod riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. The Earthing of equipments shall be carried out as per Drg. No. TB-4-331-509-107 : Equipment earthing details Drawings as per enclosed Annexure-D.
18.1 | 65 x 8 mm GS Flat | km | 2.8 | material shall be free issued by BHEL. |  | 0
18.2 | 50 x 6 mm GS Flat | km | 1.8 | material shall be free issued by BHEL. |  | 0
18.3 | 25 x 3 mm GS Flat | km | 0.2 | material shall be free issued by BHEL. |  | 0
18.4 | Auxillary Earthmat | Nos. | 58 | material shall be free issued by BHEL. |  | 0
19 | Galvanised steel structures including hardware
19.1 | Lattice Structures (excluding Circuit Breaker) | MT | 235 | 0 |  | 0
20 | CONTROL ROOM EQUIPMENT as per Annexure-H | LOT | 1 | 0 |  | 0
21 | AUXILIARY SUPPLY - (BATTERY/ CHARGER/ DIST BD)
21.1 | 220V DC Battery Bank | Set | 2 | 0 |  | 0
21.2 | 48V DC Battery Bank | Set | 2 | 0 |  | 0
21.3 | 220V DC, Float CUM Boost Charger | Set | 2 | 0 |  | 0
21.4 | 48V DC, Float CUM Boost Charger | Set | 2 | 0 |  | 0
21.5 | 415V main LT Switchgear ACDB | Set | 1 | 0 |  | 0
21.6 | 220V DCDB | Set | 2 | 0 |  | 0
21.7 | 48 V DCDB | Set | 2 | 0 |  | 0
22 | Mandatory Spares as per Annexure-F | LOT | 1 | MANDATORY SPARES TO BE HANDLED & STORED |  | 0
23 | FIRE FIGHTING SYSTEM as per Annexure-I | LOT | 1 | The scope of work covers supply, inspection and testing at bidder's and/ or his sub vendor's work(s), proper packing for transportation, delivery, storage and handling at site, erection, testing and commissioning, final painting and carrying out acceptance tests at site to the satisfaction of owner. |  | 0
| Total Amount (Rs.) |  |  |  |  | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
1 | Loading / Unloading, handling, multiple shifting to & from stores, proper storage, assembly, installation, pre-commissioning test and commissioning tests are included in the scope.
2 | MS/ GS welding - As per Equipment earthing details : TB-4-331-509-107 enclosed
3 | All the drawings and documents as per Annexure- E shall be followed for ETC work.
4 | Equipment labels to be painted as per requirement.
5 | Quoted rates are deemed to be inclusive of miscellenaous works viz. erection of clamps and connectors, bundle spacers & misc clamps.
6 | For SPARES only unloading, storage & handling is applicable. Spares of equipments is covered in Annexure-F (MANDATORY SPARES TO BE HANDLED & STORED)
7 | Cable gland quantity & technical specification attached as Annexure-G.
8 | Note for Earthing: The earthing includes earthing of all switchyard equipment, towers and LM's, lattice structures, cable trenches, fence and Control room equipments using necessary Connectors for earthing flats.
9 | NOTE for PLCC: Testing and commisioning shall be done under the supervision of respective PLCC panel suppliers.
10 | Control Room Equipments shall be as per Annexure- H.
11 | 10% welding joints in earthing shall be tested for dye penetration test.
12 | Mounting of phase color discs & Danger plates is included in the scope.
13 | Equipment labels to be painted as per requirement.
14 | Minor Civil works such as modification of civil foundations, making holes in the trenches, grouting for towers, LA, LM, BPI foundations, fixing of trench material will be in the scope of ETC contractor.
15 | FIRE FIGHTING SYSTEM shall be as per Annexure- I.