## Total
BOARD NAME: 415V FGD SERVICE PMCC-1, #0DA
CURRENT RATING: 3200A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 3200A | DAET (I/C) | 1
| Incomer-2 3200A | DAET (I/C) | 1
| Bus Coupler-3200A | DAET (B/C) | 1
| Bus PT-50VA | G1 | 2
| CST-2kVA | CS | 2
Power (A)
| 16 | E1 | 32
| 63 | E1 | 7
| 16 | E/E3 | 42
| 32 | E/E3 | 15
| 63 | E/E3 | 15
| 160 | E/E3 | 2
| 250 | E/E3 | 2
| 1250 | DAE (O/G) | 1
DOL (KW)
| 3.1-5.5 | DK2 | 2
| 13.1-24.0 | DK2 | 5
| 30.0-37.0 | DK21 | 19
| 37.1-55.0 | DK21 | 5
| 80.1-100.0 | DK21 | 2
| ACB Panel |  | A.R
| MCC Panel-DFDO |  | A.R
BOARD NAME: 415V FGD SERVICE PMCC-2, #0DB
CURRENT RATING: 3200A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 3200A | DAET (I/C) | 1
| Incomer-2 3200A | DAET (I/C) | 1
| Bus Coupler-3200A | DAET (B/C) | 1
| Bus PT-50VA | G1 | 2
| CST-2kVA | CS | 2
Power (A)
| 16 | E1 | 32
| 63 | E1 | 7
| 16 | E/E3 | 42
| 32 | E/E3 | 15
| 63 | E/E3 | 15
| 160 | E/E3 | 5
| 250 | E/E3 | 2
| 1250 | DAE (O/G) | 1
DOL (KW)
| 3.1-5.5 | DK2 | 2
| 13.1-24.0 | DK2 | 5
| 30.0-37.0 | DK21 | 19
| 37.1-55.0 | DK21 | 5
| 80.1-100.0 | DK21 | 2
| ACB Panel |  | A.R
| MCC Panel-DFDO |  | A.R
BOARD NAME: 415V FGD COMMON PMCC, #0DC
CURRENT RATING: 4000A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 4000A | DAET (I/C) | 1
| Incomer-2 4000A | DAET (I/C) | 1
| Bus Coupler-4000A | DAET (B/C) | 1
| Bus PT-50VA | G1 | 2
| CST-2kVA | CS | 2
Power (A)
| 16 | E1 | 12
| 16 | E/E3 | 35
| 32 | E/E3 | 5
| 63 | E/E3 | 5
| 250 | E/E3 | 3
| 800 | DAE (O/G) | 2
| 1250 | DAE (O/G) | 2
DOL (KW)
| 3.1-5.5 | DK2 | 4
| 13.1-24.0 | DK2 | 8
| 30.0-37.0 | DK21 | 13
| 37.1-55.0 | DK21 | 3
| 80.1-100 | DK21 | 5
| 110.0-200.0 | DM | 3
| ACB Panel |  | A.R
| MCC Panel-DFDO |  | A.R
BOARD NAME: 415V FGD EMERGENCY MCC, #0MA
CURRENT RATING: 1250A
BOTTOM CABLE ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 1250A | DAE (I/C) | 1
| Incomer-2 1250A | DAE (I/C) | 1
| Incomer-3 1250A | DG | 1
| Bus Coupler-1250A | DAE (B/C) | 1
| Bus PT-50VA | G1 | 2
| CST-2kVA | CS | 2
Power (A)
| 32 | E/E3 | 5
| 63 | E/E3 | 4
| 100 | E/E3 | 4
| 160 | E/E3 | 2
| 250 | E/E3 | 5
DOL (KW)
| 1.6-3.0 | DK2 | 5
| 3.1-5.5 | DK2 | 22
| 7.1-13.0 | DK2 | 5
| 30.0-37.0 | DK21 | 10
| 37.1-55.0 | DK21 | 10
| ACB Panel |  | A.R
| MCC Panel-DFDO |  | A.R
BOARD NAME: 415V MISC MCC, #0SA
CURRENT RATING: 1250A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 1250A | DAE (I/C) | 1
| Incomer-2 1250A | DAE (I/C) | 1
| Bus Coupler-1250A | DAE (B/C) | 1
| Bus PT-50VA | G1 | 2
| CST-2kVA | CS | 2
Power (A)
| 16 | E1 | 93
| 32 | E1 | 27
| 16 | E/E3 | 33
| 32 | E/E3 | 9
| 63 | E/E3 | 4
| 250 | E/E3 | 3
DOL (KW)
| 1.1-1.5 | DK2 | 111
| 1.6-3.0 | DK2 | 26
| 13.1-24.0 | DK2 | 2
| 30.0-37.0 | DK21 | 8
| 37.1-55.0 | DK21 | 5
| ACB Panel |  | A.R
| MCC Panel-DFDO |  | A.R
BOARD NAME: 415V GHP/GDW MCC, #0SB
CURRENT RATING: 800A
BOTTOM CABLE ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 800A | DAE (I/C) | 1
| Incomer-2 800A | DAE (I/C) | 1
| Bus Coupler-800A | DAE (B/C) | 1
| Bus PT-50VA | G1 | 2
| CST-2kVA | CS | 2
Power (A)
| 16 | E/E3 | 8
| 32 | E/E3 | 5
| 63 | E/E3 | 8
| 100 | E/E3 | 2
| 160 | E/E3 | 3
DOL (KW)
| 1.1-1.5 | DK2 | 3
| 1.6-3.0 | DK2 | 5
| 3.1-5.5 | DK2 | 8
| 7.1-13.0 | DK2 | 8
| 13.1-24.0 | DK2 | 7
| 30.0-37.0 | DK21 | 7
| 37.1-55.0 | DK21 | 7
| ACB Panel |  | A.R
| MCC Panel-DFDO |  | A.R
BOARD NAME: 415V LSS TANK MCC, #0SC
CURRENT RATING: 250A
BOTTOM CABLE ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 250A | CC (I/C) | 1
| Incomer-2 250A | CC (I/C) | 1
| Bus Coupler-250A | CC (B/C) | 1
| Bus PT-50VA | VM | 2
| CST-1kVA | CS | 2
DOL (KW)
| 37.1-55.0 | DK21 | 3
| MCC Panel-DFDO |  | A.R
BOARD NAME: 220V FGD DCDB, #0FA
CURRENT RATING: 63A
BOTTOM CABLE ENTRY
DOUBLE FRONT FIXED TYPE
FLOOR MOUNTED
| DESCRIPTION | FEEDER TYPE | QUANTITY
| Incomer-1 63A | CH | 2
| Incomer-2 63A | DB | 2
| Bus Coupler-63A | HD | 3
| Metering & Protection | S | 2
Power (A)
| 16 | X | 20
| 32 | X | 8
| 63 | X | 6
| DCDB Panel-DFF |  | A.R
BOARD NAME: 415V AC FUSEBOARD
CURRENT RATING: 63A
BOTTOM CABLE ENTRY
FIXED TYPE
FLOOR MOUNTED
| Incomer-1 63A | H2 | 1
| Outgoing-16A | ACFB O/G TP | 10
| Outgoing-16A | ACFB O/G SP | 6
BOARD NAME: 220V DC FUSEBOARD
CURRENT RATING: 63A
BOTTOM CABLE ENTRY
FIXED TYPE
FLOOR MOUNTED
| Incomer-1 63A | H3 | 1
| Outgoing-16A | DCFB O/G | 10

## Annexure B1-FGD SERV PMCC-1
BOARD NAME: 415V FGD SERVICE PMCC-1, #0DA
CURRENT RATING: 3200A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 3200A | DAET (I/C) | 1
2 | Incomer-2 3200A | DAET (I/C) | 1
3 | Bus Coupler-3200A | DAET (B/C) | 1
5 | Bus PT-50VA | G1 | 2
6 | CST-2kVA | CS | 2
Power (A)
7 | 16 | E1 | 32
8 | 63 | E1 | 7
9 | 16 | E/E3 | 42
10 | 32 | E/E3 | 15
11 | 63 | E/E3 | 15
12 | 160 | E/E3 | 2
13 | 250 | E/E3 | 2
14 | 1250 | DAE (O/G) | 1
DOL (KW)
15 | 3.1-5.5 | DK2 | 2
16 | 13.1-24.0 | DK2 | 5
17 | 30.0-37.0 | DK21 | 19
18 | 37.1-55.0 | DK21 | 5
19 | 80.1-100.0 | DK21 | 2
20 | ACB Panel |  | A.R
21 | MCC Panel-DFDO |  | A.R

## Annexure-B2-FGD SERV PMCC-2
BOARD NAME: 415V FGD SERVICE PMCC-2, #0DB
CURRENT RATING: 3200A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 3200A | DAET (I/C) | 1
2 | Incomer-2 3200A | DAET (I/C) | 1
3 | Bus Coupler-3200A | DAET (B/C) | 1
5 | Bus PT-50VA | G1 | 2
6 | CST-2kVA | CS | 2
Power (A)
7 | 16 | E1 | 32
8 | 63 | E1 | 7
9 | 16 | E/E3 | 42
10 | 32 | E/E3 | 15
11 | 63 | E/E3 | 15
12 | 160 | E/E3 | 5
13 | 250 | E/E3 | 2
14 | 1250 | DAE (O/G) | 1
DOL (KW)
15 | 3.1-5.5 | DK2 | 2
16 | 13.1-24.0 | DK2 | 5
17 | 30.0-37.0 | DK21 | 19
18 | 37.1-55.0 | DK21 | 5
19 | 80.1-100.0 | DK21 | 2
20 | ACB Panel |  | A.R
21 | MCC Panel-DFDO |  | A.R

## Annexure-B3-FGD COMMON PMCC
BOARD NAME: 415V FGD COMMON PMCC, #0DC
CURRENT RATING: 4000A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 4000A | DAET (I/C) | 1
2 | Incomer-2 4000A | DAET (I/C) | 1
3 | Bus Coupler-4000A | DAET (B/C) | 1
5 | Bus PT-50VA | G1 | 2
6 | CST-2kVA | CS | 2
Power (A)
7 | 16 | E1 | 12
8 | 16 | E/E3 | 35
9 | 32 | E/E3 | 5
10 | 63 | E/E3 | 5
11 | 250 | E/E3 | 3
12 | 800 | DAE (O/G) | 2
13 | 1250 | DAE (O/G) | 2
DOL (KW)
14 | 3.1-5.5 | DK2 | 4
15 | 13.1-24.0 | DK2 | 8
16 | 30.0-37.0 | DK21 | 13
17 | 37.1-55.0 | DK21 | 3
18 | 80.1-100 | DK21 | 5
19 | 110.0-200.0 | DM | 3
20 | ACB Panel |  | A.R
21 | MCC Panel-DFDO |  | A.R

## Annexure-B4-FGD EMER MCC
BOARD NAME: 415V FGD EMERGENCY MCC, #0MA
CURRENT RATING: 1250A
BOTTOM CABLE ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 1250A | DAE (I/C) | 1
2 | Incomer-2 1250A | DAE (I/C) | 1
3 | Incomer-3 1250A | DG | 1
4 | Bus Coupler-1250A | DAE (B/C) | 1
5 | Bus PT-50VA | G1 | 2
6 | CST-2kVA | CS | 2
Power (A)
7 | 32 | E/E3 | 5
8 | 63 | E/E3 | 4
9 | 100 | E/E3 | 4
10 | 160 | E/E3 | 2
11 | 250 | E/E3 | 5
DOL (KW)
12 | 1.6-3.0 | DK2 | 5
13 | 3.1-5.5 | DK2 | 22
14 | 7.1-13.0 | DK2 | 5
15 | 30.0-37.0 | DK21 | 10
16 | 37.1-55.0 | DK21 | 10
17 | ACB Panel |  | A.R
18 | MCC Panel-DFDO |  | A.R

## Annexure B5-FGD MISC MCC
BOARD NAME: 415V FGD MISC MCC, #0SA
CURRENT RATING: 1250A
TOP/SIDE NSPB ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 1250A | DAE (I/C) | 1
2 | Incomer-2 1250A | DAE (I/C) | 1
3 | Bus Coupler-1250A | DAE (B/C) | 1
4 | Bus PT-50VA | G1 | 2
5 | CST-2kVA | CS | 2
Power (A)
| 16 | E1 | 93
| 32 | E1 | 27
6 | 16 | E/E3 | 33
7 | 32 | E/E3 | 9
8 | 63 | E/E3 | 4
9 | 250 | E/E3 | 3
DOL (KW)
9 | 1.1-1.5 | DK2 | 111
10 | 1.6-3.0 | DK2 | 26
11 | 13.1-24.0 | DK2 | 2
12 | 30.0-37.0 | DK21 | 8
13 | 37.1-55.0 | DK21 | 5
14 | ACB Panel |  | A.R
15 | MCC Panel-DFDO |  | A.R

## Annexure B6-GHP GDW MCC
BOARD NAME: 415V FGD GHP/GDW MCC, #0SB
CURRENT RATING: 800A
BOTTOM CABLE ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 800A | DAE (I/C) | 1
2 | Incomer-2 800A | DAE (I/C) | 1
3 | Bus Coupler-800A | DAE (B/C) | 1
4 | Bus PT-50VA | G1 | 2
5 | CST-2kVA | CS | 2
Power (A)
6 | 16 | E/E3 | 8
7 | 32 | E/E3 | 5
8 | 63 | E/E3 | 8
9 | 100 | E/E3 | 2
10 | 160 | E/E3 | 3
DOL (KW)
11 | 1.1-1.5 | DK2 | 3
12 | 1.6-3.0 | DK2 | 5
13 | 3.1-5.5 | DK2 | 8
14 | 7.1-13.0 | DK2 | 8
15 | 13.1-24.0 | DK2 | 7
16 | 30.0-37.0 | DK21 | 7
17 | 37.1-55.0 | DK21 | 7
18 | ACB Panel |  | A.R
19 | MCC Panel-DFDO |  | A.R

## Annexure B7-LSS TANK MCC
BOARD NAME: 415V LSS TANK MCC, #0SC
CURRENT RATING: 250A
BOTTOM CABLE ENTRY
DOUBLE FRONT DRAW OUT TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 250A | CC (I/C) | 1
2 | Incomer-2 250A | CC (I/C) | 1
3 | Bus Coupler-250A | CC (B/C) | 1
4 | Bus PT-50VA | VM | 2
5 | CST-1kVA | CS | 2
DOL (KW)
6 | 37.1-55.0 | DK21 | 3
7 | MCC Panel-DFDO |  | A.R

## Annexure B8-FGD DCDB
BOARD NAME: 220V FGD DCDB, #0FA
CURRENT RATING: 63A
BOTTOM CABLE ENTRY
DOUBLE FRONT FIXED TYPE
FLOOR MOUNTED
SL NO | DESCRIPTION | FEEDER TYPE | QUANTITY | Unit Price | Total Price
1 | Incomer-1 63A | CH | 2
2 | Incomer-2 63A | DB | 2
3 | Bus Coupler-63A | HD | 3
4 | Metering & Protection | S | 2
Power (A)
5 | 16 | X | 20
6 | 32 | X | 8
7 | 63 | X | 6
8 | DCDB Panel-DFF |  | A.R
BOARD NAME: 415V AC FUSEBOARD
CURRENT RATING: 63A
BOTTOM CABLE ENTRY
FIXED TYPE
FLOOR MOUNTED
1 | Incomer-1 63A | H2 | 1
2 | Outgoing | ACFB O/G TP | 10
3 | Outgoing | ACFB O/G SP | 6
BOARD NAME: 220V DC FUSEBOARD
CURRENT RATING: 63A
BOTTOM CABLE ENTRY
FIXED TYPE
FLOOR MOUNTED
1 | Incomer-1 63A | H3 | 1
2 | Outgoing | DCFB O/G | 10

## Annexure E
TOOLS & TACKLES
Sl. No. | Description | UOM | Qty | Unit price | Total price
1 | TROLLEY FOR ACB HANDLING (MANUALLY OPERATED) | Nos | 3
2 | ACB RACKING HANDLE | Nos | 10
3 | MODULE RACKING HANDLE | Nos | 20
4 | FUSE PULLER | Nos | 15
TOTAL

## Annexure D
MANDATORY SPARES FOR LT SWITCHGEAR
Sl | Description of Spare | UOM | Quantity | Unit Price | Total Price
No
1 | Air Circuit breaker of each type and rating | Nos | 10% of each type & rating(min 1
No)
2 | Ammeter | Nos | 2 Nos of each type, size & range
3 | Voltmeter | Nos | 2 Nos of each type, size & range
4 | Relays | Nos | 10 % of each type (min 2 Nos)
5 | Bus bar support insulators | Nos | 10
6 | Spring charging motors | Nos | 3 Nos of each type & rating
7 | Aux. Contact set | Set | 6 sets of each type & rating
8 | Limit switches | Nos | 10 Nos of each type.
9 | Arc chutes | Nos | 10% of each type & rating
10 | Fixed contact set | Nos | 3 Nos sets of each type & rating
11 | Moving contact set | Nos | 3 Nos sets of each type & rating
12 | Arcing contact | Nos | 3 Nos sets of each type
13 | Charging spring | Nos | 2 Nos of each type & rating
14 | Current transformer | Nos | 3 Nos of each type & ratio
15 | Closing coil | Nos | 6 Nos of each type & rating
16 | Trip coil | Nos | 6 Nos of each type & rating
17 | CT for Bimetal O/L relays | Nos | 3 Nos of each type & rating
18 | Voltage transformer | Nos | 3 Nos of each type & ratio
19 | Control supply transformer | Nos | 3 Nos of each type and rating
20 | (a) Power contactor | Nos | 2 Nos of each type & rating
| (b) Coil of above contactor | Nos | 2 Nos of each type & rating
21 | Air break switches/ MCCBs | Nos | 3 Nos of each type & rating
22 | DP air break switches (DC) | Nos | 3 Nos of each type & rating
23 | Control & selector switches | Nos | 3 Nos of each type & rating
24 | Control fuses & neutral links | Nos | Total 50 Nos (Fuses) & 10 Nos (Neutral links), to cover all the ratings.
25 | Indicating lamps | Nos | Total 30 Nos to cover all the types & ratings
26 | Vertical bus bar dropper support insulators | Nos | 25 Nos.
27 | (a) Primary disconnect in MCC (Bus bar end (Male/female contact) | Nos | Total 15 Nos. proportionately divide for all ratings
| (b) Secondary disconnect in MCC | Nos | Total 15 Nos. proportionately divide for all ratings
(Cable end)
28 | Push buttons | Nos | 10 Nos of each type
29 | Power fuses | Nos | Total 20% proportionately divide for all ratings (min 3 Nos)
30 | Thermal Bimetal relays | Nos | Total 5%. proportionately divide for all ratings (min 1 No)
31 | Current transducers | Nos | 2 Nos of each type & rating
32 | Voltage transducers | Nos | 2 Nos of each type & rating
33 | Busbar aluminium flat pieces | Mtr | 12 meters of each type & rating
34 | Busbar angles/formed pieces for breaker | Nos | 2 Nos. of each type
35 | Terminal blocks | Nos | 12 Nos of each type & rating

## Annexure F
ERECTION & COMMISSIONING SPARES
Sl.No. | ITEM / COMPONENT | UNIT | QUANTITY | UNIT PRICE | TOTAL PRICE
1 | FACTORY BUILT ASSEMBLIES (PCC/MCC/DB)
1.1 | Horizontal Busbar Supports | Set (3)
1.2 | Primary isolating contacts each rating (Bus side) | Set (3)
1.3 | Primary isolating contacts each rating (Load side) | Set (3)
1.4 | Secondary isolating contacts each rating | Set (3)
1.5 | Gaskets (each size) | Meter
1.6 | Fixed terminal (one way) | Nos.
1.7 | Shrouds for outgoing modules each size | Nos.
1.8 | Wire for secondary wiring, 2.5 mm2 | Meter
1.9 | Wire for secondary wiring, 1.5 mm2 | Meter
1.1 | Lugs for secondary wiring | Nos
2 | Air Circuit Breaker Components
2.1 | Shunt Trip Coil-Each rating | Nos.
2.2 | Spring charging motor-Each rating | Nos.
2.3 | Closing coil-Each Rating | Nos.
3 | Isolating Switch
3.1 | Main contact kit of each rating | Set (3)
4 | POWER CONTACTORS
4.1 | Contactor coil of each rating (110V AC) | Nos.
4.2 | Contacts kit of each rating (Main) | Nos.
5 | AUXILIARY CONTACTORS
5.1 | Complete unit with 2NO + 2NC contacts, each rating | Nos.
6 | HRC Fuse
6.1 | Fuse base each rating | Nos.
6.2 | Fuse link each rating | Nos.
7 | PUSH BUTTONS
7.1 | Actuator contacts | Nos.
7.2 | Element | Nos.
8 | INDICATING LAMP (CLUSTER LED) - Each Type | Nos.
9 | OTHERS
9.1 | AC Voltmeter (0-415V) | Nos.
9.2 | DC Ammeter (0-220V) | Nos.
TOTAL

## Annexure G
NUMERICAL RELAY COMMISSIONING CHARGES
SL.NO | DETAILS | UOM | QUANTITY | UNIT PRICE | TOTAL PRICE
1 | LUMP SUM ALL INCLUSIVE CHARGES PER NUMERICAL RELAY COMMISSIONING (INCLUDING CONVEYANCE TO SITE, BOARDING AND LOADGING) | NOS | 35
GRAND TOTAL (in Rs)

## Annexure H
SITE MODIFICATION CHARGES
SL.NO | DETAILS | UOM | QUANTITY | UNIT PRICE | TOTAL PRICE
1 | LUMP SUM FIXED CHARGES PER VISIT PER TECHNICIAN | VISIT | 3
2 | LUMP SUM DAILY CHARGES (ALL INCLUSIVE INCLUDING CONVEYENCE TO SITE, BOARDING AND LOADGING) PER TECHNICIAN | DAY | 18
3 | LUMP SUM FIXED CHARGES PER VISIT PER ENGINEER | VISIT | 5
4 | LUMP SUM DAILY CHARGES (ALL INCLUSIVE INCLUDING CONVEYENCE TO SITE, BOARDING AND LOADGING) PER ENGINEER | DAY | 15
GRAND TOTAL (in Rs)