Indent nos -78133T           Fluoroscent Tubes etc.

Item No 1

Annexure A.					Flurescent Tube

Description

1• Low-pressure mercury discharge lamps with a tubular 16 mm

envelope

2• High lamp efficacies approx ;  100 lm/W

3• Highly efficient 3-band fluorescent coating in combination with

precoating

4• Suitable  for operation with electronic gear and well

suited for dimming

5• Can be ignited from -15° to +50°C

6• Green end-plate indicating full recyclable lamp technology

7• Lamp lengths enable easy fitting into ceiling module systems

8• Virtually constant lumen level with excellent lumen maintenance

9•  suited for recessed, surface-mounted and suspended

luminaires in applications like offices, public buildings

and industry (low ceiling).

10  . Type TL5 high efficiency  .

11. Lamp Wattage 28 W

12. Color Rendering Index : 80-85

13. Color temp -  Cool White  4000 deg K

Item No 2

Annexure  B :                       Luminaire

1.Specially designed optical system of high purity aluminium .

2. The reflector is fixed to the housing by mirror holding clips and can be hinged to the housing during installation / maintenance

3. High-efficiency mirror optic reflector of high quality

aluminium with diffuse white lamellae designed for high

optical efficiency and widespread light distribution

4. Housing made of CRCA sheet steel, white inside &

outside accommodating all electrical accessories

prewired upto a terminal block Innovative corner brackets.

5. Provided with HF electronic gear for the 2X28W TL5     fluoresent lamps .(Details of the electronic gear as per annex  B1 )

7. The Luminaire should be compatible to the  fluoresent lamps  2X  28 Watts(lamp Type TL5) as mentioned in annex A ( Item No 1 )

8. Installation: Provision for recessed mounting or direct on surface. It can also be pendent mounted.

9.Type TCS 350/228 C5 HF 2 x TL-5 28W  of Philips or equivalent

Annxure  B1                    HF Electronic gear

Flat, slim,  lightweight high-frequency electronic ballast for TL5 fluorescent

lamps provided with following details :

- • Equipped with electrode heating cut-off circuit, ensuring optimal lamp operation with respect to lumen curve of lamp and reduction in system energy losses.

- • Smart power: constant light independent of mains voltage fluctuations

- • Unit to be  protected against excessive mains voltages and incorrect

connections

- • Automatic stop circuit should be  activated within five seconds in case of lamp failure (safety stop); once the lamp has been replaced, the ballast resets automatically.

- Provided with  thermal protection.

- Mains operation Rated mains voltage 220 - 240 V AC  with tolerances

: +/- 10% (198 - 264 V) , frequency 50 Hz.

- DC voltage operation (during emergency back-up)

Required battery voltage for operation of lamps 176 - 254V DC.

- Overvoltage protection 48 hr at 320 V AC 2 hr at 350 V AC.

- It should have immunity to line  transients and harmonics .

- Hum and noise level inaudible.

- The test certificate should include the insulation resistance test 500 V DC from line/neutral to Earth.