Annexure – I

Sub. : Removal /Dismantling, Shifting, Erection, Commissioning and Trial

Run of Steam heated Drying Oven No. 6/B/33 from Blk-3 Bay-8 to Blk-3

Bay-5 TRM Divn.

SCOPE OF WORK:

The contractor shall ensure erection and commissioning of steam heated oven complete in all respect and any work not covered in this specification but essential for completion of work shall be included in the scope of the contractor.

SIZE OF OVEN /PLANT: 13500 X 11600 X 6000 MM

1.0	REMOVAL/ DISMANTLING OF STEAM HEATED DRYING OVEN:

Removal/Dismantling of Complete Thermal insulation from the all out side duct of oven area.

Removal /Dismantling of Complete blower duct (02Nos.) out side of oven area.

Removal/Dismantling of Small Door (02 Nos.) of oven.

Removal/Dismantling of Blower Impeller, Shaft, Hub etc.(Both side Blower).

Removal/Dismantling of Complete Air circulating duct from inside of oven area.

Removal/Dismantling of complete oven Wall panel (all four side).

Removal/Dismantling of all steel structural item from inside of oven and out side area (like Ladder, Railing, platform etc).

2.0	ELECTRICAL ITEMS:

Removal/Dismantling of complete Electric cable, Electric Motor, Panel etc.

3.0	ELECTRIC OPERATED DOOR:

Removal /Dismantling of sliding Shutter with all side panel, sliding cover etc.

Removal/Dismantling of all bent structure connecting with door portion.

4.0	STEAM AND STEAM CONDENSATE PIPELINE:

Removal /Dismantling of all Thermal insulation from the steam & steam condensate pipeline.

Removal/ Dismantling of all steam and steam condensate pipeline size 80NB to 20NB, which connected with oven, steam heated radiator/blower.

NOTE: Carriage of all dismantle material/items within the Block area lead by mechanical transport including, loading, unloading & stacking of material from bay-8 to bay-5 as direction by BHEL Engineer-In charge.

5.0	ERECTION / RE-ASSEMBLING, COMMISSIONING OF WALL PANEL OVEN:

Assembling/Fixing of all shifted structures columns in Bay-5.

Fitting/Fixing/Erection of Oven wall panel with structure column.

Fitting/ Fixing/Assembling of small door with oven.

Fitting/ Fixing/Assembling of Complete blower duct (02Nos.) out side of oven area.

Fitting/ Fixing/Assembling of Small Door (02 Nos.) of oven.

Fitting/ Fixing/Assembling of Blower Impeller, Shaft, Hub etc.(Both side Blower).

Fitting/ Fixing/Assembling of Complete Air circulating duct from inside of oven area.

Fitting/ Fixing/Assembling of complete oven Wall panel (all four side).

Fitting/ Fixing/Assembling of all steel structural item inside and outside of oven area (like Ladder, Railing, platform etc).

6.0	ELECTRICAL ITEMS:

Fitting/ Fixing/Re-Assembling of complete Electric cable, Electric Motor, Panel etc. of drying oven.

7.0	ELECTRIC OPERATED DOOR:

Fitting/ Fixing/Re-Assembling of sliding Shutter with all side panel, sliding cover etc.

Fitting/ Fixing/Re-Assembling of all bent structure connecting with door portion.

Fitting/ Fixing/Re-Assembling of all limit switches of door.

Note: The contractor has to offer the erection, fitting / assembling of parts of drying oven for stage wise inspection to BHEL Engineer-In charge.

8.0	FABRICATION OF NEW DUCT WHEREVER IS DAMAGE:

Fabrication of New MS Duct by 1.5mm Thk MS Sheet with all Branches duct  approx size X 2 side inside of oven wherever is damaged.

Fabrication of MS flange for new Duct.

Fabrication of MS Bend for new Duct

Fabrication MS duct Reducer as per existing size.

Fabrication of New Steel structural support for Fixing of New Duct inside of Oven.

Laying Erection of New Fabricate Duct on Top portion of oven/ on the existing duct with proper fitting Bend, flanges, Structural Supports, Branch duct etc.

Connection of New Duct with new Blower.

Painting of Complete duct with one coat of Red Oxide and one coat of Heat Resistant Aluminum paint with supply of all painting material and labour.

Qty: approx. 300’

9.0	EXTENSION /LAYING OF MAIN STEAM PIPELINE:

Fabrication, Erection & Laying of new overhead (at a height of approx 30 feets) process Steam pipeline as per IBR in TRM block as per attached drawing/sketch for shifted air circulating drying oven 6/B/33.

Fabrication, Erection, Laying and jointing of approx 30 meters, 3” (80NB) size, overhead main CS Seamless Steam pipeline with all pipe fittings (Bend, Tee, Flanges etc.) at Column No. F-10 to F-13 as per attached sketch at a height of 30 feet

Fabrication, Erection, Laying and Jointing of approx 60 meters, 1½” (40NB) size, down take steam pipeline connecting with new laid steam pipeline with all pipe fittings (Bend, Tee, Flanges etc.) supply for steam heated Radiators.

Fabrication & erection of hanging/sliding supports (as per site suitability) and hanging of newly laid steam pipeline with bracings of adjacent columns using these hanging supports. As per IBR standard.

Fabrication, Erection & joining of 03 Nos. Steam trap assembly of ¾”or 1” at the bottom of expansion loops of above newly laid 3” size pipeline.

Note: Development of isometric drawings as per our piping layout plan & actual site condition for IBR approval & approval of the same from IBR authorities shall be contractor’s scope.

10.0) FABRICATION & ERECTION:

Fabrication, erection and testing of the pipeline includes cleaning, cutting edge preparation, alignment,

Welding, machining, grinding, hydro testing, surface preparation, painting, cutting and fitting of gaskets etc.

The erection of piping system includes installation of Isolating valves, drain valves, pressure & temperature Gauge, fittings, flanges, elbows, bends, tees etc. as per drawings attached.

While connecting any piping to any equipment/piping, the contractor shall ensure that the alignment of the Piping is perfect and no stress is transmitted due to any misalignment.

Flange connections: shall be true and perpendicular to the axis of pipe.

Valves shall be installed as per the isometric drawings submitted. Directional valves, check valves, etc shall be fitted according to the direction of fluid flow.

All the codes & standards required for fabrication, erection & testing of process steam piping is to be followed during execution of work.

Welding of the steam pipelines shall be performed by the IBR certified welder.

11.0) PIPE AND VALVE SUPPORTS:

Fabrication & welding of supports of angle channel etc. with existing support structure for pipe support is contractor’s scope. Clamping of pipeline with existing support structure & Fixing of anchor fasteners, wherever required, is also in contractor’s scope.

For the field run piping and valve supports shall be fabricated and installed as per approved drawing at location indicated.

Pipe supports must be made in such a manner that they will not contribute to the over stressing of the line.

Welding in any piping will not be permitted unless otherwise indicated on the approved drawing.

Material for the supports including “C” channel, Angle, Plates etc. will be provided by the BHEL free of cost.

12.0) TESTING & APPROVAL:

Hydrostatic testing of all the newly laid steam pipelines is to be done as per norms. Final hydrostatic testing of the system will not be considered successful until test pressure is maintained without significant drop on

Pressure for a not less than 12 hours. Any failure revealed in the system, test shall be carried out again.

Repairs or replacement of components as directed by site Engineer-In charge.

All the required tests of pipelines are to be performed by the contractor as per IBR rules & IBR requirement.

The contractor shall arrange all equipment, instruments, tools, manpower etc, for and shall carry out the Various tests as required that may be furnished to him during the performance of the work, at his own expense.

13.0	IBR APPROVAL:

Contractor shall carry out the fabrication, erection and testing of this piping as per requirements of Indian Boiler Regulations and to the entire satisfaction of the boiler inspector/IBR authorities.

All IBR approvals from IBR authorities for Fabrication, installation, erection, testing of steam pipeline etc falling under IBR purview shall be obtained by the contractor. All arrangements for organizing IBR inspectors visit and testing etc to be conducted in front of him and final commissioning of the line will be contractor’s scope. All statutory charges& fee to be deposited in boiler inspector’s office/IBR authorities’ office/local authorities’ office for IBR approval shall be borne by the contractor.

Development of Isometric drawing as per our piping layout plan & actual site condition for IBR approval & approval of the same from IBR authorities will be contractor’s scope.

Contractor has to submit approved drawing from IBR authorities before start of work to us.

After Completion of work contractor has to take charging permission of pipelines from IBR authorities / Director of boilers M.P and same is to be submitted to us.

14.0	EXTENSION /LAYING OF STEAM CONDENSATE PIPELINE:

Fabrication, Erection & laying of new overhead (at a height of approx 30 feets) Steam condensate pipeline in TRM block as per attached drawing/sketch for shifted air circulating drying oven 6/B/33.

Fabrication, Erection, Laying and Jointing of approx 30 meters, 3”(80NB) size, Overhead main CS Seamless Steam condensate pipeline with all pipe fittings (Bend, Tee, Flanges etc.) at Column No. F-10 to F-13 as per attached sketch at a height of 30 feet

Fabrication, Erection, Laying and Jointing of approx 60 meters, 1½” (40NB) size, down take steam pipeline connecting with new laid steam pipeline with all pipe fittings (Bend, Tee, Flanges etc.) supply for steam heated Radiators.

Fabrication & erection of hanging/sliding supports (as per site suitability) and hanging of newly laid steam condenser pipeline with bracings of adjacent columns using these hanging supports. As per IBR standard.

Fabrication, Erection & joining of 03 Nos. Steam trap assembly of ¾”or 1” at the bottom of expansion loops of above newly laid 3” size pipeline.

15.0	HYDROSTATIC TESTINGOF RADIATORS & STEAM CONDENSATE PIPELINE:

Hydrostatic testing of all the Radiators and newly laid steam condensate pipelines is to be done as per norms. Final hydrostatic testing of the system will not be considered successful until test pressure is maintained without significant drop on pressure for a not less than 12 hours. Any failure revealed in the system, test shall be carried out again repairs or replacement of components as directed by site Engineer-In charge.

- 16.0	THERMAL INSULATION PIPING WORK:

Thermal Insulation of above newly laid Process Steam pipelines, Steam condensate pipeline of 3” (80 NB), 1½”(40NB) & ¾” (120NB) and thermal insulation of steam trap assembly size ¾” as per below:

Cleaning of all outer surface of steam pipeline to be insulated.

Welding of broken brackets on which rock wool mattresses /LRB pad will be fixed.

Fixing/jointing of aluminum foil on steam pipeline wherever required.

Application/Fixing of rock wool mattresses /LRB Pad on the steam pipeline. (50MM Thk.)

Fixing of rock wool mattresses/LRB Pad by wire mess /stitched with GI wire.

Bending & grooving of aluminum sheet to proper shape and size and fixing with self-tapping screws.

Fixing of water proofing “tar felt” between the sheet overlap/joint securing with metallic "bands wherever required at any height.

Fixing of steel structural supports for fixing of Insulation and aluminum sheet wherever required.

Making all boxes by aluminum sheet for steam pipe line fittings (Bend,

Flanges, Tee, valve etc) Pipeline fittings i.e. flange, valve, Tee etc shall be

Insulated with rock wool insulation clamped to the box to enable removal of

the insulation for any maintenance work.

Cleaning of site after completion of work.

Size: 3” (80NB”) to 20NB (¾”)

QTY.: 150Mtr

10.0 THERMAL INSULATION ON OVEN BLOWER/ BLOWER DUCT:

Cleaning of outer surface of Oven/Blower /Blower duct which to be insulated.

Welding of broken brackets on which Thermal insulation / mattresses /LRB pad to be fixed.

Fixing of Thermal insulation Mattresses /LRB Pad on the all-outer surface of Oven/Blower Duct (100MM Thk.) Density- 100 kg/m3

Fixing of Thermal insulation Mattresses/LRB Pad by wire mess /with GI wire 24 SWG.

Covering of Thermal Insulation mattresses/LRB pad by Aluminum sheet 24SWG and fixing by self-tapping screw.

Fabrication of steel structural supports wherever required. on outer surface of Oven/Blower /Blower Duct.

QTY.: 40 Sq.Mtr

11.0	PAINTING OF COMPLETE OVEN :

Providing of paint material with all painting work in Oven with Synthetic enamels Heat Resistant Aluminum paints of glossy finish as per IS 13183 : 1991 either Asian or Nerolac or Berger or Shalimar should   only be used for painting of above pipelines, Duct and Oven Area.

The Thinner used for mixing of paints must be thinner 111 or equivalent.

The complete length of pipelines, Duct, Oven surface area should be first thoroughly cleaned with wire brush / sand paper so as remove all dust / rust particles from the surface of the pipelines, Duct and Oven Surface before applying the paint.

Apply Red oxide primer wherever needed and making surface ready before painting. Second coat of finish paint is two be done only after 24 hrs of first coat.

Qty. : 1200 Sq. Ft.

12.0	INSTALLATION OF NEW ELECTRI CONTROL PANEL:

Installation of new control panel with all provision in control panel like both side Blower Motor Control Switch, Temperature controller, Door controller switch, Temperature Recorder etc in the new panel. Control panel will be fixed, grouting on base plate nearest the oven with laying of cable work of oven.

Qty- 01 No.

13.0	INSTALLATION OF CONTROL VALVE & TEMPERATURE RECORDER:

Installation of new Temperature control valve in-between Steam Inlet Pipeline (Both blower) with laying of electric/pneumatic supply for control valve system   and installation of Controller recorder system installed with new control panel.

Qty. 02 Nos.

14.0 SUPPLY OF MATERIAL:

Supply of material for Removal/Dismantling, Shifting, Erection, Commissioning and trial Run of Steam heated Drying Oven No. 6/B/33 from Blk-3 Bay-8 to Blk-3 bay-5 TRM Divn.

- Tentative bill of quantity /supply of material are as follows  :

| Sl.No. | Description of Item | Qty. |
| --- | --- | --- |
| 01- | “AIRA” Make WCB Body 2 Way Diaphragm Operated ON-OFF Type Globe Pattern Control Valve Flanged End ANSI B 16.5.150#. with Three Part : 01-ACTUATOR, 02- PRESSURE CONTROL VALVE (CKD MODEL), 03- 3/2 WAY DIRECT ACTING TYPE SINGLE SOLENOID VALVE 220 V AC SIZE : 1½” (40NB) | 02 Nos |
| 02- | Vertical Inverted Bucket Steam Trap Size : ¾”(20NB) End : Screwed d End (IBR) Specification of Trap Materials No. Part Material 1 - Base - Cast Iron (IBR Gr.A) 2- Product Description - Inverted Bucket Trap 3- Trim - Bucket SS (Type 304) 4- End Details - Flanges as per BS 10 Table F 5- Working Pr. - 13Kg/cm2 6- Hyd. Test Pr.t - 26 Kg/cm2 Make : Leader/ Standard | 03 Nos. |
| 03- | CS Seamless Heavy duty ASTM, A106 Gr.B Sch.40, Size : 80NB (3”) as per IBR standard with Test Certificate. Make : ISMT/Maharashtra Seamless | 60 Mtr. |

| Sl.No. | Description of Item | Qty. |
| --- | --- | --- |
| 04- | CS Seamless Heavy duty ASTM, A106 Gr.B Sch.40 Size : 40NB (1½”) as per IBR standard with Test Certificate. Make : ISMT/Maharashtra Seamless | 60 Mtrs. |
| 05- | CS Seamless Heavy duty ASTM, A106 Gr.B Sch.40, Size : 25NB (1”) as per IBR standard with Test Certificate. Make : ISMT/Maharashtra Seamless | 20 Mtr. |
| 06- | Elbow 90Degree, BW : 1.50:B ASTM A234 WBP Size : 40NB (1½”) Sch.40 (IBR) | 10 Nos. |
| 07- | Elbow 90Degree, BW : 1.50:B ASTM A234 WBP Size : 25NB (1”) Sch.40 (IBR) | 20 Nos. |
| 08- | MS Flange 80NB (3”) Confirming to A.S.A.150, with raised face. (IBR) | 10 Nos. |
| 09- | MS Flange 40NB (1½”) Confirming to A.S.A.150, with raised face. (IBR) | 20 Nos. |
| 10- | MS Flange 25NB (1”) Confirming to A.S.A.150, with raised face. (IBR) | 16 Nos. |
| 11- | M.S. HEAVY Duty Slip on Blind Flange #150 Size : 80NB (3”) | 02 Nos. |
| 12- | Bronze Steam Stop Globe Valve With IBR Test certificate Make : Leader/Standard, Size : 40NB (1½”) End : Flange End | 06 Nos. |
| 13- | Bronze Steam Stop Globe Valve With IBR Test certificate Make : Leader/Standard, Size : 25NB (1”) End : Flange End | 03 Nos. |
| 14- | Bronze “Y”-Type Steam Strainer (End : Screwed End) Size : 25NB(1”) With IBR Test Certificate | 03 Nos. |
| 15- | Steam NRV GM as per IS: 778, Class – 2 (End : Screw End) Size : 25NB(1”) With IBR Test Certificate | 03 Nos. |
| 16- | Supply of Electric Control Panel with all cabling work | 01 No. |
| 17- | Supply of 1.5mm Thk MS sheet for fabrication of Repair/ Modification of Duct, Blower Duct and Interconnecting duct & Branches inside of oven with all supporting structural steel work like MS Channel, Angle, Clamp, pipe etc. | 300 Sq. Ft. |
| 18- | THERMAL INSULATION MATERIAL : Thermal Insulation (Glass wool/LRB Pad)-50MM Thk. Aluminum sheet24 SWG Wire mesh Self Tapping screw | 80 Sq.Mtr 80 Sq.Mtr 80 Sq.mtr 2000 Nos. |
| 19- | Supply of Complete Hard Ware items & Steel Support Structure (Nuts, Bolts, Gaskets, Sealing Material, PP Support Clamps etc. | As per required for complete work |

15.0	INSPECTION OF PRE-FABRICATED PIPING:

- 15.1   Pipe work that has been done shall be checked with the drawing/sketch and other related documents to very that is as fabricated complies with dimensions and specification. Tacks should be equally spaced as follows:

- a)       For 2.5” NB Pipe and smaller -2 tacks

- b)      For 3” NB to 12”NB pipe - 4 Tacks

- c)       Welders and welding procedures shall be qualified in accordance with the requirements of the codes and IS-817. 1966. Horizontal and / Or Vertical welding qualification shall be shown on qualifications papers.

- d)   All welding shall have full thickness penetration and shall be done by electric arc process. The initial root runs of all but welds shall be carried out with electrodes not exceeding 12SWG. In case of SS, root shall be done by argon arc.

- e)   In multiple pass welding the slag shall be cleaned from each layer and any serious defects chipped out before the next layer is applied. Penning shall be done if necessary to prepare a bead for the next pass.

- f)   The completed weld shall be cleaned of slag and spatter metal on all surfaces, and when possible the inside bead should be ground smooth.

- g)    No undercutting of pipe adjacent to the completed weld should be permitted.

h)   Finished welds shall project not less than 1.5 mm but not more than 3 mm from the outer surface of the pipe

i)  The contractor has to offer the job for stage wise inspection to BHEL Engineer-In charge

16.0	ELECTRODE:

- a) Welding electrodes used for carbon steel piping work shall be in accordance with IS 6013 and of high quality from reputed manufacturers. (ESAB/ADVANI/D&H).

- Welding electrodes used for stainless steel piping works shall be of high quality tungsten from EWIL (eutectic welding)/advani orlikon suitable for inert gas and manual arc process. Chemical properties of electrodes shall be

- Equivalent / better than the pipes to be joined.

- 17.0 FABRICATION & ERECTION:

Fabrication, erection and testing of the pipeline includes cleaning, cutting edge preparation, alignment, welding, machining, grinding, hydro testing, surface preparation, painting, cutting and fitting of gaskets etc.

The erection of piping system includes installation of Isolating valves, drain valves, pressure & temperature Gauge, fittings, elbows, bends, tees etc. as per drawings attached.

While connecting any piping to any equipment/piping, the contractor shall ensure that the alignment of the piping is perfect and no stress is transmitted due to any misalignment.

- 18.0 Note:-

- (a) All Pipes, Pipe Fittings, Flanges, Valves Material of above work is to be provided by the contractor.

- (b) All required paints, primer & painting brush for painting, Hardware, Structural material of above pipeline is to be provided by the contractor.

- (c) Welding Machine, Gas cutting set and all consumables like welding electrode, cutting gas etc. is in the scope of contractor. However basic facilities like Electricity, Air & Water , Crane, Lifter, Truck will be provided by BHEL free of cost.

19.0 WORKING AT HEIGHT

The contractor shall obtain ‘Permit for working at height’ containing a checklist of the safety measures to be adopted by the contractors.

Contractor are responsible for ensuring that their workmen while working overhead and at heights, hookup their safety harness with permanent structure only.

While working at height, safety net is to be used wherever feasible.

- Erection /Assembling of the electrical and mechanical equipment shall be carried out as per existing plant. Proper care of material / items shall be taken so that no chance of damaged due to faulty or careless dismantling and erection procedure. The BHEL decision shall be final regarding any damage due to wrong dismantling or faulty erection procedure and the entire cost of replacement of the damaged part shall be borne by the Contractor.

- Party shall have to complete total job within the time schedule.

- Supervision of erection, testing and commissioning of Plant / equipments.

- The items shall have guarantee/ warrantee against defective materials, bad workmen ship for a period of 12 months from the date of commissioning.

- The contractor shall ensure erection and commissioning of the Air Circulating Oven complete in all respect and any work not covered in this specification but essential for completion of work shall be included in the scope of the contractor.

- After completion of the work, the party shall promptly remove from the premises everything brought in by him and shall leave the premises in an acceptable clean condition.

- Contractor are advised to visit Plant/ site before quoting so that they are acquainted with site conditions and requirements.