## ScheduleElec
SCH | SWBD | CABLE CODE | BOQ | CABLE NO | FROM | TO | CABLE DETAILS | LENGTH | LAYING | LENGTH | DRUM | TERMINATION | PLAN | PURPOSE | REMARK | SCHEDULE | ACTUAL
SL |  | CMS | PTX |  |  |  |  | DRG | DATE | ACTUAL | NO | STATUS |  |  |  | CABLE ROUTE | CABLE ROUTE | FROM | TO
1 | 1FA | E04V0.5 | 10.7.02 | 1FA01BC01 | 220V CHARGER-1A | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 54 | 61 | 30.11.2019 | DR0720_4798-4G-83 |  |  | CHARGER-1A OVERLOAD, CHARGER-1A TROUBLE, BATTERY-1A ON BOOST | OVERALL SCREENED | LV07-L3, LV76-06, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
2 | 1FA | E02W0.5 | 10.8.01 | 1FA01BC02 | 220V CHARGER-1A | DDCMIS # CRE66 | 02P X 0.5 Paired Screened(I) ( 225 V ) | 54 | [5 empty] | CHARGER-1A CURRENT & VOLTAGE MEASUREMENT | INDIVIDUAL & OVERALL SCREENED | LV07-L3, LV76-06, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
3 | 1FA | D01Q400 | 10.4.04 | 1FA01BP01 | 220V SWGR I/C MODULE # 1FA01FB | FCBC-1A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 29 | 30 | 05.09.2019 | DR1006_0003 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV10-R1, LV49-02, LV07-L1, ZZ99- |  | EPD | PEM
4 | 1FA | D01Q400 | 10.4.04 | 1FA01BP02 | 220V SWGR I/C MODULE # 1FA01FB | FCBC-1A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 29 | 30 | 05.09.2019 | DR1006_0003 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV10-R1, LV49-02, LV07-L1, ZZ99- |  | EPD | PEM
5 | 1FA | E04V0.5 | 10.7.02 | 1FA01QC01 | 220V CHARGER-1A (FUSE BOX) | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 62 | 30.11.2019 | DR0720_4798-4G-83 |  |  | BATTERY-1A FUSE FAILURE | OVERALL SCREENED | DR02-02, DC06-02, DC05-02, DC04-02, DC03-02, DC02-02, DC01-02, LV80-02, LV25-R3, LV74-04, LR07-02, CC90-02, CC81-02, CC31-01, CC67-04, CC68-02, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
| 1FA | E04V0.5 | 10.7.02 | 1FA03FC01 | 220V SWGR I/C MODULE # 1FA3FA | FCBC-01A | 04P X 0.5 Paired Screened(O) ( 225 V ) | 30 | 35 | 25.10.2019 | DR0720_4798-4G-82
6 | 1FA | D01Q630 | 10.4.05 | 1FA01QP01 | 220V SWGR I/C MODULE # 1FA01RC | BAT FUSE BOX-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 41 | 48 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV10-L1, LV43-01, LV24-R1, LV80-01, DC01-01, DC02-01, DC03-01, DC04-01, DC05-01, DC06-01, DR02-01, ZZ99- |  | EPD | PEM
7 | 1FA | D01Q630 | 10.4.05 | 1FA01QP02 | 220V SWGR I/C MODULE # 1FA01RC | BAT FUSE BOX-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 42 | 48 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV10-R1, LV43-01, LV24-R1, LV80-01, DC01-01, DC02-01, DC03-01, DC04-01, DC05-01, DC06-01, DR02-01, ZZ99- |  | EPD | PEM
8 | 1FA | D01Q630 | 10.4.05 | 1FA01QP03 | 220V SWGR I/C MODULE # 1FA01RC | BAT FUSE BOX-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 42 | 48 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV10-R1, LV43-01, LV24-R1, LV80-01, DC01-01, DC02-01, DC03-01, DC04-01, DC05-01, DC06-01, DR02-01, ZZ99- |  | EPD | PEM
9 | 1FA | D01Q630 | 10.4.05 | 1FA01QP04 | 220V SWGR I/C MODULE # 1FA01RC | BAT FUSE BOX-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 42 | 48 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV10-R1, LV43-01, LV24-R1, LV80-01, DC01-01, DC02-01, DC03-01, DC04-01, DC05-01, DC06-01, DR02-01, ZZ99- |  | EPD | PEM
9 | 1FA | D01Q630 | 10.4.05 | 1FA FB01 P01 | BAT FUSE BOX-1A | BATTERY-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 15 | 28.11.2019 | DR1050_0011
9 | 1FA | D01Q630 | 10.4.05 | 1FA FB01 P02 | BAT FUSE BOX-1A | BATTERY-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 15 | 28.11.2019 | DR1050_0011
9 | 1FA | D01Q630 | 10.4.05 | 1FA FB01 P03 | BAT FUSE BOX-1A | BATTERY-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 16 | 28.11.2019 | DR1050_0011
9 | 1FA | D01Q630 | 10.4.05 | 1FA FB01 P04 | BAT FUSE BOX-1A | BATTERY-1A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 16 | 28.11.2019 | DR1050_0011
10 | 1FA | D02L2.5 | 10.4.24 | 1FA02PP01 | 220V SWGR O/G MODULE # 1FA02RB | SEQUENCE TRIMMING DEVICE | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | POWER SUPPLY (0.042kW) | XLPE-CU UNARMOURED | LV10-L4, LV11-L4, LV12-L4, LV58-02, LV04-L4, LV64-05, TR25-05, TP55-02, TP56-02, TP57-02, ZZ99- |  | EPD | PEM
11 | 1FA | D02L2.5 | 10.4.24 | 1FA02SP01 | 220V SWGR O/G MODULE # 1FA02RE | ERV LOCAL CONTROLLER BOX | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (0.3kW) | XLPE-CU UNARMOURED | LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BR68-02, ZZ99- |  | EPD | PEM
12 | 1FA | D02Q010 | 10.4.06 | 1FA02TP01 | 220V SWGR O/G MODULE # 1FA02RF | AVR PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 38 | 50 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV10-L1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01, CC50-01 |  | EPD | EDN
13 | 1FA | D02Q025 | 10.4.07 | 1FA02UP01 | 220V SWGR O/G MODULE # 1FA02RG | 6.6KV STATION SWBD # 0CA | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV10-L1, LV11-L3, LV12-L2, LV13-L2, LV63-02, LV64-03, TR48-03, MR16-02, MV99-02, MV98-02, MV97-02, MV96-02, MV95-01, MV38-01, ZZ99- |  | EPD | BPL
14 | 1FA | D02Q010 | 10.4.06 | 1FA02VP01 | 220V SWGR O/G MODULE # 1FA02RH | UNIT PMCC # 1DA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 54 | 65 | 12.09.2019 | DR0816_0002 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV10-R1, LV44-01, LV76-01, MR10-03, MA05-01, MV68-01, MV67-01, MV66-01, MV65-03, MV64-03, MV63-04, ZZ99- |  | EPD | EPD
15 | 1FA | E04V0.5 | 10.7.02 | 1FA03BC01 | 220V SWGR BUS PT MODULE # 1FA03FB | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 56 | 64 | 30.11.2019 | DR0720_4798-4G-83 |  |  | U/V, O/V, E/F | OVERALL SCREENED | LV10-R4, LV43-04, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC35-03, CC59-05, CC39-03 |  | EPD | EDN
16 | 1FA | D02Q010 | 10.4.06 | 1FA03CP01 | 220V SWGR O/G MODULE # 1FA03FC | BOP PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV10-L1, LV43-01, LV24-L1, LV75-01, LR06-01, ZZ99- |  | EPD | EDN
17 | 1FA | D02Q025 | 10.4.07 | 1FA03DP01 | 220V SWGR O/G MODULE # 1FA03FD | 6.6KV COMP. SWBD # 1CC | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV10-L1, LV11-L2, LV12-L2, LV58-01, LV04-L1, LV03-L1, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, CM07-R1, CM08-R1, ZZ99- |  | EPD | BPL
18 | 1FA | D02Q025 | 10.4.07 | 1FA03EP01 | 220V SWGR O/G MODULE # 1FA03FE | BREAKER PANEL FOR ID FAN-1A | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 294 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV10-L1, LV43-01, LV42-01, LV41-01, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES96-02, ES16-02, ES26-R1, ES25-R1, ES24-R2, ES23-R2, ES22-R1, ZZ99- |  | EPD | BPL
19 | 1FA | D02Q010 | 10.4.06 | 1FA03HP01 | 220V SWGR O/G MODULE # 1FA03FH | DATA CONCENTRATOR (HT & LT) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV10-L1, LV43-01, LV24-L1, LV75-01, LR06-01, CC91-01, CC83-01, CC93-01, CC34-01, CC35-01 |  | EPD | BPL
20 | 1FA | D01Q400 | 10.4.04 | 1FA03NP01 | 220V SWGR O/G MODULE # 1FA03RA | JACKING OIL PUMP-2 (MAV32AP001) | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 78 | 89 | 02.03.20 | DR0968_0009 |  |  | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | LV10-L1, LV11-L1, LV12-L2, LV58-01, LV04-L1, LV64-02, TR48-02, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, ZZ99- |  | EPD | HWR
21 | 1FA | D01Q400 | 10.4.04 | 1FA03NP02 | 220V SWGR O/G MODULE # 1FA03RA | JACKING OIL PUMP-2 (MAV32AP001) | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 78 | 90 | 02.03.20 | DR0968_0009 |  |  | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | LV10-L1, LV11-L1, LV12-L2, LV58-01, LV04-L1, LV64-02, TR48-02, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, ZZ99- |  | EPD | HWR
22 | 1FA | D02Q095 | 10.4.09 | 1FA03QP01 | 220V SWGR O/G MODULE # 1FA03RC | FEEDER TO LDB - TGB MV SWGR ROOM (1UH) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV10-L1, LV11-L1, LV12-L2, LV58-01, LV04-L1, LV64-02, TR48-02, MR16-02, MV99-02, MV98-02, MV97-02, MV96-02, MV95-01, MV37-01, ZZ99- |  | EPD | EPD
23 | 1FA | D02Q095 | 10.4.09 | 1FA03QP02 | 220V SWGR O/G MODULE # 1FA03RC | FEEDER TO LDB - TGB MV SWGR ROOM (1UH) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV10-L1, LV11-L1, LV12-L2, LV58-01, LV04-L1, LV64-02, TR48-02, MR16-02, MV99-02, MV98-02, MV97-02, MV96-02, MV95-01, MV37-01, ZZ99- |  | EPD | EPD
24 | 1FA | D02L2.5 | 10.4.24 | 1FA03RP01 | 220V SWGR O/G MODULE # 1FA03RD | ERV LOCAL CONTROLLER BOX | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (0.3kW) | XLPE-CU UNARMOURED | LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BR68-02, ZZ99- |  | EPD | PEM
25 | 1FA | D02Q010 | 10.4.06 | 1FA03SP01 | 220V SWGR O/G MODULE # 1FA03RE | STN PMCC # 0DA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 62 | 78 | 12.09.2019 | DR0816_0002 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV10-L1, LV44-01, LV76-01, MR10-03, MA05-01, MV68-01, MV67-01, MV66-01, MV65-03, MV64-03, MV48-01, MV49-01, ZZ99- |  | EPD | EPD
26 | 1FA | D02Q010 | 10.4.06 | 1FA03UP01 | 220V SWGR O/G MODULE # 1FA03RG | GRP-1 | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | 46 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV10-L1, LV44-01, LV76-01, LR05-03, CC92-01, CC89-01, CC51-01 |  | EPD | BPL
27 | 1FA | D02Q095 | 10.4.09 | 1FA04CP01 | 220V SWGR O/G MODULE # 1FA04FC | DC SEAL OIL PUMP (MKW13AP001) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 131 | [5 empty] | POWER SUPPLY (8.5kW) | XLPE-AL UNARMOURED | LV11-L1, LV10-L1, LV44-01, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG31-01, TR06-01, TG32-01, TG33-01, ZZ99- |  | EPD | HWR
28 | 1FA | D02Q025 | 10.4.07 | 1FA04DP01 | 220V SWGR O/G MODULE # 1FA04FD | BREAKER PANEL FOR ID FAN-1B | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 297 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-R2, LV48-02, LV47-01, LV46-02, LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES96-02, ES16-02, ES26-R1, ES25-R1, ES24-R2, ES23-R2, ZZ99- |  | EPD | BPL
29 | 1FA | D02Q010 | 10.4.06 | 1FA04EP01 | 220V SWGR O/G MODULE # 1FA04FE | UNIT EMER. MCC # 1DG | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 34 | 43 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R1, LV48-02, LV47-02, LV46-02, LV38-L3, LV39-L1, ZZ99- |  | EPD | EPD
30 | 1FA | D02Q010 | 10.4.06 | 1FA04FP01 | 220V SWGR O/G MODULE # 1FA04FF | BOILER MCC # 1HA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 20 | 25 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV13-L2, ZZ99- |  | EPD | EPD
31 | 1FA | D02Q095 | 10.4.09 | 1FA04GP01 | 220V SWGR O/G MODULE # 1FA04FG | FEEDER TO LDB - TGB LV SWGR ROOM (1UJ) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV11-L1, LV12-L2, LV57-01, LV56-02, LV31-L1, ZZ99- |  | EPD | EPD
32 | 1FA | D02Q095 | 10.4.09 | 1FA04GP02 | 220V SWGR O/G MODULE # 1FA04FG | FEEDER TO LDB - TGB LV SWGR ROOM (1UJ) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV11-L1, LV12-L2, LV57-02, LV56-02, LV31-L1, ZZ99- |  | EPD | EPD
33 | 1FA | D02Q010 | 10.4.06 | 1FA04HP01 | 220V SWGR O/G MODULE # 1FA04FH | SUPPLY FOR ELECTRONIC MODULE | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EDN
34 | 1FA | D02Q095 | 10.4.09 | 1FA04PP01 | 220V SWGR O/G MODULE # 1FA04RB | DC FUSE DB #01 ESP CR 3.5MTR | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 314 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV11-L1, LV48-02, LV47-01, LV46-02, LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES02-02, ES30-02, ER01-02, ZZ99- |  | EPD | EPD
35 | 1FA | D02Q025 | 10.4.07 | 1FA04QP01 | 220V SWGR O/G MODULE # 1FA04RC | GCB # 1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 146 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV58-01, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TP18-01, TP19-01, TP22-01, TP27-01, TP28-01, TP29-01, TP30-01, TP31-01, TP32-01, TP33-01, ZZ99- |  | EPD | PEM
36 | 1FA | D02Q025 | 10.4.07 | 1FA04TP01 | 220V SWGR O/G MODULE # 1FA04RF | BREAKER PANEL FOR CEP-1A | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 31 | 51 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV48-02, LV47-02, LV29-L2, ZZ99- |  | EPD | BPL
37 | 1FA | D02Q095 | 10.4.09 | 1FA04UP01 | 220V SWGR O/G MODULE # 1FA04RG | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 311 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV11-L1, LV48-02, LV47-02, LV46-02, LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES02-02, ES30-02, ER01-02, ZZ99- |  | EPD | EPD
38 | 1FA | D02Q010 | 10.4.06 | 1FA04VP01 | 220V SWGR O/G MODULE # 1FA04RH | ECP | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV10-L1, LV44-01, LV76-01, LR05-01, ZZ99- |  | EPD | EDN
39 | 1FA | D02Q095 | 10.4.09 | 1FA05BP01 | 220V SWGR O/G MODULE # 1FA05FB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 486 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV11-L1, LV48-02, LV47-02, LV46-02, LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-02, IM28-02, IM29-02, IM30-02, IM31-02, IR37-02, IL01-02, IL02-02, IL03-02, IL04-02, IL05-02, IL06-02, IL07-02, IL08-02, IL09-02, PR01-02, ET01-L1, ET02-L1, ET09-01, ZZ99- |  | EPD | EPD
40 | 1FA | D02Q095 | 10.4.09 | 1FA05CP01 | 220V SWGR O/G MODULE # 1FA05FC | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 486 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV11-L1, LV48-02, LV47-02, LV46-02, LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-02, IM28-02, IM29-02, IM30-02, IM31-02, IR37-02, IL01-02, IL02-02, IL03-02, IL04-02, IL05-02, IL06-02, IL07-02, IL08-02, IL09-02, PR01-02, ET01-L1, ET02-L1, ET09-01, ZZ99- |  | EPD | EPD
41 | 1FA | D02Q025 | 10.4.07 | 1FA05DP01 | 220V SWGR O/G MODULE # 1FA05FD | 6.6KV UNIT SWBD # 1CA | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 45 | 53 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV58-01, LV04-L1, LV64-03, TR48-03, MR16-02, MV99-02, MV02-L2, ZZ99- |  | EPD | BPL
42 | 1FA | D02Q025 | 10.4.07 | 1FA05FP01 | 220V SWGR O/G MODULE # 1FA05FF | 6.6KV UNIT SWBD # 1CB | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 49 | 57 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV57-02, LV20-R1, LV19-R1, LV18-R1, LV71-02, MR02-02, MA01-02, MV34-L2, ZZ99- |  | EPD | BPL
43 | 1FA | D02Q025 | 10.4.07 | 1FA05GP01 | 220V SWGR O/G MODULE # 1FA05FG | BREAKER PANEL FOR CEP-1B | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 31 | 48 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV48-02, LV47-02, LV29-L2, ZZ99- |  | EPD | BPL
44 | 1FA | D02L2.5 | 10.4.24 | 1FA05HP01 | 220V SWGR O/G MODULE # 1FA05FH | ERV LOCAL CONTROLLER BOX | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | POWER SUPPLY (0.3kW) | XLPE-CU UNARMOURED | LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BR68-02, ZZ99- |  | EPD | PEM
45 | 1FA | D02Q010 | 10.4.06 | 1FA05PP01 | 220V SWGR O/G MODULE # 1FA05RB | TURBINE MCC # 1KA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 28 | 46 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
46 | 1FA | D02Q010 | 10.4.06 | 1FA05QP01 | 220V SWGR O/G MODULE # 1FA05RC | VENTILATION & AIR WASHER MCC # 1TA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 75 | 68 | 12.09.2019 | DR0816_0002 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV10-L1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ13-01, BQ12-01, ZZ99- |  | EPD | EPD
47 | 1FA | D02Q010 | 10.4.06 | 1FA05RP01 | 220V SWGR O/G MODULE # 1FA05RD | A/C MCC # 0TA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | 80 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV48-02, LV23-L1, LV24-L1, LV25-L1, LV74-02, DC07-03, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, AC13-01, DR07-01, AC14-L1, AC15-L1, AC16-L1, AC17-L1, AC18-L1 |  | EPD | EPD
48 | 1FA | D02Q010 | 10.4.06 | 1FA05TP01 | 220V SWGR O/G MODULE # 1FA05RF | MISC SERVICE MCC # 0SA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 27 | 41 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV48-02, LV23-L1, ZZ99- |  | EPD | EPD
49 | 1FA | D02Q010 | 10.4.06 | 1FA05UP01 | 220V SWGR O/G MODULE # 1FA05RG | ST # 1 MARSHALLING BOX | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV57-02, LV20-R1, LV19-R1, LV18-R1, LV71-02, LR02-02, TY15-R1, TY16-R2, TY17-R2, TY18-R2, YR02-02, TY25-02, TY26-02, TY27-01, ZZ99- |  | EPD | JHS
50 | 1FA | D02Q010 | 10.4.06 | 1FA05VP01 | 220V SWGR O/G MODULE # 1FA05RH | UT # 1A MARSHALLING BOX | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV13-L2, LV14-L1, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY09-01, TY10-01, ZZ99- |  | EPD | JHS
51 | 1FA | D02Q095 | 10.4.09 | 1FA06BP01 | 220V SWGR O/G MODULE # 1FA06FB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 301 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV11-L1, LV12-L2, LV57-02, LV20-R1, LV19-R1, LV18-R1, LV71-02, LR02-02, TY15-R1, TY16-R2, TY17-R2, TY18-R2, TY19-R2, IP01-R3, IP02-R3, IR03-R2, IP14-L2, IP15-R2, IP16-R2, IP17-R2, IP18-R2, IP19-R2, IR38-R2, IP23-R2, IP24-R2, IP25-R2, IP26-R2, IP27-L3, IP28-L2, IP29-L2, IP30-L2, IP31-L2, IP32-L2, IP33-L3, IP34-L2, IP35-L1, HR01-L1, CT01-L1, ZZ99- |  | EPD | EPD
52 | 1FA | D02Q095 | 10.4.09 | 1FA06CP01 | 220V SWGR O/G MODULE # 1FA06FC | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 301 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV11-L1, LV12-L2, LV57-02, LV20-R1, LV19-R1, LV18-R1, LV71-02, LR02-02, TY15-R1, TY16-R2, TY17-R2, TY18-R2, TY19-R2, IP01-R3, IP02-R3, IR03-R2, IP14-L2, IP15-R2, IP16-R2, IP17-R2, IP18-R2, IP19-R2, IR38-R2, IP23-R2, IP24-R2, IP25-R2, IP26-R2, IP27-L3, IP28-L2, IP29-L2, IP30-L2, IP31-L2, IP32-L2, IP33-L3, IP34-L2, IP35-L1, HR01-L1, CT01-L1, ZZ99- |  | EPD | EPD
53 | 1FA | D02Q095 | 10.4.09 | 1FA06DP01 | 220V SWGR O/G MODULE # 1FA06FD | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
54 | 1FA | D02Q095 | 10.4.09 | 1FA06EP01 | 220V SWGR O/G MODULE # 1FA06FE | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
55 | 1FA | D02Q095 | 10.4.09 | 1FA06PP01 | 220V SWGR O/G MODULE # 1FA06RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
56 | 1FA | D02Q095 | 10.4.09 | 1FA06QP01 | 220V SWGR O/G MODULE # 1FA06RC | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
57 | 1FA | E02W0.5 | 10.8.01 | 1FA07AC01 | 220V SWGR B/C MODULE # 1FA07FA | DDCMIS # CRE66 | 02P X 0.5 Paired Screened(I) ( 225 V ) | 66 | [5 empty] | BUS-B & BUS-C VOLTAGE MEAS. | INDIVIDUAL & OVERALL SCREENED | LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
58 | 1FA | D02Q010 | 10.4.06 | 1FA07CP01 | 220V SWGR O/G MODULE # 1FA07FC | FSSS PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R1, LV48-02, LV47-02, LV46-02, LV38-L3, LV39-L1, LV73-02, LR08-02, ZZ99- |  | EPD | EDN
59 | 1FA | D02Q010 | 10.4.06 | 1FA07UP01 | 220V SWGR O/G MODULE # 1FA07RG | BTS-1 1CA - 0CA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | 61 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R1, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01, CC50-01, CC61-01 |  | EPD | BPL
59A | 1FA | D02Q010 | 10.4.06 | 1FA07VP01 | 220V SWGR O/G MODULE # 1FA07RH | BTS-2 1CB - 0CA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | 61 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R1, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01, CC50-01, CC61-01 |  | EPD | BPL
60 | 1FA | D02Q010 | 10.4.06 | 1FA08FP01 | 220V SWGR O/G MODULE # 1FA08FE | BTS-1 1CA - 0CA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | 61 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R1, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01, CC50-01, CC61-01 |  | EPD | BPL
61 | 1FA | D02Q095 | 10.4.09 | 1FA08QP01 | 220V SWGR O/G MODULE # 1FA08RC | DC FUSE DB #02 ESP CR 3.5MTR | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
62 | 1FA | D02Q095 | 10.4.09 | 1FA08RP01 | 220V SWGR O/G MODULE # 1FA08RD | FEEDER TO LDB - TGB LV SWGR ROOM (1UJ) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV11-R1, LV12-R1, LV57-02, LV20-L2, LV61-01, LV31-L1, ZZ99- |  | EPD | EPD
63 | 1FA | D02Q095 | 10.4.09 | 1FA08RP02 | 220V SWGR O/G MODULE # 1FA08RD | FEEDER TO LDB - TGB LV SWGR ROOM (1UJ) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV11-R1, LV12-R1, LV57-02, LV20-L2, LV61-01, LV31-L1, ZZ99- |  | EPD | EPD
64 | 1FA | D02Q095 | 10.4.09 | 1FA09BP01 | 220V SWGR O/G MODULE # 1FA09FB | EMERG. OIL PUMP-1 (MAV24AP001) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 66 | 82 | 43892 | DR0822_0002 |  |  | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV11-R1, LV12-R1, LV13-R1, LV63-02, LV64-03, TR48-03, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, ZZ99- |  | EPD | HWR
65 | 1FA | D02Q095 | 10.4.09 | 1FA09BP02 | 220V SWGR O/G MODULE # 1FA09FB | EMERG. OIL PUMP-1 (MAV24AP001) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 66 | 82 | 43892 | DR0822_0002 |  |  | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV11-R1, LV12-R1, LV13-R1, LV63-02, LV64-03, TR48-03, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, ZZ99- |  | EPD | HWR
66 | 1FA | D02Q010 | 10.4.06 | 1FA09DP01 | 220V SWGR O/G MODULE # 1FA09FD | FSSS PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 61 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-L2, LV48-02, LV47-02, LV46-02, LV38-L3, LV39-L1, LV73-02, LR08-02, CC01-02, CC73-01, ZZ99- |  | EPD | EDN
60A | 1FA | D02Q010 | 10.4.06 | 1FA08GP01 | 220V SWGR O/G MODULE # 1FA08FF | BTS-2 1CB - 0CA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | 61 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R1, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01, CC50-01, CC61-01 |  | EPD | BPL
67 | 1FA | D02Q010 | 10.4.06 | 1FA09FP01 | 220V SWGR O/G MODULE # 1FA09FF | MISC SERVICE MCC # 0SA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 22 | 44 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV12-R1, LV57-02, LV21-R1, ZZ99- |  | EPD | EPD
68 | 1FA | D02Q095 | 10.4.09 | 1FA09GP01 | 220V SWGR O/G MODULE # 1FA09FG | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
69 | 1FA | D02Q025 | 10.4.07 | 1FA09HP01 | 220V SWGR O/G MODULE # 1FA09FH | BREAKER PANEL FOR ID FAN-1A | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 301 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-R2, LV48-02, LV47-02, LV46-02, LV38-R1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES96-02, ES16-02, ES26-R1, ES25-R1, ES24-R2, ES23-R2, ES22-R1, ZZ99- |  | EPD | BPL
70 | 1FA | D02Q095 | 10.4.09 | 1FA09PP01 | 220V SWGR O/G MODULE # 1FA09RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
71 | 1FA | D02Q025 | 10.4.07 | 1FA09QP01 | 220V SWGR O/G MODULE # 1FA09RC | BREAKER PANEL FOR ID FAN-1B | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 295 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-R2, LV48-02, LV47-02, LV46-02, LV38-R1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES96-02, ES16-02, ES26-R1, ES25-R1, ES24-R2, ES23-R2, ZZ99- |  | EPD | BPL
72 | 1FA | D02Q010 | 10.4.06 | 1FA09RP01 | 220V SWGR O/G MODULE # 1FA09RD | VENTILATION & AIR WASHER MCC # 1TA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 76 | 68 | 12.09.2019 | DR0816_0002 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ13-01, BQ12-01, ZZ99- |  | EPD | EPD
73 | 1FA | D02Q010 | 10.4.06 | 1FA09SP01 | 220V SWGR O/G MODULE # 1FA09RE | TURBINE MCC # 1KA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 29 | 46 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV49-01, LV06-R1, ZZ99- |  | EPD | EPD
74 | 1FA | D02Q010 | 10.4.06 | 1FA09UP01 | 220V SWGR O/G MODULE # 1FA09RG | GT # 1 MARSHALLING BOX | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 140 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV12-R1, LV13-R1, LV14-R1, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-01, TY04-01, TY05-01, TY06-01, TY07-01, ZZ99- |  | EPD | BPL
75 | 1FA | D02Q025 | 10.4.07 | 1FA09VP01 | 220V SWGR O/G MODULE # 1FA09RH | BREAKER PANEL FOR CEP-1A | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 31 | 56 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV48-02, LV47-02, LV29-L2, ZZ99- |  | EPD | BPL
76 | 1FA | D02Q010 | 10.4.06 | 1FA09WP01 | 220V SWGR O/G MODULE # 1FA09RI | BOILER MCC # 1HA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 26 | 23 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV12-R1, LV13-R1, LV14-R1, LV15-R1, ZZ99- |  | EPD | EPD
77 | 1FA | D02Q095 | 10.4.09 | 1FA10AP01 | 220V SWGR O/G MODULE # 1FA10FA | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
78 | 1FA | D02Q010 | 10.4.06 | 1FA10CP01 | 220V SWGR O/G MODULE # 1FA10FC | UNIT EMER. MCC # 1DG | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | 49 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV48-02, LV47-02, LV46-02, LV37-L2, ZZ99- |  | EPD | EPD
79 | 1FA | D02Q010 | 10.4.06 | 1FA10DP01 | 220V SWGR O/G MODULE # 1FA10FD | ECP | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV10-R1, LV44-01, LV76-01, LR05-01, ZZ99- |  | EPD | EDN
80 | 1FA | D02Q010 | 10.4.06 | 1FA10FP01 | 220V SWGR O/G MODULE # 1FA10FF | STN PMCC # 0DA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 69 | 88 | 12.09.2019 | DR0816_0002 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV12-R1, LV13-R1, LV63-02, LV64-02, TR48-03, MR16-02, MV99-02, MV98-02, MV97-02, MV96-02, MV95-01, MV94-01, MV51-01, ZZ99- |  | EPD | EPD
81 | 1FA | D02Q010 | 10.4.06 | 1FA10HP01 | 220V SWGR O/G MODULE # 1FA10FH | DATA CONCENTRATOR (HT & LT) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV48-02, LV23-L1, LV24-L1, LV75-01, LR06-01, CC91-01, CC83-01, CC93-01, CC34-01, CC35-01 |  | EPD | BPL
82 | 1FA | D02Q010 | 10.4.06 | 1FA10IP01 | 220V SWGR O/G MODULE # 1FA10FI | BOP PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV48-02, LV23-L1, LV24-L1, LV75-01, LR06-01, ZZ99- |  | EPD | EDN
83 | 1FA | D02Q095 | 10.4.09 | 1FA10PP01 | 220V SWGR O/G MODULE # 1FA10RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
84 | 1FA | D02L2.5 | 10.4.24 | 1FA10SP01 | 220V SWGR O/G MODULE # 1FA10RE | ERV LOCAL CONTROLLER BOX | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (0.3kW) | XLPE-CU UNARMOURED | LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, ZZ99- |  | EPD | PEM
85 | 1FA | D02Q025 | 10.4.07 | 1FA10VP01 | 220V SWGR O/G MODULE # 1FA10RH | 6.6KV COMP. SWBD # 1CC | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 166 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV13-L2, LV14-L1, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, ZZ99- |  | EPD | BPL
86 | 1FA | D02Q095 | 10.4.09 | 1FA11AP01 | 220V SWGR O/G MODULE # 1FA11FA | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
87 | 1FA | D02Q095 | 10.4.09 | 1FA11EP01 | 220V SWGR O/G MODULE # 1FA11FE | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
88 | 1FA | D02Q095 | 10.4.09 | 1FA11FP01 | 220V SWGR O/G MODULE # 1FA11FF | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
89 | 1FA | E04V0.5 | 10.7.02 | 1FA11GC01 | 220V SWGR BUS PT MODULE # 1FA11FG | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | 72 | 30.11.2019 | DR0720_4798-4G-83 |  |  | U/V, O/V, E/F | OVERALL SCREENED | LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
90 | 1FA | D02Q095 | 10.4.09 | 1FA11PP01 | 220V SWGR O/G MODULE # 1FA11RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
91 | 1FA | D02Q025 | 10.4.07 | 1FA11RP01 | 220V SWGR O/G MODULE # 1FA11RD | BREAKER PANEL FOR CEP-1B | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 31 | 52 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV48-02, LV47-02, LV29-L2, ZZ99- |  | EPD | BPL
92 | 1FA | D02Q010 | 10.4.06 | 1FA11TP01 | 220V SWGR O/G MODULE # 1FA11RF | UT # 1B MARSHALLING BOX | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 108 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV12-R1, LV13-R1, LV14-R1, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY08-01, ZZ99- |  | EPD | JHS
93 | 1FA | D02Q025 | 10.4.07 | 1FA11UP01 | 220V SWGR O/G MODULE # 1FA11RG | GCB # 1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 146 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV58-01, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TP18-01, TP19-01, TP22-01, TP27-01, TP28-01, TP29-01, TP30-01, TP31-01, TP32-01, TP33-01, ZZ99- |  | EPD | PEM
94 | 1FA | D02Q095 | 10.4.09 | 1FA11VP01 | 220V SWGR O/G MODULE # 1FA11RH | SCANNER AIR FAN DC MOTOR STARTER BOX | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 82 | 82 | 43891 | DR0822_0002 |  |  | POWER SUPPLY (10kW) | XLPE-AL UNARMOURED | LV11-R1, LV10-R1, LV44-01, LV76-01, LV79-01, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BD10-01, BD11-01, ZZ99- |  | EPD | TRY
94 | 1FA | D02Q095 | 10.4.09 | 1FA11VP02 | SCANNER AIR FAN DC MOTOR STARTER BOX | SCANNER AIR FAN DC MOTOR | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 96 | 96 | 43891 | DR0822_0002
95 | 1FA | D02Q025 | 10.4.07 | 1FA12BP01 | 220V SWGR O/G MODULE # 1FA12FB | 6.6KV STATION SWBD # 0CA | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV12-L2, LV13-L2, LV63-02, LV64-03, TR48-03, MR16-02, MV99-02, MV98-02, MV97-02, MV96-02, MV95-01, MV38-01, ZZ99- |  | EPD | BPL
96 | 1FA | D02L2.5 | 10.4.24 | 1FA12CP01 | 220V SWGR O/G MODULE # 1FA12FC | ERV LOCAL CONTROLLER BOX | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (0.3kW) | XLPE-CU UNARMOURED | LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, ZZ99- |  | EPD | PEM
97 | 1FA | D02Q010 | 10.4.06 | 1FA12DP01 | 220V SWGR O/G MODULE # 1FA12FD | AVR (FB) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 48 | 58 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-R2, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01, CC70-01, ZZ99- |  | EPD | EDN
98 | 1FA | D02Q010 | 10.4.06 | 1FA12EP01 | 220V SWGR O/G MODULE # 1FA12FE | UNIT PMCC # 1DA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 69 | 74 | 12.09.2019 | DR0816_0002 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV10-R1, LV44-01, LV76-01, MR10-01, MA05-01, MV68-01, MV67-01, MV66-01, MV65-03, MV64-03, MV48-01, MV69-02, ZZ99- |  | EPD | EPD
99 | 1FA | D02Q095 | 10.4.09 | 1FA12FP01 | 220V SWGR O/G MODULE # 1FA12FF | FEEDER TO LDB - TGB MV SWGR ROOM (1UH) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV11-R1, LV12-R1, LV58-01, LV04-L1, LV64-03, TR48-02, MR16-02, MV99-02, MV98-02, MV97-02, MV96-02, MV95-01, MV37-01, ZZ99- |  | EPD | EPD
100 | 1FA | D02Q095 | 10.4.09 | 1FA12FP02 | 220V SWGR O/G MODULE # 1FA12FF | FEEDER TO LDB - TGB MV SWGR ROOM (1UH) | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (125A) | XLPE-AL UNARMOURED | LV11-R1, LV12-R1, LV58-01, LV04-L1, LV64-03, TR48-03, MR16-02, MV99-02, MV98-02, MV97-02, MV96-02, MV95-01, MV37-01, ZZ99- |  | EPD | EPD
101 | 1FA | D02Q010 | 10.4.06 | 1FA12QP01 | 220V SWGR O/G MODULE # 1FA12RC | A/C MCC # 0TA | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 94 | 96 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV48-02, LV23-L1, LV24-L1, LV25-L1, LV74-02, DC07-03, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, AC13-01, DR07-01, AC14-L1, AC15-L1, AC16-L1, ZZ99- |  | EPD | EPD
102 | 1FA | D02Q095 | 10.4.09 | 1FA12RP01 | 220V SWGR O/G MODULE # 1FA12RD | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED(SPARE) | SITE ROUTING |  | EPD | EPD
103 | 1FA | D02Q010 | 10.4.06 | 1FA12SP01 | 220V SWGR O/G MODULE # 1FA12RE | GRP-3 | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 43 | 55 | 11.09.2019 | DR0816_0004 |  |  | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01 |  | EPD | BPL
104 | 1FA | D02Q010 | 10.4.06 | 1FA12TP01 | 220V SWGR O/G MODULE # 1FA12RF | AVR PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV11-R2, LV10-R1, LV44-01, LV76-01, LR05-01, CC92-01, CC89-01, CC51-01, CC50-01 |  | EPD | EDN
105 | 1FA | D02Q025 | 10.4.07 | 1FA12UP01 | 220V SWGR O/G MODULE # 1FA12RG | 6.6KV UNIT SWBD # 1CB | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 57 | 50 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV10-L1, LV44-01, LV76-01, MR10-01, MA05-01, MV68-01, MV67-01, MV66-01, MV29-L2, ZZ99- |  | EPD | BPL
106 | 1FA | D02Q025 | 10.4.07 | 1FA12VP01 | 220V SWGR O/G MODULE # 1FA12RH | 6.6KV UNIT SWBD # 1CA | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 49 | 47 | 02.12.2019 | DR0816_0002 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV11-L2, LV10-L1, LV44-01, LV76-01, MR10-01, MA05-01, MV07-L2, ZZ99- |  | EPD | BPL
107 | 1FA | E04V0.5 | 10.7.02 | 1FA13DC01 | 220V CHARGER-1B | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 57 | 59 | 30.11.2019 | DR0720_4798-4G-83 |  |  | CHARGER-1B OVERLOAD, CHARGER-1B TROUBLE, BATTERY-1B ON BOOST | OVERALL SCREENED | LV10-R4, LV44-04, LV76-06, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
| 1FA | E04V0.5 | 10.7.02 | 1FA13FC01 | 220V SWGR I/C MODULE # 1FA13FA | FCBC-02A | 04P X 0.5 Paired Screened(O) ( 225 V ) | 30 | 30 | 25.10.2019 | DR0720_4798-4G-82
108 | 1FA | E02W0.5 | 10.8.01 | 1FA13DC02 | 220V CHARGER-1B | DDCMIS # CRE66 | 02P X 0.5 Paired Screened(I) ( 225 V ) | 57 | [5 empty] | CHARGER-1B CURRENT & VOLTAGE MEASUREMENT | INDIVIDUAL & OVERALL SCREENED | LV10-R4, LV44-04, LV76-06, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
109 | 1FA | D01Q400 | 10.4.04 | 1FA13DP01 | 220V SWGR I/C MODULE # 1FA13FD | FCBC-1B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 23 | 29 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV11-L1, LV10-L1, ZZ99- |  | EPD | PEM
110 | 1FA | D01Q400 | 10.4.04 | 1FA13DP02 | 220V SWGR I/C MODULE # 1FA13FD | FCBC-1B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 23 | 29 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV11-L1, LV10-L1, ZZ99- |  | EPD | PEM
111 | 1FA | E04V0.5 | 10.7.02 | 1FA13RC01 | 220V CHARGER-1B (FUSE BOX) | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 62 | 60 | 30.11.2019 | DR0720_4798-4G-83 |  |  | BATTERY-1B FUSE FAILURE | OVERALL SCREENED | DC02-02, DC01-02, LV80-02, LV25-R3, LV74-04, LR07-04, CC90-02, CC81-02, CC31-01, CC67-04, CC68-02, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
112 | 1FA | D01Q630 | 10.4.05 | 1FA13RP01 | 220V SWGR I/C MODULE # 1FA13RD | BAT FUSE BOX-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 41 | 47 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV11-L1, LV48-01, LV23-L1, LV24-L1, LV80-01, DC01-01, DC02-01, ZZ99- |  | EPD | PEM
113 | 1FA | D01Q630 | 10.4.05 | 1FA13RP02 | 220V SWGR I/C MODULE # 1FA13RD | BAT FUSE BOX-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 44 | 47 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV11-L1, LV48-02, LV23-L1, LV24-L1, LV80-01, DC01-01, DC02-01, ZZ99- |  | EPD | PEM
114 | 1FA | D01Q630 | 10.4.05 | 1FA13RP03 | 220V SWGR I/C MODULE # 1FA13RD | BAT FUSE BOX-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 44 | 47 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV11-L1, LV48-02, LV23-L1, LV24-L1, LV80-01, DC01-01, DC02-01, ZZ99- |  | EPD | PEM
115 | 1FA | D01Q630 | 10.4.05 | 1FA13RP04 | 220V SWGR I/C MODULE # 1FA13RD | BAT FUSE BOX-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 44 | 47 | 06.09.2019 | DR1050_0014 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | LV11-L1, LV48-02, LV23-L1, LV24-L1, LV80-01, DC01-01, DC02-01, ZZ99- |  | EPD | PEM
115 | 1FA | D01Q630 | 10.4.05 | 1FA FB02 P01 | BAT FUSE BOX-1B | BATTERY BANK-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 17 | 28.11.2019 | DR1050_0011
115 | 1FA | D01Q630 | 10.4.05 | 1FA FB02 P02 | BAT FUSE BOX-1B | BATTERY BANK-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 17 | 28.11.2019 | DR1050_0011
115 | 1FA | D01Q630 | 10.4.05 | 1FA FB02 P03 | BAT FUSE BOX-1B | BATTERY BANK-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 20 | 28.11.2019 | DR1050_0011
115 | 1FA | D01Q630 | 10.4.05 | 1FA FB02 P04 | BAT FUSE BOX-1B | BATTERY BANK-1B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 15 | 20 | 28.11.2019 | DR1050_0011
75 | 1FA | E04W0.5 | 10.8.02 | 1GD66AC17 | 220V CHG-A | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EPD | EDN
75A | 1FA | E08W0.5 | 10.8.03 | 1GD66AC17A | 220V CHG-A | DDCMIS CRE66 | 08P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 08P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EPD | EDN
76 | 1FA | E04W0.5 | 10.8.02 | 1GD66AC18 | 220V CHG-B | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EPD | EDN
76A | 1FA | E08W0.5 | 10.8.03 | 1GD66AC18A | 220V CHG-B | DDCMIS CRE66 | 08P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 08P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EPD | EDN
1 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP1-P01 | 220V DCDB OGF ESP01 # FDR-01 | ESP SWGR PANEL # 1DB1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | EPD
2 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP1-P02 | 220V DCDB OGF ESP01 # FDR-02 | ESP SWGR PANEL # 1DB2 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | EPD
3 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP1-P03 | 220V DCDB OGF ESP01 # FDR-03 | ESP AC-VENT MCC # 1TB | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | EPD
4 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP1-P04 | 220V DCDB OGF ESP01 # FDR-04 | ID VFD SWGR ID-A PANEL # 1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | BPL
5 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP1-P05 | 220V DCDB OGF ESP01 # FDR-05 | ID VFD SWGR ID-B PANEL # 1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | BPL
6 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP2-P01 | 220V DCDB OGF ESP02 # FDR-01 | ESP SWGR PANEL # 1DB1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | EPD
7 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP2-P02 | 220V DCDB OGF ESP02 # FDR-02 | ESP SWGR PANEL # 1DB2 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | EPD
8 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP2-P03 | 220V DCDB OGF ESP02 # FDR-03 | ESP AC-VENT MCC # 1TB | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | EPD
9 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP2-P04 | 220V DCDB OGF ESP02 # FDR-04 | ID VFD SWGR ID-A PANEL # 1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | BPL
10 | 1FAESP | D02Q025 | 10.4.07 | 1FAESP2-P05 | 220V DCDB OGF ESP02 # FDR-05 | ID VFD SWGR ID-B PANEL # 1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [9 empty] | EPD | BPL
1 | 0FB | D02Q025 | 10.4.07 | 0FB01CP01 | 220V SWGR O/G MODULE # 0FB01FC | 33kV BREAKER PANEL-1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | BPL
2 | 0FB | D02Q025 | 10.4.07 | 0FB01DP01 | 220V SWGR O/G MODULE # 0FB01FD | 33kV BREAKER PANEL-2 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | BPL
3 | 0FB | D02Q025 | 10.4.07 | 0FB01EP01 | 220V SWGR O/G MODULE # 0FB01FE | 6.6KV RW SWBD # 0CD | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV09-R1, RV08-R1, ZZ99- |  | EPD | BPL
4 | 0FB | D02Q025 | 10.4.07 | 0FB01FP01 | 220V SWGR O/G MODULE # 0FB01FF | 415V RAW WATER PMCC # 0DB | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 34 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV15-L2, RV19-R1, ZZ99- |  | EPD | EPD
5 | 0FB | D02Q010 | 10.4.06 | 0FB01PP01 | 220V SWGR O/G MODULE # 0FB01RB | CONTROL PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV15-L2, RV19-R1, RV20-R1, RV21-R1, RV22-R1, RV23-R1, ZZ99- |  | EPD | PEM
6 | 0FB | D02Q010 | 10.4.06 | 0FB01SP01 | 220V SWGR O/G MODULE # 0FB01RE | RWT # 1A MARSHALLING BOX | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (6A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV15-L2, RV19-R1, RV20-R1, ZZ99- |  | EPD | PEM
7 | 0FB | D02Q095 | 10.4.09 | 0FB02CP01 | 220V SWGR I/C MODULE # 0FB02FC | FCBC-1A | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (25A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV13-L1, RV14-L1, ZZ99- |  | EPD | PEM
8 | 0FB | D02Q095 | 10.4.09 | 0FB02DP01 | 220V SWGR I/C MODULE # 0FB02FD | BATTERY-1A | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV44-01, ZZ99- |  | EPD | PEM
9 | 0FB | D02Q010 | 10.4.06 | 0FB02PP01 | 220V SWGR O/G MODULE # 0FB02RB | DATA CONCENTRATOR (HT & LT) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | BPL
10 | 0FB | D02Q010 | 10.4.06 | 0FB02QP01 | 220V SWGR O/G MODULE # 0FB02RC | BOP PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EDN
11 | 0FB | D02Q095 | 10.4.09 | 0FB03PP01 | 220V SWGR O/G MODULE # 0FB03RB | FEEDER TO LP - RW PUMP HOUSE | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
12 | 0FB | D02Q025 | 10.4.07 | 0FB03TP01 | 220V SWGR O/G MODULE # 0FB03RF | BREAKER PANEL FOR RW INTAKE PUMP-B | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (20A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, ZZ99- |  | EPD | BPL
13 | 0FB | D02Q025 | 10.4.07 | 0FB03UP01 | 220V SWGR O/G MODULE # 0FB03RG | BREAKER PANEL FOR RW INTAKE PUMP-A | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (20A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV09-R1, RV08-R1, RV07-R1, RV06-R1, ZZ99- |  | EPD | BPL
14 | 0FB | D02Q025 | 10.4.07 | 0FB04PP01 | 220V SWGR O/G MODULE # 0FB04RB | 33kV BREAKER PANEL-1 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | BPL
15 | 0FB | D02Q025 | 10.4.07 | 0FB04QP01 | 220V SWGR O/G MODULE # 0FB04RC | 33kV BREAKER PANEL-2 | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | BPL
16 | 0FB | D02Q025 | 10.4.07 | 0FB04RP01 | 220V SWGR O/G MODULE # 0FB04RD | 6.6KV RW SWBD # 0CD | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV09-R1, RV08-R1, ZZ99- |  | EPD | BPL
17 | 0FB | D02Q025 | 10.4.07 | 0FB04SP01 | 220V SWGR O/G MODULE # 0FB04RE | 415V RAW WATER PMCC # 0DB | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 34 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV15-L2, RV19-R1, ZZ99- |  | EPD | EPD
18 | 0FB | D02Q025 | 10.4.07 | 0FB04UP01 | 220V SWGR O/G MODULE # 0FB04RG | BREAKER PANEL FOR RW INTAKE PUMP-A | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (20A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV09-R1, RV08-R1, RV07-R1, RV06-R1, ZZ99- |  | EPD | BPL
19 | 0FB | D02Q095 | 10.4.09 | 0FB05CP01 | 220V SWGR I/C MODULE # 0FB05FC | FCBC-1B | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (25A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV13-L1, RV14-L1, ZZ99- |  | EPD | PEM
20 | 0FB | D02Q095 | 10.4.09 | 0FB05DP01 | 220V SWGR I/C MODULE # 0FB05FD | BATTERY-1B | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV44-01, ZZ99- |  | EPD | PEM
21 | 0FB | D02Q010 | 10.4.06 | 0FB05QP01 | 220V SWGR O/G MODULE # 0FB05RC | FOR OPERATION OF AUX. RELAYS | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EDN
22 | 0FB | D02Q025 | 10.4.07 | 0FB05TP01 | 220V SWGR O/G MODULE # 0FB05RF | BREAKER PANEL FOR RW INTAKE PUMP-B | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (20A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, ZZ99- |  | EPD | BPL
23 | 0FB | D02Q095 | 10.4.09 | 0FB06BP01 | 220V SWGR O/G MODULE # 0FB06FB | FEEDER TO LP - RW PUMP HOUSE | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
24 | 0FB | D02Q010 | 10.4.06 | 0FB06CP01 | 220V SWGR O/G MODULE # 0FB06FC | RWT # 1B MARSHALLING BOX | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 39 | [5 empty] | POWER SUPPLY (6A) | XLPE-AL UNARMOURED | RV47-01, RV46-01, RV12-L1, RV11-L1, RV10-R1, RV15-L2, RV16-L2, RV17-L2, ZZ99- |  | EPD | PEM
25 | 0FB | D02Q010 | 10.4.06 | 0FB06FP01 | 220V SWGR O/G MODULE # 0FB06FF | DATA CONCENTRATOR (HT & LT) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | BPL
26 | 0FB | D02Q010 | 10.4.06 | 0FB06GP01 | 220V SWGR O/G MODULE # 0FB06FG | BOP PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EDN
1 | 0FC | D02Q095 | 10.4.09 | 0FC01CP01 | 220V SWGR I/C MODULE # 0FC01FC | FCBC-1A | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (25A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
2 | 0FC | D02Q095 | 10.4.09 | 0FC01DP01 | 220V SWGR I/C MODULE # 0FC01FD | BATTERY-1A | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, ZZ99- |  | EPD | PEM
3 | 0FC | D02Q095 | 10.4.09 | 0FC01PP01 | 220V SWGR O/G MODULE # 0FC01RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
4 | 0FC | D02Q025 | 10.4.07 | 0FC01QP01 | 220V SWGR O/G MODULE # 0FC01RC | 415V PTP PMCC # 1DD | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, FP07-02, FP22-01, FP21-01, FP20-L1, FP19-L1, FP18-L1, ZZ99- |  | EPD | EPD
5 | 0FC | D02Q010 | 10.4.06 | 0FC01SP01 | 220V SWGR O/G MODULE # 0FC01RE | 415V FW & CLARIFIED WATER MCC # 0SC | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, FP07-02, FP06-R1, FP05-R2, FP04-R2, ZZ99- |  | EPD | EPD
6 | 0FC | D02Q010 | 10.4.06 | 0FC01UP01 | 220V SWGR O/G MODULE # 0FC01RG | CONTROL PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | FP08-02, FP09-01, FP10-01, FP11-01, ZZ99- |  | EPD | PEM
7 | 0FC | D02Q095 | 10.4.09 | 0FC02PP01 | 220V SWGR O/G MODULE # 0FC02RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
8 | 0FC | D02Q095 | 10.4.09 | 0FC02RP01 | 220V SWGR O/G MODULE # 0FC02RD | FEEDER TO LP - FW PUMP HOUSE | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 222 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, FP07-02, FP06-R1, FP05-R2, FP04-R2, FP03-R2, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, ZZ99- |  | EPD | PEM
9 | 0FC | D02Q010 | 10.4.06 | 0FC02SP01 | 220V SWGR O/G MODULE # 0FC02RE | DATA CONCENTRATOR | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | FP08-02, FP09-01, FP10-01, FP11-01, ZZ99- |  | EPD | BPL
10 | 0FC | D02Q010 | 10.4.06 | 0FC02TP01 | 220V SWGR O/G MODULE # 0FC02RF | BOP PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | FP08-02, FP09-02, FP10-01, FP11-01, ZZ99- |  | EPD | EDN
11 | 0FC | D02Q095 | 10.4.09 | 0FC03PP01 | 220V SWGR O/G MODULE # 0FC03RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
12 | 0FC | D02Q095 | 10.4.09 | 0FC03QP01 | 220V SWGR O/G MODULE # 0FC03RC | FEEDER TO LP - FW PUMP HOUSE | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 222 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, FP07-02, FP06-R1, FP05-R2, FP04-R2, FP03-R2, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, ZZ99- |  | EPD | PEM
13 | 0FC | D02Q010 | 10.4.06 | 0FC03UP01 | 220V SWGR O/G MODULE # 0FC03RG | BOP PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | FP08-02, FP09-02, FP10-01, FP11-01, ZZ99- |  | EPD | EDN
14 | 0FC | D02Q010 | 10.4.06 | 0FC03VP01 | 220V SWGR O/G MODULE # 0FC03RH | DATA CONCENTRATOR | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | FP08-02, FP09-02, FP10-01, FP11-01, ZZ99- |  | EPD | BPL
15 | 0FC | D02Q095 | 10.4.09 | 0FC04CP01 | 220V SWGR I/C MODULE # 0FC04FC | FCBC-1B | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (25A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
16 | 0FC | D02Q095 | 10.4.09 | 0FC04DP01 | 220V SWGR I/C MODULE # 0FC04FD | BATTERY-1B | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, ZZ99- |  | EPD | PEM
17 | 0FC | D02Q095 | 10.4.09 | 0FC04PP01 | 220V SWGR O/G MODULE # 0FC04RB | DC FUSE DB | 02C X 095 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (50A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
18 | 0FC | D02Q010 | 10.4.06 | 0FC04SP01 | 220V SWGR O/G MODULE # 0FC04RE | FOR OPERATION OF AUX. RELAYS | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EDN
19 | 0FC | D02Q010 | 10.4.06 | 0FC04UP01 | 220V SWGR O/G MODULE # 0FC04RG | 415V FW & CLARIFIED WATER MCC # 0SC | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (5A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, FP07-02, FP06-R1, FP05-R2, FP04-R2, ZZ99- |  | EPD | EPD
20 | 0FC | D02Q025 | 10.4.07 | 0FC04VP01 | 220V SWGR O/G MODULE # 0FC04RH | 415V PTP PMCC # 1DD | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (10A) | XLPE-AL UNARMOURED | ZZ99- , FP08-02, FP07-02, FP22-01, FP21-01, FP20-L1, FP19-L1, FP18-L2, ZZ99- |  | EPD | EPD
1 | 0CA | D05C2.5 | 10.5.07 | 0CA01AC01 | 6.6kV STN SWBD # 0CA PANEL NO 01 (MAIN I/C) | STRP | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | CT CONNECTION FOR DIFFERENTIAL PROTECTION (87ST) | PVC-CU UNARMOURED | MV37-02, MV36-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | TBG
2 | 0CA | D02C1.5 | 10.5.01 | 0CA01AC02 | 6.6kV STN SWBD # 0CA PANEL NO 01 (MAIN I/C) | STRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | STN. PROTECTION TRIP (FOR TRIPPING CKT.) | PVC-CU UNARMOURED | MV37-02, MV36-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | TBG
3 | 0CA | D02C1.5 | 10.5.01 | 0CA01AC03 | 6.6kV STN SWBD # 0CA PANEL NO 01 (MAIN I/C) | STRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | STN. PROTECTION NOT OPTD. (FOR CLOSING CKT.) | PVC-CU UNARMOURED | MV37-02, MV36-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | TBG
4 | 0CA | D02C1.5 | 10.5.01 | 0CA01AC04 | 6.6kV STN SWBD # 0CA PANEL NO 01 (MAIN I/C) | SWYD. | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | ST HVCB CLOSED | PVC-CU UNARMOURED | MV37-02, MV36-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | TBG
5 | 0CA | E04V0.5 | 10.7.02 | 0CA01AC05 | 6.6kV STN SWBD # 0CA PANEL NO 01 (MAIN I/C) | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV37-03, MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
6 | 0CA | E04V0.5 | 10.7.02 | 0CA01AC06 | 6.6kV STN SWBD # 0CA PANEL NO 01 (MAIN I/C) | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | LINE PT IN SERVICE | OVERALL SCREENED | MV37-03, MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
7 | 0CA | D02C1.5 | 10.5.01 | 0CA01AC07 | 6.6kV STN SWBD # 0CA PANEL NO 01 (MAIN I/C) | SWYD. | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | 51N FOR REVERSE BLOCKING | PVC-CU UNARMOURED | MV37-02, MV36-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | TBG
8 | 0CA | E04V0.5 | 10.7.02 | 0CA02AC01 | 6.6kV STN SWBD # 0CA PANEL NO 02 (DP PANEL) | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | DC SUPPLY - 1 & 2 FAILURE | OVERALL SCREENED | MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
9 | 0CA | E04V0.5 | 10.7.02 | 0CA03AC01 | 6.6kV STN SWBD # 0CA PANEL NO 03 (TIE TO 1CB) | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
10 | 0CA | E04V0.5 | 10.7.02 | 0CA03AC02 | 6.6kV STN SWBD # 0CA PANEL NO 03 (TIE TO 1CB) | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | LINE PT IN SERVICE | OVERALL SCREENED | MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
11 | 0CA | D02L2.5 | 10.4.24 | 0CA03AC03 | 6.6kV STN SWBD # 0CA PANEL NO 03 (TIE TO 1CB) | BTS-2 1CB - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV38-02, MV39-02, MV40-02, MV41-02, MV42-02, MV43-02, MV45-L2, MV44-L2, MA06-03, MR09-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC88-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
12 | 0CA | D05C1.5 | 10.5.06 | 0CA03AC04 | 6.6kV STN SWBD # 0CA PANEL NO 03 (TIE TO 1CB) | BTS-2 1CB - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | BREAKER OPEN & IN SERVICE, BREAKER CLOSE & IN SERVICE, 86 RE | PVC-CU UNARMOURED | MV38-02, MV39-02, MV40-02, MV41-02, MV42-02, MV43-02, MV45-L2, MV44-L2, MA06-03, MR09-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC88-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
13 | 0CA | E04V0.5 | 10.7.02 | 0CA04AC01 | 6.6kV STN SWBD # 0CA PANEL NO 04 (BUS PT) | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | BUS PT IN SERVICE, N/V | OVERALL SCREENED | MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
14 | 0CA | D02L2.5 | 10.4.24 | 0CA04AC02 | 6.6kV STN SWBD # 0CA PANEL NO 04 (BUS PT) | BTS-2 1CB - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV38-02, MV39-02, MV40-02, MV41-02, MV42-02, MV43-02, MV45-L2, MV44-L2, MA06-03, MR09-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC88-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
15 | 0CA | D03C1.5 | 10.5.03 | 0CA04AC03 | 6.6kV STN SWBD # 0CA PANEL NO 04 (BUS PT) | BTS-1 1CA - 0CA | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | BUS PT IN SERVICE, BUS PT MCB HEALTHY | PVC-CU UNARMOURED | MV38-02, MV39-02, MV40-02, MV41-02, MV42-02, MV43-02, MV45-L2, MV44-L2, MA06-03, MR09-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC88-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
16 | 0CA | E04V0.5 | 10.7.02 | 0CA05AC01 | 6.6kV STN SWBD # 0CA PANEL NO 05 (TIE TO 1CA) | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
17 | 0CA | E04V0.5 | 10.7.02 | 0CA05AC02 | 6.6kV STN SWBD # 0CA PANEL NO 05 (TIE TO 1CA) | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | LINE PT IN SERVICE | OVERALL SCREENED | MV38-03, MV39-03, MV40-03, MV41-03, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
18 | 0CA | D02L2.5 | 10.4.24 | 0CA05AC03 | 6.6kV STN SWBD # 0CA PANEL NO 05 (TIE TO 1CA) | BTS-1 1CA - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV38-02, MV39-02, MV40-02, MV41-02, MV42-02, MV43-02, MV45-L2, MV44-L2, MA06-03, MR09-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC88-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
19 | 0CA | D05C1.5 | 10.5.06 | 0CA05AC04 | 6.6kV STN SWBD # 0CA PANEL NO 05 (TIE TO 1CA) | BTS-1 1CA - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | BREAKER OPEN & IN SERVICE, BREAKER CLOSE & IN SERVICE, 86 RE | PVC-CU UNARMOURED | MV38-02, MV39-02, MV40-02, MV41-02, MV42-02, MV43-02, MV45-L2, MV44-L2, MA06-03, MR09-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC88-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
1 | 1CA | D05C2.5 | 10.5.07 | 1CA01AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | GRP | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | 100 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CT CONNECTION FOR DIFFERENTIAL PROTECTION (87UT) | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
2 | 1CA | D02C1.5 | 10.5.01 | 1CA01AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | UNIT PROTECTION TRIP (FOR TRIPPING CKT.) | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
3 | 1CA | D02C1.5 | 10.5.01 | 1CA01AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | UNIT PROTECTION NOT OPTD. (FOR CLOSING CKT.) | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
4 | 1CA | D02C1.5 | 10.5.01 | 1CA01AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | GT HVCB CLOSED | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
5 | 1CA | D05C1.5 | 10.5.06 | 1CA01AC05 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | BTS-1 1CA - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | CLOSE AND TRIP COMMAND TO CB | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
6 | 1CA | E04V0.5 | 10.7.02 | 1CA01AC06 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 100 | 13.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
7 | 1CA | E04V0.5 | 10.7.02 | 1CA01AC07 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 100 | 13.09.2019 | DR0817_4798-4G-104 |  |  | LINE PT IN SERVICE | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
8 | 1CA | D02L2.5 | 10.4.24 | 1CA01AC08 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | BTS-1 1CA - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
9 | 1CA | D05C1.5 | 10.5.06 | 1CA01AC09 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | BTS-1 1CA - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | BREAKER OPEN & IN SERVICE, BREAKER CLOSE & IN SERVICE, 86 RE | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
10 | 1CA | D02C1.5 | 10.5.01 | 1CA01AC10 | 6.6kV UNIT SWBD # 1CA PANEL NO 01 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | 51N FOR REVERSE BLOCKING | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
11 | 1CA | E04V0.5 | 10.7.02 | 1CA01AC11 | BTS-1 1CA - 0CA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 83 | [5 empty] | BTS OUT OPERATED | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | BPL | EDN
12 | 1CA | D03L2.5 | 10.4.26 | 1CA02AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 02 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 299 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV16-L2, MV01-03, MR01-03, LR01-03, TY14-L4, TY15-L4, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP35-L3, HR01-L3, CT01-L3, CT02-L3, CT03-L3, CT04-L3, CT05-L3, CT06-L3 |  | BPL | EPD
13 | 1CA | D02C1.5 | 10.5.01 | 1CA02AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 02 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 299 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV16-L2, MV01-03, MR01-03, LR01-03, TY14-L4, TY15-L4, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP35-L3, HR01-L3, CT01-L3, CT02-L3, CT03-L3, CT04-L3, CT05-L3, CT06-L3 |  | BPL | EPD
14 | 1CA | D05C1.5 | 10.5.06 | 1CA02AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 02 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 291 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV16-L2, MV01-03, MR01-03, LR01-03, TY14-L4, TY15-L4, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, CT11-02 |  | BPL | JHS
15 | 1CA | E04V0.5 | 10.7.02 | 1CA02AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 02 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 96 | 13.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
16 | 1CA | B03Q150 | 10.1.02 | 1CA02AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 02 (O/G T/F FDR) | CT SERV TRF # 1DCT01 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 279 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV16-L1, MV01-01, MR01-01, LR01-01, TY14-L1, TY15-L1, TY16-L1, TY17-L1, TY18-L1, TY19-L1, IP01-L1, IP02-L1, IR03-L1, IP14-R1, IP15-L1, IP16-L1, IP17-L1, IP18-L1, IP19-L1, IR38-L1, IP23-L1, IP24-L1, IP25-L1, IP26-L1, IP27-L1, IP28-L1, IP29-L1, IP30-L1, IP31-L1, IP32-L1, IP33-L1, IP34-L1, IP36-L1, IP37-L1, CT11-01, ZZ99- |  | BPL | JHS
17 | 1CA | D03L2.5 | 10.4.26 | 1CA03AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 03 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 144 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV15-02, MV17-L2, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | EPD
18 | 1CA | D02C1.5 | 10.5.01 | 1CA03AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 03 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 144 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV15-02, MV17-L2, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | EPD
19 | 1CA | D05C1.5 | 10.5.06 | 1CA03AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 03 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV15-02, MV17-L2, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02 |  | BPL | JHS
20 | 1CA | E04V0.5 | 10.7.02 | 1CA03AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 03 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 94 | 13.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
21 | 1CA | B03Q150 | 10.1.02 | 1CA03AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 03 (O/G T/F FDR) | SWYD SERV TRF | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 135 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV02-L1, MV16-R1, MV17-R1, MV18-R1, MV35-R1, MA02-01, MR03-01, LR03-01, TY16-L1, TY17-L1, TY18-L1, YR02-01, TY25-01, TY26-01, TY28-01, TY29-01, TY30-01, TY31-01, TY32-01, ZZ99- |  | BPL | JHS
22 | 1CA | E04V0.5 | 10.7.02 | 1CA04AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 04 (TIE) | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 93 | 13.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
23 | 1CA | E04V0.5 | 10.7.02 | 1CA04AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 04 (TIE) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 93 | 13.09.2019 | DR0817_4798-4G-104 |  |  | LINE PT IN SERVICE | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
24 | 1CA | D02L2.5 | 10.4.24 | 1CA04AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 04 (TIE) | BTS-1 1CA - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
25 | 1CA | D05C1.5 | 10.5.06 | 1CA04AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 04 (TIE) | BTS-1 1CA - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | BREAKER OPEN & IN SERVICE, BREAKER CLOSE & IN SERVICE, 86 RE | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
26 | 1CA | D02C1.5 | 10.5.01 | 1CA04AC05 | 6.6kV UNIT SWBD # 1CA PANEL NO 04 (TIE) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | 51N FOR REVERSE BLOCKING | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
27 | 1CA | E04V0.5 | 10.7.02 | 1CA05AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 05 (BUS PT) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 93 | 13.09.2019 | DR0817_4798-4G-104 |  |  | BUS PT IN SERVICE, N/V | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
28 | 1CA | D02L2.5 | 10.4.24 | 1CA05AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 05 (BUS PT) | BTS-1 1CA - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
29 | 1CA | D03C1.5 | 10.5.03 | 1CA05AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 05 (BUS PT) | BTS-1 1CA - 0CA | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | BUS PT IN SERVICE, BUS PT MCB HEALTHY | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV09-02, MV08-L2, MA05-03, MR10-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
30 | 1CA | D03L2.5 | 10.4.26 | 1CA06AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 06 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 488 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV85-02, MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-03, IM28-03, IM29-03, IM30-03, IM31-03, IR37-03, IL01-03, IL02-03, IL03-03, IL04-03, IL05-03, IL06-03, IL07-03, IL08-03, IL09-03, PR01-03, ET01-L4, ET02-L4, ET03-L4, ET04-L4, ET05-L4, ET06-L4 |  | BPL | EPD
31 | 1CA | D02C1.5 | 10.5.01 | 1CA06AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 06 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 488 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV85-02, MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-03, IM28-03, IM29-03, IM30-03, IM31-03, IR37-03, IL01-03, IL02-03, IL03-03, IL04-03, IL05-03, IL06-03, IL07-03, IL08-03, IL09-03, PR01-03, ET01-L4, ET02-L4, ET03-L4, ET04-L4, ET05-L4, ET06-L4 |  | BPL | EPD
32 | 1CA | D05C1.5 | 10.5.06 | 1CA06AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 06 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 480 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV15-02, MV14-02, MV13-02, MV12-02, MV85-02, MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-03, IM28-03, IM29-03, IM30-03, IM31-03, IR37-03, IL01-03, IL02-03, IL03-03, IL04-03, IL05-03, IL06-03, IL07-03, IL08-03, IL09-03, PR01-03, ET23-02, ET24-02, ET25-02, ET26-02 |  | BPL | JHS
33 | 1CA | E04V0.5 | 10.7.02 | 1CA06AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 06 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 93 | 13.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
34 | 1CA | B03Q150 | 10.1.02 | 1CA06AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 06 (O/G T/F FDR) | ETP SERV TRF # 1DET01 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 474 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV02-L1, MV98-01, MV14-01, MV91-01, MV90-01, MV32-L1, MV79-01, MV78-01, MV77-01, MV58-L1, MV59-L1, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L2, IM12-L2, IM13-L2, IM14-L2, IM15-L2, IM16-L2, IM17-L2, IM18-L2, IM19-L2, IM20-L2, IM21-L1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, IM27-01, IM28-01, IM29-01, IM30-01, IM31-01, IR37-01, IL01-01, IL02-01, IL03-01, IL04-01, IL05-01, IL06-01, IL07-01, IL08-01, IL09-01, PR01-01, ET23-01, ET24-01, ET25-01, ET26-01, ZZ99- |  | BPL | JHS
35 | 1CA | D03L2.5 | 10.4.26 | 1CA07AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 07 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 479 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV14-02, MV15-02, MV16-L2, MV01-03, MR01-03, LR01-03, TY14-L4, TY15-L4, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, FR01-03, FP01-03, FP16-02, FP17-L3 |  | BPL | EPD
36 | 1CA | D02C1.5 | 10.5.01 | 1CA07AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 07 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 479 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV14-02, MV15-02, MV16-L2, MV01-03, MR01-03, LR01-03, TY14-L4, TY15-L4, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, FR01-03, FP01-03, FP16-02, FP17-L3 |  | BPL | EPD
37 | 1CA | D05C1.5 | 10.5.06 | 1CA07AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 07 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 468 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV14-02, MV15-02, MV16-L2, MV01-03, MR01-03, LR01-03, TY14-L4, TY15-L4, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, FR01-03, FP02-02 |  | BPL | JHS
38 | 1CA | E04V0.5 | 10.7.02 | 1CA07AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 07 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 71 | 92 | 13.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
39 | 1CA | B03Q150 | 10.1.02 | 1CA07AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 07 (O/G T/F FDR) | PTP SERV TRF # 1DDT01 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 456 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-R1, MV02-L1, MV01-01, MR01-01, LR01-01, TY14-L1, TY15-L1, TY16-L1, TY17-L1, TY18-L1, TY19-L1, IP01-L1, IP02-L1, IR03-L1, IP14-R1, IP15-L1, IP16-L1, IP17-L1, IP18-L1, IP19-L1, IR38-L1, IP23-L1, IP24-L1, IP25-L1, IP26-L1, IP27-L1, IP28-L1, IP29-L1, IP30-L1, IP31-L1, IP32-L1, IP33-L1, IP34-L1, IP36-L1, IP37-L1, IP38-L1, IR04-L1, IP39-L1, IP40-L1, IP41-L1, IP42-L1, IP43-L1, IP44-L1, IP45-L1, IP46-L1, IP47-L1, IP48-L1, IP49-L1, IP50-L1, IR05-L1, IP51-L1, IP52-L1, FR01-01, FP02-01, ZZ99- |  | BPL | JHS
40 | 1CA | E04V0.5 | 10.7.02 | 1CA08AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 08 (O/G FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 71 | 92 | 13.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
41 | 1CA | B01Q400 | 10.1.01 | 1CA08AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 08 (O/G FDR) | COMP. SWBD # 1CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 162 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV02-L1, MV01-01, MR01-01, LR01-01, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-L1, CM05-L1, CM06-L1, CM07-L1, CM08-L1, ZZ99- |  | BPL | BPL
42 | 1CA | B01Q400 | 10.1.01 | 1CA08AP02 | 6.6kV UNIT SWBD # 1CA PANEL NO 08 (O/G FDR) | COMP. SWBD # 1CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 162 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV02-L1, MV01-01, MR01-01, LR01-01, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-L1, CM05-L1, CM06-L1, CM07-L1, CM08-L1, ZZ99- |  | BPL | BPL
43 | 1CA | B01Q400 | 10.1.01 | 1CA08AP03 | 6.6kV UNIT SWBD # 1CA PANEL NO 08 (O/G FDR) | COMP. SWBD # 1CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 162 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV02-L1, MV01-01, MR01-01, LR01-01, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-L1, CM05-L1, CM06-L1, CM07-L1, CM08-L1, ZZ99- |  | BPL | BPL
44 | 1CA | B01Q400 | 10.1.01 | 1CA08AP04 | 6.6kV UNIT SWBD # 1CA PANEL NO 08 (O/G FDR) | COMP. SWBD # 1CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 163 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV02-L1, MV01-01, MR01-01, LR01-01, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-L1, CM05-L1, CM06-L2, CM07-L2, CM08-L2, ZZ99- |  | BPL | BPL
45 | 1CA | B01Q400 | 10.1.01 | 1CA08AP05 | 6.6kV UNIT SWBD # 1CA PANEL NO 08 (O/G FDR) | COMP. SWBD # 1CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 163 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV02-L1, MV01-01, MR01-01, LR01-01, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-L1, CM05-L1, CM06-L2, CM07-L2, CM08-L2, ZZ99- |  | BPL | BPL
46 | 1CA | B01Q400 | 10.1.01 | 1CA08AP06 | 6.6kV UNIT SWBD # 1CA PANEL NO 08 (O/G FDR) | COMP. SWBD # 1CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 163 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV02-L1, MV01-01, MR01-01, LR01-01, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-L1, CM05-L1, CM06-L2, CM07-L2, CM08-L2, ZZ99- |  | BPL | BPL
47 | 1CA | D05C1.5 | 10.5.06 | 1CA09AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 09 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV14-02, MV97-04, MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR01-03, IP03-03, IP05-03, IP06-03, WR07-03, CW09-03, CW10-03, CW12-03, CW14-03, WR06-02, CW15-02 |  | BPL | EPD
48 | 1CA | D02L2.5 | 10.4.24 | 1CA09AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 09 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV14-02, MV97-04, MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR01-03, IP03-03, IP05-03, IP06-03, WR07-03, CW09-03, CW10-03, CW12-03, CW14-03, WR06-02, CW15-02 |  | BPL | BPL
49 | 1CA | B03Q240 | 10.1.03 | 1CA09AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 09 (MOTOR FDR) | CWP-1C | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 161 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-R1, MV98-01, MV97-01, MV19-01, MV18-L1, MV35-L1, MA02-01, MR03-01, LR03-01, TY16-L1, TY17-L1, TY18-L1, TY19-L1, IP01-L1, IP02-L1, IR01-01, IP03-01, IP05-01, IP06-01, WR07-01, CW09-01, CW10-01, CW12-01, CW14-01, WR06-01, CW15-01, ZZ99- |  | BPL | BPL
50 | 1CA | D05C1.5 | 10.5.06 | 1CA10AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 10 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV14-02, MV97-04, MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR01-03, IP03-03, IP05-03, IP06-03, WR07-03, CW09-03, CW10-03,WR04-L2 CW11-02 |  | BPL | EPD
51 | 1CA | D02L2.5 | 10.4.24 | 1CA10AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 10 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV14-02, MV97-04, MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR01-03, IP03-03, IP05-03, IP06-03, WR07-03, CW09-03, CW10-03, WR04-L2 CW11-02 |  | BPL | BPL
52 | 1CA | B03Q240 | 10.1.03 | 1CA10AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 10 (MOTOR FDR) | CWP-1A | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 146 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-R1, MV98-01, MV97-01, MV19-01, MV18-L1, MV35-L1, MA02-01, MR03-01, LR03-01, TY16-L1, TY17-L1, TY18-L1, TY19-L1, IP01-L1, IP02-L1, IR01-01, IP03-01, IP05-01, IP06-01, WR07-01, CW09-01, CW10-01, WR04-L1 CW11-01, ZZ99- |  | BPL | BPL
53 | 1CA | E04V0.5 | 10.7.02 | 1CA11AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 11 (O/G FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 71 | 89 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
54 | 1CA | B01Q400 | 10.1.01 | 1CA11AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 11 (O/G FDR) | CHP SWBD # 0CB SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1260 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV92-01, MV91-01, MV90-01, MV32-L1, MV79-01, MV78-01, MV77-01, MV58-L1, MV59-L1, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM21-L1, IM32-L1, IM33-L1, IR31-L1, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
55 | 1CA | B01Q400 | 10.1.01 | 1CA11AP02 | 6.6kV UNIT SWBD # 1CA PANEL NO 11 (O/G FDR) | CHP SWBD # 0CB SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1260 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV92-01, MV91-01, MV90-01, MV32-L1, MV79-01, MV78-01, MV77-01, MV58-L1, MV59-L1, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM21-L1, IM32-L1, IM33-L1, IR31-L1, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
56 | 1CA | B01Q400 | 10.1.01 | 1CA11AP03 | 6.6kV UNIT SWBD # 1CA PANEL NO 11 (O/G FDR) | CHP SWBD # 0CB SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1260 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV92-01, MV91-01, MV90-01, MV32-L1, MV79-01, MV78-01, MV77-01, MV58-L1, MV59-L1, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM21-L1, IM32-L1, IM33-L1, IR31-L1, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
57 | 1CA | B01Q400 | 10.1.01 | 1CA11AP04 | 6.6kV UNIT SWBD # 1CA PANEL NO 11 (O/G FDR) | CHP SWBD # 0CB SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1260 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV92-01, MV91-01, MV90-01, MV32-L1, MV79-01, MV78-01, MV77-01, MV58-L1, MV59-L1, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM21-L1, IM32-L1, IM33-L1, IR31-L1, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
58 | 1CA | B01Q400 | 10.1.01 | 1CA11AP05 | 6.6kV UNIT SWBD # 1CA PANEL NO 11 (O/G FDR) | CHP SWBD # 0CB SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1260 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV92-01, MV91-01, MV90-01, MV32-L1, MV79-01, MV78-01, MV77-01, MV58-L1, MV59-L1, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM21-L1, IM32-L1, IM33-L1, IR31-L1, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
59 | 1CA | B01Q400 | 10.1.01 | 1CA11AP06 | 6.6kV UNIT SWBD # 1CA PANEL NO 11 (O/G FDR) | CHP SWBD # 0CB SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1260 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV03-L1, MV92-01, MV91-01, MV90-01, MV32-L1, MV79-01, MV78-01, MV77-01, MV58-L1, MV59-L1, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM21-L1, IM32-L1, IM33-L1, IR31-L1, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
60 | 1CA | D03L2.5 | 10.4.26 | 1CA12AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 12 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 37 | 58 | 17.03.2020 | DR1050_0012 |  |  | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV14-02, MV91-03, MV90-03, MV32-L2, MV79-03, MV78-03, MV49-02 |  | BPL | EPD
61 | 1CA | D02C1.5 | 10.5.01 | 1CA12AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 12 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 37 | 58 | 17.03.20 | DR1150_17PA011783 |  |  | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV14-02, MV91-03, MV90-03, MV32-L2, MV79-03, MV78-03, MV49-02 |  | BPL | EPD
62 | 1CA | D05C1.5 | 10.5.06 | 1CA12AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 12 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 31 | 51 | 17.03.2020 | DR1150_17PA011779 |  |  | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV14-02, MV91-03, MV90-03, MV32-L2, MV31-L2, MV83-02, ZZ99- |  | BPL | JHS
63 | 1CA | E04V0.5 | 10.7.02 | 1CA12AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 12 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 71 | 90 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
64 | 1CA | B03Q240 | 10.1.03 | 1CA12AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 12 (O/G T/F FDR) | STN SERV TRF # 0DAT01 | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 28 | 41 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV03-R1, MV92-01, MV91-01, MV90-01, MV32-L1, MV31-L1, MV83-01, ZZ99- |  | BPL | JHS
65 | 1CA | D05C1.5 | 10.5.06 | 1CA17AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 17 (O/G T/F FDR) | VFD TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 65 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV13-02, MV14-02, MV15-02, MV17-L2, MV18-L2, MA01-03, MR02-03, LV71-03, LV18-L4, LV19-L4, LV61-05, LV20-L4, LV21-L4, LV51-02, LV29-L4 |  | BPL | EDN
66 | 1CA | B03Q150 | 10.1.02 | 1CA17AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 17 (O/G T/F FDR) | VFD TRF (CEP-1A) | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 69 | 64 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV04-L1, MV03-R1, MV02-L1, MV16-R1, MV17-R1, MV18-R1, MA01-01, MR02-01, LV71-01, LV18-L1, LV19-L1, LV61-03, LV20-L1, LV21-L1, LV51-01, LV29-L1, ZZ99- |  | BPL | BPL
67 | 1CA | B03Q150 | 10.1.02 | 1CA17AP02 | VFD TRF (CEP-1A) I/P BKR. Q1 | VFD Panel | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 72 | 64 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | LV29-L1, LV28-L1, LV27-L1, LV26-L1, LV74-01, DC07-01, DC08-01, DC09-01, DC10-01, DC11-01, DR03-01, AC01-01, AC04-01, AC09-01, DR06-01, AC10-01, AC11-01, AC12-01, ZZ99- |  | BPL | EDN
68 | 1CA | B03Q150 | 10.1.02 | 1CA17AP03 | VFD Panel | VFD TRF (CEP-1A) O/P BKR. Q2 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 74 | 61 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | AC12-01, AC11-01, AC10-01, DR06-01, AC09-01, AC04-01, AC01-01, DR03-01, DC11-01, DC10-01, DC09-01, DC08-01, DC07-01, LV74-01, LV26-L1, LV27-L1, LV28-L1, LV29-L1, ZZ99- |  | BPL | BPL
69 | 1CA | B03Q150 | 10.1.02 | 1CA17AP04 | VFD TRF (CEP-1A) O/P BKR. Q2 | CEP-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 112 | 145 | 15.01.20 | DR1658_2147483647B |  |  | POWER CABLE | XLPE-AL UNARMOURED | LV29-L1, LV51-01, LV52-01, LV53-01, LV54-01, TR49-01, MR14-01, TR01-01, TG87-02, TG17-L1, TG15-L2, TG14-L2, TG13-L2, TG12-L2, TG11-L2, TG10-L2, TG09-L1, TG08-L1, TG07-01, ZZ99- |  | BPL | BPL
70 | 1CA | D05C1.5 | 10.5.06 | 1CA19AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 19 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 85 | 80 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV13-02, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3 |  | BPL | EPD
71 | 1CA | D05C2.5 | 10.5.07 | 1CA19AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 19 (MOTOR FDR) | MOTOR TB | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 85 | [5 empty] | CT CONNECTION FOR MOTOR DIFF.PROTECTION | PVC-CU UNARMOURED | MV13-02, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3 |  | BPL | BPL
72 | 1CA | D02L2.5 | 10.4.24 | 1CA19AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 19 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 85 | 80 | 6.3.20 | DR1095_0045 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV13-02, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3 |  | BPL | BPL
73 | 1CA | B01Q400 | 10.1.01 | 1CA19AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 19 (MOTOR FDR) | MDBFP-1A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 81 | 71 | 43815 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV04-L1, MV03-L1, MV99-01, MR17-01, TG82-01, TG81-01, TG84-01, TG86-01, TG15-L1, TG14-L1, TG13-L1, TG12-L1, TG11-L1, TG10-L1, TG09-L1, ZZ99- |  | BPL | BPL
74 | 1CA | B01Q400 | 10.1.01 | 1CA19AP02 | 6.6kV UNIT SWBD # 1CA PANEL NO 19 (MOTOR FDR) | MDBFP-1A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 81 | 71 | 43815 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV04-L1, MV03-L1, MV99-01, MR17-01, TG82-01, TG81-01, TG84-01, TG86-01, TG15-L1, TG14-L1, TG13-L1, TG12-L1, TG11-L1, TG10-L1, TG09-L1, ZZ99- |  | BPL | BPL
75 | 1CA | B01Q400 | 10.1.01 | 1CA19AP03 | 6.6kV UNIT SWBD # 1CA PANEL NO 19 (MOTOR FDR) | MDBFP-1A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 81 | 71 | 43815 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV04-L1, MV03-L1, MV99-01, MR17-01, TG82-01, TG81-01, TG84-01, TG86-01, TG15-L1, TG14-L1, TG13-L1, TG12-L1, TG11-L1, TG10-L1, TG09-L1, ZZ99- |  | BPL | BPL
76 | 1CA | E04V0.5 | 10.7.02 | 1CA1AAC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 1A (LV PANEL) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | [5 empty] | DC SUPPLY - 1 & 2 FAILURE | OVERALL SCREENED | ZZ99- , MV15-03, MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
77 | 1CA | D05C1.5 | 10.5.06 | 1CA21AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 21 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 36 | 54 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV12-02, MV11-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03 |  | BPL | EPD
78 | 1CA | D05C2.5 | 10.5.07 | 1CA21AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 21 (MOTOR FDR) | MOTOR TB | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | CT CONNECTION FOR MOTOR DIFF.PROTECTION | PVC-CU UNARMOURED | MV12-02, MV11-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03 |  | BPL | BPL
79 | 1CA | D05C2.5 | 10.5.07 | 1CA21AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 21 (MOTOR FDR) | 1CB PANEL NO. 17 | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 14 | [5 empty] | CT CONNECTION FOR MOTOR DIFF.PROTECTION | PVC-CU UNARMOURED | MV12-02, MV81-03, MV22-02 |  | BPL | BPL
80 | 1CA | D02L2.5 | 10.4.24 | 1CA21AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 21 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 36 | 48 | 6.3.20 | DR1095_0045 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV12-02, MV11-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03 |  | BPL | BPL
81 | 1CA | B01Q400 | 10.1.01 | 1CA21AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 21 (MOTOR FDR) | MDBFP-1C | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | 39 | 43816 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV05-L1, MV06-L1, MV75-01, TR51-01, TG69-01, TG70-01, ZZ99- |  | BPL | BPL
82 | 1CA | B01Q400 | 10.1.01 | 1CA21AP02 | 6.6kV UNIT SWBD # 1CA PANEL NO 21 (MOTOR FDR) | MDBFP-1C | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | 39 | 43816 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV05-L1, MV06-L1, MV75-01, TR51-01, TG69-01, TG70-01, ZZ99- |  | BPL | BPL
83 | 1CA | B01Q400 | 10.1.01 | 1CA21AP03 | 6.6kV UNIT SWBD # 1CA PANEL NO 21 (MOTOR FDR) | MDBFP-1C | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | 39 | 43816 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV05-L1, MV06-L1, MV75-01, TR51-01, TG69-01, TG70-01, ZZ99- |  | BPL | BPL
84 | 1CA | D05C1.5 | 10.5.06 | 1CA22AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 22 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 23 | 55 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV12-02, MV86-02, MR18-03, MA04-02, TG21-02, TG18-02 |  | BPL | EPD
85 | 1CA | D02L2.5 | 10.4.24 | 1CA22AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 22 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 23 | 40 | 07.12.19 | DR3111-11601 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV12-02, MV86-02, MR18-03, MA04-02, TG21-02, TG18-02 |  | BPL | BPL
86 | 1CA | B03Q150 | 10.1.02 | 1CA22AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 22 (MOTOR FDR) | DMCW PUMP-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 21 | 22 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV05-L1, MR18-01, MA04-01, TG21-01, TG18-01, ZZ99- |  | BPL | BPL
87 | 1CA | D05C1.5 | 10.5.06 | 1CA23AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 23 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 49 | 43 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV11-02, MV12-02, MV13-02, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03 |  | BPL | EPD
88 | 1CA | D02L2.5 | 10.4.24 | 1CA23AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 23 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | 51 | 07.12.19 | DR3111-11601 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV11-02, MV12-02, MV13-02, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03 |  | BPL | BPL
89 | 1CA | B03Q150 | 10.1.02 | 1CA23AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 23 (MOTOR FDR) | ACW PUMP-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 46 | 38 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV06-R1, MV05-R1, MV04-R1, MV03-R1, MV99-01, MR17-01, TG82-02, TG81-01, TG84-01, TG86-01, ZZ99- |  | BPL | BPL
90 | 1CA | E04V0.5 | 10.7.02 | 1CA24AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 24 (O/G FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 85 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
91 | 1CA | B01Q400 | 10.1.01 | 1CA24AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 24 (O/G FDR) | AHP SWBD # 0CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-L1, MV07-L1, MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV46-L1, MV61-L1, MV60-R1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM21-R1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
92 | 1CA | B01Q400 | 10.1.01 | 1CA24AP02 | 6.6kV UNIT SWBD # 1CA PANEL NO 24 (O/G FDR) | AHP SWBD # 0CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-L1, MV07-L1, MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV46-L1, MV61-L1, MV60-R1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM21-R1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
93 | 1CA | B01Q400 | 10.1.01 | 1CA24AP03 | 6.6kV UNIT SWBD # 1CA PANEL NO 24 (O/G FDR) | AHP SWBD # 0CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-L1, MV07-L1, MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV46-L1, MV61-L1, MV60-R1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM21-R1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
94 | 1CA | B01Q400 | 10.1.01 | 1CA24AP04 | 6.6kV UNIT SWBD # 1CA PANEL NO 24 (O/G FDR) | AHP SWBD # 0CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 382 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-R1, MV07-R1, MV08-R1, MV26-R1, MV27-R1, MV44-R1, MV45-R1, MV46-R1, MV61-R1, MV60-L1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
95 | 1CA | B01Q400 | 10.1.01 | 1CA24AP05 | 6.6kV UNIT SWBD # 1CA PANEL NO 24 (O/G FDR) | AHP SWBD # 0CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 382 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-R1, MV07-R1, MV08-R1, MV26-R1, MV27-R1, MV44-R1, MV45-R1, MV46-R1, MV61-R1, MV60-L1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
96 | 1CA | B01Q400 | 10.1.01 | 1CA24AP06 | 6.6kV UNIT SWBD # 1CA PANEL NO 24 (O/G FDR) | AHP SWBD # 0CC SEC-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 382 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-R1, MV07-R1, MV08-R1, MV26-R1, MV27-R1, MV44-R1, MV45-R1, MV46-R1, MV61-R1, MV60-L1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
97 | 1CA | D03L2.5 | 10.4.26 | 1CA25AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 25 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 31 | 60 | 17.03.2020 | DR1050_0012 |  |  | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV11-02, MV73-03, MV72-03, MV71-03, MV70-03, MV48-02 |  | BPL | EPD
98 | 1CA | D02C1.5 | 10.5.01 | 1CA25AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 25 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 31 | 60 | 17.03.20 | DR1150_17PA011783 |  |  | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV11-02, MV73-03, MV72-03, MV71-03, MV70-03, MV48-02 |  | BPL | EPD
99 | 1CA | D05C1.5 | 10.5.06 | 1CA25AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 25 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 33 | 32 | 17.03.2020 | DR1150_17PA011779 |  |  | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV11-02, MV73-03, MV72-03, MV29-L2, MV65-05, ZZ99- |  | BPL | JHS
100 | 1CA | E04V0.5 | 10.7.02 | 1CA25AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 25 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 85 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
101 | 1CA | B03Q150 | 10.1.02 | 1CA25AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 25 (O/G T/F FDR) | UNIT SERV TRF # 1DAT01 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 29 | 37 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV06-R1, MV07-R1, MV08-R1, MV26-R1, MV27-R1, MV28-R1, MV65-01, ZZ99- |  | BPL | JHS
102 | 1CA | D05C1.5 | 10.5.06 | 1CA27AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 27 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 606 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV11-02, MV12-02, MV81-03, MV80-03, MV79-03, MV78-03, MV77-03, MV76-03, MR05-L3, TY24-R2, TY23-R2, TY22-R2, TY21-R2, TY20-R2, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW18-02 |  | BPL | EPD
103 | 1CA | D02L2.5 | 10.4.24 | 1CA27AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 27 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 606 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV11-02, MV12-02, MV81-03, MV80-03, MV79-03, MV78-03, MV77-03, MV76-03, MR05-L3, TY24-R2, TY23-R2, TY22-R2, TY21-R2, TY20-R2, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW18-02 |  | BPL | BPL
104 | 1CA | B03Q150 | 10.1.02 | 1CA27AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 27 (MOTOR FDR) | HYDRANT PUMP-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 597 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-L1, MV05-L1, MV82-01, MV81-01, MV80-01, MV79-01, MV78-01, MV77-01, MV76-01, MR05-L1, TY24-R1, TY23-R1, TY22-R1, TY21-R1, TY20-R1, IP01-L1, IP02-L1, IR03-L1, IP14-R1, IP15-L1, IP16-L1, IP17-L1, IP18-L1, IP19-L1, IR38-L1, IP23-L1, IP24-L1, IP25-L1, IP26-L1, IP27-L1, IP28-L1, IP29-L1, IP30-L1, IP31-L1, IP32-L1, IP33-L1, IP34-L1, IP36-L1, IP37-L1, IP38-L1, IR04-L1, IP39-L1, IP40-L1, IP41-L1, IP42-L1, IP43-L1, IP44-L1, IP45-L1, IP46-L1, IP47-L1, IP48-L1, IP49-L1, IP50-L1, IR05-L1, IP51-L1, IP52-L1, IP53-01, IP54-01, IP56-01, IP57-01, IP58-01, IP59-01, IP60-01, IP61-01, ZR01-01, FW01-01, FW02-01, FW03-01, FW04-01, FW05-01, FW08-01, FW09-01, FW10-01, FW11-01, FW18-01, ZZ99- |  | BPL | BPL
105 | 1CA | D05C1.5 | 10.5.06 | 1CA28AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 28 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 620 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV11-02, MV12-02, MV81-03, MV80-03, MV79-03, MV78-03, MV77-03, MV76-03, MR05-L3, TY24-R2, TY23-R2, TY22-R2, TY21-R2, TY20-R2, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, FW15-02 |  | BPL | EPD
106 | 1CA | D02L2.5 | 10.4.24 | 1CA28AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 28 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 620 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV11-02, MV12-02, MV81-03, MV80-03, MV79-03, MV78-03, MV77-03, MV76-03, MR05-L3, TY24-R2, TY23-R2, TY22-R2, TY21-R2, TY20-R2, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, FW15-02 |  | BPL | BPL
107 | 1CA | B03Q150 | 10.1.02 | 1CA28AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 28 (MOTOR FDR) | SPRAY PUMP-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 612 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-L1, MV05-L1, MV82-01, MV81-01, MV80-01, MV79-01, MV78-01, MV77-01, MV76-01, MR05-L1, TY24-R1, TY23-R1, TY22-R1, TY21-R1, TY20-R1, IP01-L1, IP02-L1, IR03-L1, IP14-R1, IP15-L1, IP16-L1, IP17-L1, IP18-L1, IP19-L1, IR38-L1, IP23-L1, IP24-L1, IP25-L1, IP26-L1, IP27-L2, IP28-L1, IP29-L1, IP30-L1, IP31-L1, IP32-L1, IP33-L2, IP34-L1, IP36-L1, IP37-L1, IP38-L1, IR04-L1, IP39-L1, IP40-L1, IP41-L1, IP42-L1, IP43-L1, IP44-L1, IP45-L1, IP46-L1, IP47-L1, IP48-L1, IP49-L1, IP50-L1, IR05-L1, IP51-L1, IP52-L1, IP53-01, IP54-01, IP56-01, IP57-01, IP58-01, IP59-01, IP60-01, IP61-01, ZR01-01, FW01-01, FW02-01, FW03-01, FW04-01, FW05-01, FW08-01, FW09-01, FW10-01, FW11-01, FW12-01, FW13-01, FW14-01, FW15-01, ZZ99- |  | BPL | BPL
108 | 1CA | E04V0.5 | 10.7.02 | 1CA29AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 29 (O/G FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 84 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
109 | 1CA | D03L2.5 | 10.4.26 | 1CA30AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 30 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 1263 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV11-02, MV73-03, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, ZZ99- |  | BPL | EPD
110 | 1CA | D02C1.5 | 10.5.01 | 1CA30AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 30 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 1263 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV11-02, MV73-03, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, ZZ99- |  | BPL | EPD
111 | 1CA | D05C1.5 | 10.5.06 | 1CA30AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 30 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 1263 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV11-02, MV73-03, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, ZZ99- |  | BPL | JHS
112 | 1CA | E04V0.5 | 10.7.02 | 1CA30AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 30 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 84 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV11-03, MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
113 | 1CA | D05C1.5 | 10.5.06 | 1CA31AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 31 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 242 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV11-02, MV73-03, MV72-03, MV71-03, MV70-03, MV69-03, MV59-R1, MV62-05, MR06-05, IM01-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IR34-02, IM97-02, IM98-02 |  | BPL | EPD
114 | 1CA | D02L2.5 | 10.4.24 | 1CA31AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 31 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 242 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV11-02, MV73-03, MV72-03, MV71-03, MV70-03, MV69-03, MV59-R1, MV62-05, MR06-05, IM01-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IR34-02, IM97-02, IM98-02 |  | BPL | BPL
115 | 1CA | B03Q150 | 10.1.02 | 1CA31AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 31 (MOTOR FDR) | MILL-1E | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 246 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV06-L1, MV07-L1, MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV46-L1, MV61-L1, MV60-R1, MV62-04, MR06-04, IM01-01, IR17-01, IM01-01, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R2, IM12-R2, IM64-01, IM65-01, IM66-01, IM67-01, IM68-01, IM72-01, IM75-01, IR28-01, IM76-01, IM77-01, IM78-01, IR32-01, IM79-01, IM80-01, IM85-01, IM86-01, IM87-01, IR34-01, IM97-01, IM98-01, ZZ99- |  | BPL | BPL
116 | 1CA | D05C1.5 | 10.5.06 | 1CA32AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 32 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 258 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IR15-02, IC41-03, IC43-03 |  | BPL | EPD
117 | 1CA | D02L2.5 | 10.4.24 | 1CA32AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 32 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 258 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IR15-02, IC41-03, IC43-03 |  | BPL | BPL
118 | 1CA | B03Q150 | 10.1.02 | 1CA32AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 32 (MOTOR FDR) | MILL-1C | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 254 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV07-L1, MV08-R1, MV26-R1, MV27-R1, MA06-01, MR09-01, LV77-01, LR10-L1, IC01-L1, IC02-L1, IC03-L1, IC04-L1, IC05-L1, IC06-L1, IC07-L1, IR08-01, IC08-01, IC09-01, IC10-01, IC11-01, IC12-01, IC13-01, IR09-01, IC24-01, IC25-01, IC26-01, IR11-01, IC27-01, IC28-01, IR12-01, IC29-01, IC33-01, IC34-01, IC38-01, IC39-01, IC40-01, IR15-01, IC41-01, IC43-01, ZZ99- |  | BPL | BPL
119 | 1CA | D05C1.5 | 10.5.06 | 1CA33AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 33 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 231 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IR13-02, IC30-03, IC32-03 |  | BPL | EPD
120 | 1CA | D02L2.5 | 10.4.24 | 1CA33AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 33 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 231 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IR13-02, IC30-03, IC32-03 |  | BPL | BPL
121 | 1CA | B03Q150 | 10.1.02 | 1CA33AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 33 (MOTOR FDR) | MILL-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 228 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV07-L1, MV08-R1, MV26-R1, MV27-R1, MA06-01, MR09-01, LV77-01, LR10-L1, IC01-L1, IC02-L1, IC03-L1, IC04-L1, IC05-L1, IC06-L1, IC07-L1, IR08-01, IC08-01, IC09-01, IC10-01, IC11-01, IC12-01, IC13-01, IR09-01, IC24-01, IC25-01, IC26-01, IR11-01, IC27-01, IC28-01, IR12-01, IC29-01, IR13-01, IC30-01, IC32-01, ZZ99- |  | BPL | BPL
122 | 1CA | D03L2.5 | 10.4.26 | 1CA34AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 34 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 290 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV10-02, MV67-05, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES30-02, ER01-02, ES76-02, ES79-L3, ES65-02 |  | BPL | EPD
123 | 1CA | D02C1.5 | 10.5.01 | 1CA34AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 34 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 290 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV10-02, MV67-05, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES30-02, ER01-02, ES76-02, ES79-L3, ES65-02 |  | BPL | EPD
124 | 1CA | D05C1.5 | 10.5.06 | 1CA34AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 34 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 284 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV10-02, MV67-05, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES30-02, ER01-02, ES76-02, ES79-L3 |  | BPL | JHS
125 | 1CA | E04V0.5 | 10.7.02 | 1CA34AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 34 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 53 | 83 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
126 | 1CA | B03Q150 | 10.1.02 | 1CA34AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 34 (O/G T/F FDR) | ESP SERV TRF # 1DBT02 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 276 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV07-L1, MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV43-01, MV64-01, MV63-01, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM60-L1, IM61-L1, IM62-L1, IM63-L1, IR25-L1, ES01-L1, ES02-01, ES30-01, ER01-01, ES76-01, ES79-L1, ZZ99- |  | BPL | JHS
127 | 1CA | D03L2.5 | 10.4.26 | 1CA35AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 35 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 312 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV10-02, MV67-05, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES16-02, ES15-02, ES14-02, ES13-02, ES44-L3, ER06-02, ES90-02, ES53-L3, ES54-L3, ES55-L3 |  | BPL | EPD
128 | 1CA | D02C1.5 | 10.5.01 | 1CA35AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 35 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 312 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV10-02, MV67-05, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES16-02, ES15-02, ES14-02, ES13-02, ES44-L3, ER06-02, ES90-02, ES53-L3, ES54-L3, ES55-L3 |  | BPL | EPD
129 | 1CA | D05C1.5 | 10.5.06 | 1CA35AC03 | 6.6kV UNIT SWBD # 1CA PANEL NO 35 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 314 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV10-02, MV67-05, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES30-02, ER01-02, ES76-02, ES79-L3, ES95-L3, ES60-02, ES59-02, ES58-02, ES57-02, ES56-L3 |  | BPL | JHS
130 | 1CA | E04V0.5 | 10.7.02 | 1CA35AC04 | 6.6kV UNIT SWBD # 1CA PANEL NO 35 (O/G T/F FDR) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 53 | 83 | 13.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV10-03, MV09-03, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
131 | 1CA | B03Q150 | 10.1.02 | 1CA35AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 35 (O/G T/F FDR) | ESP SERV TRF # 1DBT01 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 305 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV07-L1, MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV43-01, MV64-01, MV63-01, MV62-01, MR06-01, IM02-L1, IM94-L1, IM95-L1, IM96-L1, IM11-L1, IM12-L1, IM13-L1, IM14-L1, IM15-L1, IM16-L1, IM17-L1, IM18-L1, IM19-L1, IM20-L1, IM60-L1, IM61-L1, IM62-L1, IM63-L1, IR25-L1, ES01-L1, ES02-01, ES30-01, ER01-01, ES76-01, ES79-L1, ES95-L1, ES60-01, ES59-01, ES58-01, ES57-01, ES56-L1, ZZ99- |  | BPL | JHS
132 | 1CA | D05C1.5 | 10.5.06 | 1CA36AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 36 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | 200 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC18-02 |  | BPL | EPD
133 | 1CA | D02L2.5 | 10.4.24 | 1CA36AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 36 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 167 | 171 | 14.02.20 | DR1006_0001 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC18-02 |  | BPL | BPL
134 | 1CA | B03Q150 | 10.1.02 | 1CA36AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 36 (MOTOR FDR) | PA FAN-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 165 | 165 | 15.01.20 | DR1658_2147483647B |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV07-R1, MV08-R1, MV26-R1, MV27-R1, MA06-01, MR09-01, LV77-01, LR10-L1, IC01-L1, IC02-L1, IC03-L1, IC04-L1, IC05-L1, IC06-L1, IC07-L1, IR08-01, IC08-01, IC09-01, IC10-01, IC11-01, IC12-01, IC13-01, IR10-01, IC14-L1, IC17-L1, IC18-01, ZZ99- |  | BPL | BPL
135 | 1CA | D05C1.5 | 10.5.06 | 1CA37AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 37 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 174 | 205 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC19-L2, IC22-02, IC23-02 |  | BPL | EPD
136 | 1CA | D02L2.5 | 10.4.24 | 1CA37AC02 | 6.6kV UNIT SWBD # 1CA PANEL NO 37 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 174 | 178 | 14.02.20 | DR1006_0001 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV10-02, MV09-02, MV26-L2, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC19-L2, IC22-02, IC23-02 |  | BPL | BPL
137 | 1CA | B03Q150 | 10.1.02 | 1CA37AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 37 (MOTOR FDR) | FD FAN-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 173 | 168 | 15.01.20 | DR1658_2147483647B |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV07-R1, MV08-R1, MV26-R1, MV27-R1, MA06-01, MR09-01, LV77-01, LR10-L1, IC01-L1, IC02-L1, IC03-L1, IC04-L1, IC05-L1, IC06-L1, IC07-L1, IR08-01, IC08-01, IC09-01, IC10-01, IC11-01, IC12-01, IC13-01, IR10-01, IC14-L1, IC17-L1, IC19-L1, IC22-01, IC23-01, ZZ99- |  | BPL | BPL
138 | 1CA | D05C1.5 | 10.5.06 | 1CA38AC01 | 6.6kV UNIT SWBD # 1CA PANEL NO 38 (O/G T/F FDR) | VFD TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 294 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV09-02, MV67-05, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES17-02, ES18-02, ES19-02, ES20-02, ES21-02, ES08-02 |  | BPL | EDN
139 | 1CA | B03Q240 | 10.1.03 | 1CA38AP01 | 6.6kV UNIT SWBD # 1CA PANEL NO 38 (O/G T/F FDR) | VFD TRF (ID FAN-1A) | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 293 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV46-L1, MV61-L1, MV60-R1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM60-R1, IM61-R1, IM62-R1, IM63-R1, IR25-R1, ES01-R1, ES96-01, ES16-01, ES15-01, ES14-01, ES13-01, ES12-01, ES11-01, ES10-01, ZZ99- |  | BPL | BPL
140 | 1CA | B03Q240 | 10.1.03 | 1CA38AP02 | 6.6kV UNIT SWBD # 1CA PANEL NO 38 (O/G T/F FDR) | VFD TRF (ID FAN-1A) | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 293 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV46-L1, MV61-L1, MV60-R1, MV62-04, MR06-04, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R2, IM12-R2, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM60-R2, IM61-R2, IM62-R2, IM63-R2, IR25-R1, ES01-R1, ES96-01, ES16-01, ES15-01, ES14-01, ES13-01, ES12-01, ES11-01, ES10-01, ZZ99- |  | BPL | BPL
141 | 1CA | B03Q240 | 10.1.03 | 1CA38AP03 | VFD TRF (ID FAN-1A) I/P BKR. Q1 | VFD Panel | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 24 | 28 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | ES10-01, ES11-01, ES12-01, ZZ99- |  | BPL | EDN
142 | 1CA | B03Q240 | 10.1.03 | 1CA38AP04 | VFD TRF (ID FAN-1A) I/P BKR. Q1 | VFD Panel | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 24 | 28 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | ES10-01, ES11-01, ES12-01, ZZ99- |  | BPL | EDN
143 | 1CA | B03Q240 | 10.1.03 | 1CA38AP05 | VFD Panel | VFD TRF (ID FAN-1A) O/P BKR. Q2 | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 23 | 28 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | ES12-01, ES11-01, ES10-01, ZZ99- |  | BPL | BPL
144 | 1CA | B03Q240 | 10.1.03 | 1CA38AP06 | VFD Panel | VFD TRF (ID FAN-1A) O/P BKR. Q2 | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 23 | 28 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | ES12-01, ES11-01, ES10-01, ZZ99- |  | BPL | BPL
145 | 1CA | B03Q240 | 10.1.03 | 1CA38AP07 | VFD TRF (ID FAN-1A) O/P BKR. Q2 | ID FAN-1A | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 237 | 139 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | ES10-01, ES11-01, ES35-L1, ES24-L1, ES25-L1, ES26-L1, ES16-01, ES96-01, ES01-L1, IR25-L1, IM63-L2, IM62-L2, IM61-L2, IM60-L2, IM21-R1, IM32-R1, IM33-R1, IR31-R1, IM34-R1, IM35-R1, IM36-R1, IM37-R1, IM38-R1, IR22-R1, IM39-R1, IM40-R1, IM41-R1, IM42-R1, IM43-R1, IR30-01, IM44-01, IM45-01, ZZ99- |  | BPL | BPL
146 | 1CA | B03Q240 | 10.1.03 | 1CA38AP08 | VFD TRF (ID FAN-1A) O/P BKR. Q2 | ID FAN-1A | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 240 | 139 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | ES10-02, ES11-02, ES35-L1, ES24-L2, ES25-L1, ES26-L1, ES16-01, ES96-01, ES01-L1, IR25-L1, IM63-L2, IM62-L2, IM61-L2, IM60-L2, IM21-R1, IM32-R1, IM33-R1, IR31-R1, IM34-R1, IM35-R1, IM36-R1, IM37-R1, IM38-R1, IR22-R1, IM39-R1, IM40-R1, IM41-R1, IM42-R1, IM43-R1, IR30-01, IM44-02, IM45-02, ZZ99- |  | BPL | BPL
1 | 1CB | D05C1.5 | 10.5.06 | 1CB01AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 01 (O/G T/F FDR) | VFD TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 290 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV25-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES16-02, ES26-L3, ES25-L3, ES24-L3, ES23-L3, ES38-L3 |  | BPL | EDN
2 | 1CB | B03Q240 | 10.1.03 | 1CB01AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 01 (O/G T/F FDR) | VFD TRF (ID FAN-1B) | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 283 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV29-L1, MV65-01, MV64-01, MV63-01, MV62-02, MR06-02, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L2, IM12-L2, IM13-L2, IM14-L2, IM15-L2, IM16-L2, IM17-L2, IM18-L2, IM19-L2, IM20-L2, IM60-L2, IM61-L2, IM62-L2, IM63-L2, IR25-L1, ES01-L1, ES96-01, ES16-01, ES26-L1, ES25-L1, ES24-L1, ES23-L1, ES38-L1, ZZ99- |  | BPL | BPL
3 | 1CB | B03Q240 | 10.1.03 | 1CB01AP02 | 6.6kV UNIT SWBD # 1CB PANEL NO 01 (O/G T/F FDR) | VFD TRF (ID FAN-1B) | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 284 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV29-L1, MV65-01, MV64-01, MV63-01, MV62-01, MR06-01, IM02-R1, IM94-R2, IM95-R2, IM96-R2, IM11-R1, IM12-R1, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM60-R1, IM61-R1, IM62-R1, IM63-R1, IR25-R1, ES01-R1, ES96-01, ES16-01, ES26-L1, ES25-L1, ES24-L1, ES23-L1, ES38-L1, ZZ99- |  | BPL | BPL
4 | 1CB | B03Q240 | 10.1.03 | 1CB01AP03 | VFD TRF (ID FAN-1B) I/P BKR. Q1 | VFD Panel | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 31 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | ES38-L1, ES23-L1, ES24-L1, ES31-R1, ES13-01, ZZ99- |  | BPL | EDN
5 | 1CB | B03Q240 | 10.1.03 | 1CB01AP04 | VFD TRF (ID FAN-1B) I/P BKR. Q1 | VFD Panel | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 31 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | ES38-L1, ES23-L1, ES24-L1, ES31-R1, ES13-01, ZZ99- |  | BPL | EDN
6 | 1CB | B03Q240 | 10.1.03 | 1CB01AP05 | VFD Panel | VFD TRF (ID FAN-1B) O/P BKR. Q2 | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 29 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | ES13-01, ES31-L1, ES24-R1, ES23-R1, ES38-R1, ZZ99- |  | BPL | BPL
7 | 1CB | B03Q240 | 10.1.03 | 1CB01AP06 | VFD Panel | VFD TRF (ID FAN-1B) O/P BKR. Q2 | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 29 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | ES13-01, ES31-L1, ES24-R1, ES23-R1, ES38-R1, ZZ99- |  | BPL | BPL
8 | 1CB | B03Q240 | 10.1.03 | 1CB01AP07 | VFD TRF (ID FAN-1B) O/P BKR. Q2 | ID FAN-1B | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 187 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | ES38-L1, ES39-L1, ES40-L1, ES05-01, ES04-01, ES03-01, ES02-01, ES01-L1, IR25-L1, IM63-R2, IM62-R2, IM61-R2, IM60-R2, IM21-L2, IM32-L1, IM33-L1, IR31-L2, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IR21-01, IM57-01, IM58-01, IM59-01, ZZ99- |  | BPL | BPL
9 | 1CB | B03Q240 | 10.1.03 | 1CB01AP08 | VFD TRF (ID FAN-1B) O/P BKR. Q2 | ID FAN-1B | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 186 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | ES38-L1, ES39-L1, ES40-L1, ES05-01, ES04-01, ES03-01, ES02-01, ES01-R1, IR25-R1, IM63-R2, IM62-R2, IM61-R2, IM60-R2, IM21-L2, IM32-L1, IM33-L1, IR31-L2, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IR21-01, IM57-01, IM58-01, IM59-01, ZZ99- |  | BPL | BPL
10 | 1CB | D05C1.5 | 10.5.06 | 1CB02AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 02 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 186 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM73-03, IR27-03, IM74-03 |  | BPL | EPD
11 | 1CB | D02L2.5 | 10.4.24 | 1CB02AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 02 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 186 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM73-03, IR27-03, IM74-03 |  | BPL | BPL
12 | 1CB | B03Q150 | 10.1.02 | 1CB02AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 02 (MOTOR FDR) | FD FAN-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 182 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV29-L1, MV28-L1, MV44-R1, MV45-R1, MV46-R1, MV61-R1, MV60-L1, MV62-03, MR06-03, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L2, IM12-L2, IM64-01, IM65-01, IM66-01, IM67-01, IM68-01, IM72-01, IM73-01, IR27-01, IM74-01, ZZ99- |  | BPL | BPL
13 | 1CB | D05C1.5 | 10.5.06 | 1CB03AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 03 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 172 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IN01-02, IR29-02, IN02-02 |  | BPL | EPD
14 | 1CB | D02L2.5 | 10.4.24 | 1CB03AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 03 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 172 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IN01-02, IR29-02, IN02-02 |  | BPL | BPL
15 | 1CB | B03Q150 | 10.1.02 | 1CB03AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 03 (MOTOR FDR) | PA FAN-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 167 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV29-L1, MV28-L1, MV44-R1, MV45-R1, MV46-R1, MV61-R1, MV60-L1, MV62-03, MR06-03, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L2, IM12-L2, IM64-01, IM65-01, IM66-01, IM67-01, IN01-01, IR29-01, IN02-01, ZZ99- |  | BPL | BPL
16 | 1CB | D03L2.5 | 10.4.26 | 1CB04AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 04 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 292 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES16-02, ES15-02, ES14-02, ES43-L3, ER05-R2, ES93-L3, ES52-L3 |  | BPL | EPD
17 | 1CB | D02C1.5 | 10.5.01 | 1CB04AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 04 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 292 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES16-02, ES15-02, ES14-02, ES43-L3, ER05-R2, ES93-L3, ES52-L3 |  | BPL | EPD
18 | 1CB | D05C1.5 | 10.5.06 | 1CB04AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 04 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 292 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES16-02, ES15-02, ES14-02, ES43-L3, ER05-R2, ES93-L3, ES52-L3 |  | BPL | JHS
19 | 1CB | E04V0.5 | 10.7.02 | 1CB04AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 04 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 72 | 14.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
20 | 1CB | B03Q150 | 10.1.02 | 1CB04AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 04 (O/G T/F FDR) | ESP SERV TRF # 1DBT03 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 282 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV29-L1, MV65-01, MV64-01, MV63-01, MV62-02, MR06-02, IM02-L1, IM94-L1, IM95-L1, IM96-L2, IM11-L2, IM12-L2, IM13-L2, IM14-L2, IM15-L2, IM16-L2, IM17-L2, IM18-L2, IM19-L2, IM20-L2, IM60-L1, IM61-L1, IM62-L1, IM63-L1, IR25-L1, ES01-L1, ES96-01, ES16-01, ES15-01, ES14-01, ES43-L1, ER05-R1, ES93-L1, ES52-L1, ZZ99- |  | BPL | JHS
21 | 1CB | D03L2.5 | 10.4.26 | 1CB05AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 05 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 303 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES30-02, ER01-02, ES76-02, ES74-L3, ES73-L3, ES72-L3, ES70-L3 |  | BPL | EPD
22 | 1CB | D02C1.5 | 10.5.01 | 1CB05AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 05 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 303 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES30-02, ER01-02, ES76-02, ES74-L3, ES73-L3, ES72-L3, ES70-L3 |  | BPL | EPD
23 | 1CB | D05C1.5 | 10.5.06 | 1CB05AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 05 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 303 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES30-02, ER01-02, ES76-02, ES74-L3, ES73-L3, ES72-L3, ES70-L3 |  | BPL | JHS
24 | 1CB | E04V0.5 | 10.7.02 | 1CB05AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 05 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 72 | 14.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
25 | 1CB | B03Q150 | 10.1.02 | 1CB05AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 05 (O/G T/F FDR) | ESP SERV TRF # 1DBT04 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 294 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV29-L1, MV65-01, MV64-01, MV63-01, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R1, IM12-R1, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM60-R1, IM61-R1, IM62-R1, IM63-R1, IR25-R1, ES01-R1, ES02-01, ES30-01, ER01-01, ES76-01, ES74-L1, ES73-L1, ES72-L1, ES70-L1, ZZ99- |  | BPL | JHS
26 | 1CB | D05C1.5 | 10.5.06 | 1CB06AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 06 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 244 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV24-02, MV25-02, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IR14-02, IC35-03, IC37-03 |  | BPL | EPD
27 | 1CB | D02L2.5 | 10.4.24 | 1CB06AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 06 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 244 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV24-02, MV25-02, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IR14-02, IC35-03, IC37-03 |  | BPL | BPL
28 | 1CB | B03Q150 | 10.1.02 | 1CB06AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 06 (MOTOR FDR) | MILL-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 240 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV29-L1, MV28-L1, MA06-01, MR09-01, LV77-01, LR10-L1, IC01-L1, IC02-L1, IC03-L1, IC04-L1, IC05-L1, IC06-L1, IC07-L1, IR08-01, IC08-01, IC09-01, IC10-01, IC11-01, IC12-01, IC13-01, IR09-01, IC24-01, IC25-01, IC26-01, IR11-01, IC27-01, IC28-01, IR12-01, IC29-01, IC33-01, IC34-01, IR14-01, IC35-01, IC37-01, ZZ99- |  | BPL | BPL
29 | 1CB | D05C1.5 | 10.5.06 | 1CB07AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 07 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 271 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV72-03, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM93-02 |  | BPL | EPD
30 | 1CB | D02L2.5 | 10.4.24 | 1CB07AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 07 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 271 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV72-03, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM93-02 |  | BPL | BPL
31 | 1CB | B03Q150 | 10.1.02 | 1CB07AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 07 (MOTOR FDR) | MILL-1D | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 268 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV72-01, MV73-01, MV74-02, MV07-L1, MV08-L1, MV26-L1, MV27-L1, MV44-L1, MV45-L1, MV46-L1, MV61-L1, MV60-R1, MV62-03, MR06-03, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L3, IM12-L3, IM64-01, IM65-01, IM66-01, IM67-01, IM68-01, IM72-01, IM75-01, IR28-01, IM76-01, IM77-01, IM78-01, IR32-01, IM79-01, IM80-01, IM85-01, IM86-01, IM87-01, IM88-01, IM89-01, IR35-01, IM90-01, IM91-01, IM93-01 |  | BPL | BPL
32 | 1CB | D03L2.5 | 10.4.26 | 1CB08AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 08 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 1270 | [5 empty] | CT INPUT FOR 64R PROT.(For CHP SERV TRF # 3B) | XLPE-CU UNARMOURED | MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, ZZ99- |  | BPL | EPD
33 | 1CB | D02C1.5 | 10.5.01 | 1CB08AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 08 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 1270 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY (For CHP SERV TRF # 3B) | PVC-CU UNARMOURED | MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, ZZ99- |  | BPL | EPD
34 | 1CB | D05C1.5 | 10.5.06 | 1CB08AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 08 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 1270 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN (For CHP SERV | PVC-CU UNARMOURED | MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, ZZ99- |  | BPL | JHS
35 | 1CB | E04V0.5 | 10.7.02 | 1CB08AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 08 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 67 | 72 | 14.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) (For C | OVERALL SCREENED | MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
36 | 1CB | E04V0.5 | 10.7.02 | 1CB09AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 09 (O/G FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 67 | 71 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) (For F | OVERALL SCREENED | MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
37 | 1CB | D05C1.5 | 10.5.06 | 1CB10AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 10 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 249 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IR33-02, IM81-02, IM82-02, IM84-02 |  | BPL | EPD
38 | 1CB | D02L2.5 | 10.4.24 | 1CB10AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 10 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 249 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IR33-02, IM81-02, IM82-02, IM84-02 |  | BPL | BPL
39 | 1CB | B03Q150 | 10.1.02 | 1CB10AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 10 (MOTOR FDR) | MILL-1F | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 259 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-R1, MV72-01, MV73-01, MV74-02, MV07-R1, MV08-R1, MV26-R1, MV27-R1, MV44-R1, MV45-R1, MV46-R1, MV61-R1, MV60-L1, MV62-03, MR06-03, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L3, IM12-L3, IM64-01, IM65-01, IM66-01, IM67-01, IM68-01, IM72-01, IM75-01, IR28-01, IM76-01, IM77-01, IM78-01, IR32-01, IM79-01, IM80-01, IR33-01, IM81-01, IM82-01, IM84-01, ZZ99- |  | BPL | BPL
40 | 1CB | D05C1.5 | 10.5.06 | 1CB11AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 11 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 608 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV23-02, MV22-02, MV80-03, MV79-03, MV78-03, MV77-03, MV76-03, MR05-L3, TY24-R2, TY23-R2, TY22-R2, TY21-R2, TY20-R2, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW17-02 |  | BPL | EPD
41 | 1CB | D02L2.5 | 10.4.24 | 1CB11AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 11 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 608 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV23-02, MV22-02, MV80-03, MV79-03, MV78-03, MV77-03, MV76-03, MR05-L3, TY24-R2, TY23-R2, TY22-R2, TY21-R2, TY20-R2, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW17-02 |  | BPL | BPL
42 | 1CB | B03Q150 | 10.1.02 | 1CB11AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 11 (MOTOR FDR) | HYDRANT PUMP-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 595 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV31-L1, MV79-01, MV78-01, MV77-01, MV76-01, MR05-L1, TY24-R1, TY23-R1, TY22-R1, TY21-R1, TY20-R1, IP01-L1, IP02-L1, IR03-L1, IP14-R1, IP15-L1, IP16-L1, IP17-L1, IP18-L1, IP19-L1, IR38-L1, IP23-L1, IP24-L1, IP25-L1, IP26-L1, IP27-L1, IP28-L1, IP29-L1, IP30-L1, IP31-L1, IP32-L1, IP33-L1, IP34-L1, IP36-L1, IP37-L1, IP38-L1, IR04-L1, IP39-L1, IP40-L1, IP41-L1, IP42-L1, IP43-L1, IP44-L1, IP45-L1, IP46-L1, IP47-L1, IP48-L1, IP49-L1, IP50-L1, IR05-L1, IP51-L1, IP52-L1, IP53-01, IP54-01, IP56-01, IP57-01, IP58-01, IP59-01, IP60-01, IP61-01, ZR01-01, FW01-01, FW02-01, FW03-01, FW04-01, FW05-01, FW08-01, FW09-01, FW10-01, FW11-01, FW12-01, FW17-01, ZZ99- |  | BPL | BPL
43 | 1CB | D03L2.5 | 10.4.26 | 1CB13AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 13 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | 52 | 17.03.2020 | DR1050_0012 |  |  | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV23-02, MV72-03, MV71-03, MV70-03 |  | BPL | EPD
44 | 1CB | D02C1.5 | 10.5.01 | 1CB13AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 13 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 24 | 52 | 17.03.20 | DR1150_17PA011783 |  |  | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV23-02, MV72-03, MV71-03, MV70-03 |  | BPL | EPD
45 | 1CB | D05C1.5 | 10.5.06 | 1CB13AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 13 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | 33 | 17.03.2020 | DR1150_17PA011778 |  |  | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV23-02, MV72-03, MV71-03 |  | BPL | JHS
46 | 1CB | E04V0.5 | 10.7.02 | 1CB13AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 13 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 67 | 74 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
47 | 1CB | B03Q150 | 10.1.02 | 1CB13AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 13 (O/G T/F FDR) | UNIT SERV TRF # 1DAT02 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 20 | 25 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV71-01, ZZ99- |  | BPL | JHS
48 | 1CB | E04V0.5 | 10.7.02 | 1CB14AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 14 (O/G FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 67 | 74 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
49 | 1CB | B01Q400 | 10.1.01 | 1CB14AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 14 (O/G FDR) | AHP SWBD # 0CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV71-01, MV70-01, MV69-01, MV59-L1, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM21-R1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
50 | 1CB | B01Q400 | 10.1.01 | 1CB14AP02 | 6.6kV UNIT SWBD # 1CB PANEL NO 14 (O/G FDR) | AHP SWBD # 0CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV71-01, MV70-01, MV69-01, MV59-L1, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM21-R1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
51 | 1CB | B01Q400 | 10.1.01 | 1CB14AP03 | 6.6kV UNIT SWBD # 1CB PANEL NO 14 (O/G FDR) | AHP SWBD # 0CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV71-01, MV70-01, MV69-01, MV59-L1, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM21-R1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, ZZ99- |  | BPL | BPL
52 | 1CB | B01Q400 | 10.1.01 | 1CB14AP04 | 6.6kV UNIT SWBD # 1CB PANEL NO 14 (O/G FDR) | AHP SWBD # 0CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV71-01, MV70-01, MV69-01, MV59-L1, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM22-02, IM23-02, IM24-02, IM25-02, IM26-02, ZZ99- |  | BPL | BPL
53 | 1CB | B01Q400 | 10.1.01 | 1CB14AP05 | 6.6kV UNIT SWBD # 1CB PANEL NO 14 (O/G FDR) | AHP SWBD # 0CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV71-01, MV70-01, MV69-01, MV59-L1, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM22-02, IM23-02, IM24-02, IM25-02, IM26-02, ZZ99- |  | BPL | BPL
54 | 1CB | B01Q400 | 10.1.01 | 1CB14AP06 | 6.6kV UNIT SWBD # 1CB PANEL NO 14 (O/G FDR) | AHP SWBD # 0CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 379 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV71-01, MV70-01, MV69-01, MV59-L1, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM22-02, IM23-02, IM24-02, IM25-02, IM26-02, ZZ99- |  | BPL | BPL
55 | 1CB | D05C1.5 | 10.5.06 | 1CB15AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 15 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 46 | 47 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV23-02, MV22-02, MV21-02, MV91-03, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03 |  | BPL | EPD
56 | 1CB | D02L2.5 | 10.4.24 | 1CB15AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 15 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 46 | 55 | 07.12.19 | DR3111-11601 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV23-02, MV22-02, MV21-02, MV91-03, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03 |  | BPL | BPL
57 | 1CB | B03Q150 | 10.1.02 | 1CB15AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 15 (MOTOR FDR) | ACW PUMP-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 49 | 45 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV31-L1, MV32-R1, MV90-02, MV91-02, MV14-01, MV98-01, MV99-01, MR17-01, TG82-02, TG81-01, ZZ99- |  | BPL | BPL
58 | 1CB | D05C1.5 | 10.5.06 | 1CB16AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 16 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 29 | 58 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV23-02, MV85-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02 |  | BPL | EPD
59 | 1CB | D02L2.5 | 10.4.24 | 1CB16AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 16 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | 46 | 07.12.19 | DR3111-11601 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV23-02, MV85-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02 |  | BPL | BPL
60 | 1CB | B03Q150 | 10.1.02 | 1CB16AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 16 (MOTOR FDR) | DMCW PUMP-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 31 | 23 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV30-L1, MV84-01, MV85-01, MV86-01, MR18-01, MA04-01, TG21-01, TG20-01, ZZ99- |  | BPL | BPL
61 | 1CB | B01Q400 | 10.1.01 | 1CB17AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 17 (MOTOR FDR) | 1CA PANEL NO. 21 | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 19 | 22 | 43816 | DR2465_8012201003 |  |  | POWER CABLE (For MDBFP-1C) | XLPE-AL UNARMOURED | MV31-L1, MV80-01, MV81-01, MV82-01, MV05-L1, ZZ99- |  | BPL | BPL
62 | 1CB | B01Q400 | 10.1.01 | 1CB17AP02 | 6.6kV UNIT SWBD # 1CB PANEL NO 17 (MOTOR FDR) | 1CA PANEL NO. 21 | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 19 | 22 | 43816 | DR2465_8012201003 |  |  | POWER CABLE (For MDBFP-1C) | XLPE-AL UNARMOURED | MV31-L1, MV80-01, MV81-01, MV82-01, MV05-L1, ZZ99- |  | BPL | BPL
63 | 1CB | B01Q400 | 10.1.01 | 1CB17AP03 | 6.6kV UNIT SWBD # 1CB PANEL NO 17 (MOTOR FDR) | 1CA PANEL NO. 21 | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 19 | 23 | 43816 | DR2465_8012201003 |  |  | POWER CABLE (For MDBFP-1C) | XLPE-AL UNARMOURED | MV31-L1, MV80-01, MV81-01, MV82-01, MV05-L1, ZZ99- |  | BPL | BPL
64 | 1CB | D05C1.5 | 10.5.06 | 1CB19AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 19 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 75 | 71 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV21-02, MV22-02, MV85-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2 |  | BPL | EPD
65 | 1CB | D05C2.5 | 10.5.07 | 1CB19AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 19 (MOTOR FDR) | MOTOR TB | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | CT CONNECTION FOR MOTOR DIFF.PROTECTION | PVC-CU UNARMOURED | MV21-02, MV22-02, MV85-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2 |  | BPL | BPL
66 | 1CB | D02L2.5 | 10.4.24 | 1CB19AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 19 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 75 | 62 | 6.3.20 | DR1095_0045 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV21-02, MV22-02, MV85-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2 |  | BPL | BPL
67 | 1CB | B01Q400 | 10.1.01 | 1CB19AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 19 (MOTOR FDR) | MDBFP-1B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 82 | 62 | 43815 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV32-L1, MV90-01, MV91-01, MV92-01, MV03-R1, MV99-01, MR17-02, TG91-01, TG90-01, TG87-01, TG17-L1, TG15-L1, TG14-L1, TG13-L1, TG12-L1, TG11-L1, TG10-L1, ZZ99- |  | BPL | BPL
68 | 1CB | B01Q400 | 10.1.01 | 1CB19AP02 | 6.6kV UNIT SWBD # 1CB PANEL NO 19 (MOTOR FDR) | MDBFP-1B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 82 | 63 | 43815 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV32-L1, MV90-01, MV91-01, MV92-01, MV03-R1, MV99-01, MR17-02, TG91-01, TG90-01, TG87-01, TG17-L1, TG15-L1, TG14-L1, TG13-L1, TG12-L1, TG11-L1, TG10-L1, ZZ99- |  | BPL | BPL
69 | 1CB | B01Q400 | 10.1.01 | 1CB19AP03 | 6.6kV UNIT SWBD # 1CB PANEL NO 19 (MOTOR FDR) | MDBFP-1B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 82 | 63 | 43816 | DR2465_8012201003 |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV32-L1, MV90-01, MV91-01, MV92-01, MV03-R1, MV99-01, MR17-02, TG91-01, TG90-01, TG87-01, TG17-L1, TG15-L1, TG14-L1, TG13-L1, TG12-L1, TG11-L1, TG10-L1, ZZ99- |  | BPL | BPL
70 | 1CB | D05C1.5 | 10.5.06 | 1CB21AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 21 (O/G T/F FDR) | VFD TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV21-02, MV91-03, MV92-03, MV03-L2, MV99-04, MR16-05, TR48-05, LV64-05, LV63-05, LV13-L4, LV12-L4, LV52-02, LV51-02, LV29-L4 |  | BPL | EDN
71 | 1CB | B03Q150 | 10.1.02 | 1CB21AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 21 (O/G T/F FDR) | VFD TRF (CEP-1B) | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 63 | 77 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV32-R1, MV33-R1, MV34-R1, MA01-01, MR02-01, LV71-01, LV18-L1, LV19-L1, LV20-L1, LV21-L1, LV51-01, LV29-L1, ZZ99- |  | BPL | BPL
72 | 1CB | B03Q150 | 10.1.02 | 1CB21AP02 | VFD TRF (CEP-1B) I/P BKR. Q1 | VFD Panel | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 62 | 58 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | LV29-L1, LV28-L1, LV27-L1, LV26-L1, LV74-01, DC07-01, DC08-01, DC09-01, DC10-01, DC11-01, DR03-01, AC01-01, DR04-01, AC02-01, AC03-01, ZZ99- |  | BPL | EDN
73 | 1CB | B03Q150 | 10.1.02 | 1CB21AP03 | VFD Panel | VFD TRF (CEP-1B) O/P BKR. Q2 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 65 | 56 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | AC03-01, AC02-01, DR04-01, AC01-01, DR03-01, DC11-01, DC10-01, DC09-01, DC08-01, DC07-01, LV74-01, LV26-L1, LV27-L1, LV28-L1, LV29-L1, ZZ99- |  | BPL | BPL
74 | 1CB | B03Q150 | 10.1.02 | 1CB21AP04 | VFD TRF (CEP-1B) O/P BKR. Q2 | CEP-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 112 | 146 | 15.01.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | LV29-R1, LV51-01, LV52-01, LV53-01, LV54-01, TR49-01, MR14-01, TR01-01, TG87-02, TG17-L1, TG15-L2, TG14-L2, TG13-L2, TG12-L2, TG11-L2, TG10-L2, TG09-L1, TG08-L1, TG07-01, ZZ99- |  | BPL | BPL
75 | 1CB | D03L2.5 | 10.4.26 | 1CB26AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 26 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | 78 | 17.03.2020 | DR1050_0012 |  |  | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV20-02, MV90-03, MV89-03, MV88-03 |  | BPL | EPD
76 | 1CB | D02C1.5 | 10.5.01 | 1CB26AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 26 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 24 | 78 | 17.03.20 | DR1150_17PA011783 |  |  | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV20-02, MV90-03, MV89-03, MV88-03 |  | BPL | EPD
77 | 1CB | D05C1.5 | 10.5.06 | 1CB26AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 26 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 21 | 31 | 17.03.2020 | DR1150_17PA011779 |  |  | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV20-02, MV90-03, MV89-03 |  | BPL | JHS
78 | 1CB | E04V0.5 | 10.7.02 | 1CB26AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 26 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | 82 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
79 | 1CB | B03Q240 | 10.1.03 | 1CB26AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 26 (O/G T/F FDR) | STN SERV TRF # 0DAT02 | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 20 | 26 | 21.02.20 | DR1658_2147483647A |  |  | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV89-01, ZZ99- |  | BPL | JHS
80 | 1CB | E04V0.5 | 10.7.02 | 1CB27AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 27 (O/G FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | 81 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
81 | 1CB | B01Q400 | 10.1.01 | 1CB27AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 27 (O/G FDR) | CHP SWBD # 0CB SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1269 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV32-R1, MV79-02, MV78-02, MV77-02, MV58-L1, MV59-L1, MV62-03, MR06-03, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM32-R1, IM33-R1, IR31-R1, IM34-R1, IM35-R1, IM36-R1, IM37-R1, IM38-R1, IR22-R1, IM39-R1, IM40-R1, IM41-R1, IM42-R1, IM43-R1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
82 | 1CB | B01Q400 | 10.1.01 | 1CB27AP02 | 6.6kV UNIT SWBD # 1CB PANEL NO 27 (O/G FDR) | CHP SWBD # 0CB SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1269 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV32-R1, MV79-02, MV78-02, MV77-02, MV58-L1, MV59-L1, MV62-03, MR06-03, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM32-R1, IM33-R1, IR31-R1, IM34-R1, IM35-R1, IM36-R1, IM37-R1, IM38-R1, IR22-R1, IM39-R1, IM40-R1, IM41-R1, IM42-R1, IM43-R1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
83 | 1CB | B01Q400 | 10.1.01 | 1CB27AP03 | 6.6kV UNIT SWBD # 1CB PANEL NO 27 (O/G FDR) | CHP SWBD # 0CB SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1269 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV32-R1, MV79-02, MV78-02, MV77-02, MV58-L1, MV59-L1, MV62-03, MR06-03, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R2, IM12-R2, IM13-R2, IM14-R2, IM15-R2, IM16-R2, IM17-R2, IM18-R2, IM19-R2, IM20-R2, IM21-R2, IM32-R1, IM33-R1, IR31-R1, IM34-R1, IM35-R1, IM36-R1, IM37-R1, IM38-R1, IR22-R1, IM39-R1, IM40-R1, IM41-R1, IM42-R1, IM43-R1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
84 | 1CB | B01Q400 | 10.1.01 | 1CB27AP04 | 6.6kV UNIT SWBD # 1CB PANEL NO 27 (O/G FDR) | CHP SWBD # 0CB SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1269 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV32-R1, MV79-02, MV78-02, MV77-02, MV58-L1, MV59-L1, MV62-03, MR06-03, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L2, IM12-L2, IM13-L2, IM14-L2, IM15-L2, IM16-L2, IM17-L2, IM18-L2, IM19-L2, IM20-L2, IM21-L1, IM32-L1, IM33-L1, IR31-L2, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
85 | 1CB | B01Q400 | 10.1.01 | 1CB27AP05 | 6.6kV UNIT SWBD # 1CB PANEL NO 27 (O/G FDR) | CHP SWBD # 0CB SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1269 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV32-R1, MV79-02, MV78-02, MV77-02, MV58-L1, MV59-L1, MV62-03, MR06-03, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L2, IM12-L2, IM13-L2, IM14-L2, IM15-L2, IM16-L2, IM17-L2, IM18-L2, IM19-L2, IM20-L2, IM21-L1, IM32-L1, IM33-L1, IR31-L2, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
86 | 1CB | B01Q400 | 10.1.01 | 1CB27AP06 | 6.6kV UNIT SWBD # 1CB PANEL NO 27 (O/G FDR) | CHP SWBD # 0CB SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 1269 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV32-R1, MV79-02, MV78-02, MV77-02, MV58-L1, MV59-L1, MV62-03, MR06-03, IM02-L3, IM94-L2, IM95-L2, IM96-L2, IM11-L2, IM12-L2, IM13-L2, IM14-L2, IM15-L2, IM16-L2, IM17-L2, IM18-L2, IM19-L2, IM20-L2, IM21-L1, IM32-L1, IM33-L1, IR31-L2, IM34-L1, IM35-L1, IM36-L1, IM37-L1, IM38-L1, IR22-L1, IM39-L1, IM40-L1, IM41-L1, IM42-L1, IM43-L1, IM51-01, IM52-01, IM53-01, IR23-01, IM54-01, IM55-01, IM56-01, ZZ99- |  | BPL | BPL
87 | 1CB | D05C1.5 | 10.5.06 | 1CB28AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 28 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV20-02, MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR01-03, IP03-03, IP05-03, IP06-03, WR07-03, CW09-03, CW10-03, CW12-03, WR05-02, CW13-02 |  | BPL | EPD
88 | 1CB | D02L2.5 | 10.4.24 | 1CB28AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 28 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV20-02, MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR01-03, IP03-03, IP05-03, IP06-03, WR07-03, CW09-03, CW10-03, CW12-03, WR05-02, CW13-02 |  | BPL | BPL
89 | 1CB | B03Q240 | 10.1.03 | 1CB28AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 28 (MOTOR FDR) | CWP-1B | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 150 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV33-L1, MV34-L1, MV35-L1, MA02-01, MR03-01, LR03-01, TY16-L1, TY17-L1, TY18-L1, TY19-L1, IP01-L2, IP02-L2, IR01-01, IP03-01, IP05-01, IP06-01, WR07-01, CW09-01, CW10-01, CW12-01, WR05-01, CW13-01, ZZ99- |  | BPL | BPL
90 | 1CB | E04V0.5 | 10.7.02 | 1CB29AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 29 (TIE) | DDCMIS # CRE63 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | 82 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
91 | 1CB | E04V0.5 | 10.7.02 | 1CB29AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 29 (TIE) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | 82 | 14.09.2019 | DR0817_4798-4G-110 |  |  | LINE PT IN SERVICE | OVERALL SCREENED | MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
92 | 1CB | D02L2.5 | 10.4.24 | 1CB29AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 29 (TIE) | BTS-2 1CB - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 72 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV25-02, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, CR01-R3, CC71-05, CC51-03, CC50-03 |  | BPL | BPL
93 | 1CB | D05C1.5 | 10.5.06 | 1CB29AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 29 (TIE) | BTS-2 1CB - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 72 | [5 empty] | BREAKER OPEN & IN SERVICE, BREAKER CLOSE & IN SERVICE, 86 RE | PVC-CU UNARMOURED | MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV25-02, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, CR01-R3, CC71-05, CC51-03, CC50-03 |  | BPL | BPL
94 | 1CB | D02C1.5 | 10.5.01 | 1CB29AC05 | 6.6kV UNIT SWBD # 1CB PANEL NO 29 (TIE) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | 51N FOR REVERSE BLOCKING | PVC-CU UNARMOURED | MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV25-02, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, CR01-R3, CC71-05, CC51-03 |  | BPL | BPL
95 | 1CB | B03Q240 | 10.1.03 | 1CB30AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 30 (MOTOR FDR) | 1CA PANEL NO. 09 | 03C X 240 XLPE-Al FRLS ( 6.6 kV ) | 27 | [5 empty] | POWER CABLE (For CWP-1C) | XLPE-AL UNARMOURED | MV33-L1, MV96-01, MV97-01, MV98-01, MV02-L1, ZZ99- |  | BPL | BPL
96 | 1CB | D03L2.5 | 10.4.26 | 1CB31AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 31 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 477 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, FR01-03, FP01-03, FP03-L4, FP04-L4, FP05-L4, FP06-L4, FP22-02, FP21-02 |  | BPL | EPD
97 | 1CB | D02C1.5 | 10.5.01 | 1CB31AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 31 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 477 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, FR01-03, FP01-03, FP03-L4, FP04-L4, FP05-L4, FP06-L4, FP22-02, FP21-02 |  | BPL | EPD
98 | 1CB | D05C1.5 | 10.5.06 | 1CB31AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 31 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 478 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, IP37-L4, IP38-L4, IR04-L3, IP39-L3, IP40-L3, IP41-L3, IP42-L3, IP43-L3, IP44-L3, IP45-L3, IP46-L3, IP47-L3, IP48-L3, IP49-L3, IP50-L3, IR05-L3, IP51-L7, IP52-L7, FR01-03, FP01-03, FP03-L4, FP04-L4, FP05-L4, FP06-L4, FP07-02, FP08-02 |  | BPL | JHS
99 | 1CB | E04V0.5 | 10.7.02 | 1CB31AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 31 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 83 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
100 | 1CB | B03Q150 | 10.1.02 | 1CB31AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 31 (O/G T/F FDR) | PTP SERV TRF # 1DDT02 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 468 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MV35-L1, MA02-01, MR03-01, LR03-01, TY16-R1, TY17-R1, TY18-R1, TY19-R1, IP01-R1, IP02-R1, IR03-R1, IP14-L1, IP15-R1, IP16-R1, IP17-R1, IP18-R1, IP19-R1, IR38-R1, IP23-R1, IP24-R1, IP25-R1, IP26-R1, IP27-R1, IP28-R1, IP29-R1, IP30-R1, IP31-R1, IP32-R1, IP33-R1, IP34-R1, IP36-R1, IP37-R1, IP38-R1, IR04-R1, IP39-R1, IP40-R1, IP41-R1, IP42-R1, IP43-R1, IP44-R1, IP45-R1, IP46-R1, IP47-R1, IP48-R1, IP49-R1, IP50-R1, IR05-R1, IP51-R1, IP52-R1, FR01-01, FP01-01, FP03-L1, FP04-L1, FP05-L1, FP06-L1, FP07-01, FP08-01, ZZ99- |  | BPL | JHS
101 | 1CB | E04V0.5 | 10.7.02 | 1CB32AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 32 (O/G FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 83 | 14.09.2019 | DR0817_4798-4G-110 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
102 | 1CB | B01Q400 | 10.1.01 | 1CB32AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 32 (O/G FDR) | COMP. SWBD # 1CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 155 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MA01-01, MR02-01, LR02-01, TY14-L1, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-R1, CM05-R1, ZZ99- |  | BPL | BPL
103 | 1CB | B01Q400 | 10.1.01 | 1CB32AP02 | 6.6kV UNIT SWBD # 1CB PANEL NO 32 (O/G FDR) | COMP. SWBD # 1CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 155 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MA01-01, MR02-01, LR02-01, TY14-L1, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-R1, CM05-R1, ZZ99- |  | BPL | BPL
104 | 1CB | B01Q400 | 10.1.01 | 1CB32AP03 | 6.6kV UNIT SWBD # 1CB PANEL NO 32 (O/G FDR) | COMP. SWBD # 1CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 155 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MA01-01, MR02-01, LR02-01, TY14-L1, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-R1, CM05-R1, ZZ99- |  | BPL | BPL
105 | 1CB | B01Q400 | 10.1.01 | 1CB32AP04 | 6.6kV UNIT SWBD # 1CB PANEL NO 32 (O/G FDR) | COMP. SWBD # 1CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 155 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MA01-01, MR02-01, LR02-01, TY14-L1, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-R1, CM05-R1, ZZ99- |  | BPL | BPL
106 | 1CB | B01Q400 | 10.1.01 | 1CB32AP05 | 6.6kV UNIT SWBD # 1CB PANEL NO 32 (O/G FDR) | COMP. SWBD # 1CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 155 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MA01-01, MR02-01, LR02-01, TY14-L1, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-R1, CM05-R1, ZZ99- |  | BPL | BPL
107 | 1CB | B01Q400 | 10.1.01 | 1CB32AP06 | 6.6kV UNIT SWBD # 1CB PANEL NO 32 (O/G FDR) | COMP. SWBD # 1CC SEC-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 155 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MA01-01, MR02-01, LR02-01, TY14-L1, TY13-L1, TY12-L1, TY11-L1, TY36-01, TY37-01, TY38-01, TY39-01, YR03-01, TY40-01, TY41-01, TY42-01, TY43-01, NR01-01, CM04-R1, CM05-R1, ZZ99- |  | BPL | BPL
108 | 1CB | E04V0.5 | 10.7.02 | 1CB33AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 33 (BUS PT) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 107 | 14.09.2019 | DR0817_4798-4G-30 |  |  | BUS PT IN SERVICE, N/V | OVERALL SCREENED | MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
109 | 1CB | D02L2.5 | 10.4.24 | 1CB33AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 33 (BUS PT) | BTS-2 1CB - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV19-02, MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV25-02, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, CR01-R3, CC71-05, CC51-03, CC50-03 |  | BPL | BPL
110 | 1CB | D03C1.5 | 10.5.03 | 1CB33AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 33 (BUS PT) | BTS-2 1CB - 0CA | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | BUS PT IN SERVICE, BUS PT MCB HEALTHY | PVC-CU UNARMOURED | MV19-02, MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV25-02, MV27-L2, MA06-03, MR09-03, LV77-03, LR10-L4, CR01-R3, CC71-05, CC51-03, CC50-03 |  | BPL | BPL
111 | 1CB | D03L2.5 | 10.4.26 | 1CB34AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 34 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 482 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV19-02, MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-03, IM28-03, IM29-03, IM30-03, IM31-03, IR37-03, IL01-03, IL02-03, IL03-03, IL04-03, IL05-03, IL06-03, IL07-03, IL08-03, IL09-03, PR01-03, ET01-L4, ET02-L4, ET03-L4, ET04-L4, ET05-L4 |  | BPL | EPD
112 | 1CB | D02C1.5 | 10.5.01 | 1CB34AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 34 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 482 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV19-02, MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-03, IM28-03, IM29-03, IM30-03, IM31-03, IR37-03, IL01-03, IL02-03, IL03-03, IL04-03, IL05-03, IL06-03, IL07-03, IL08-03, IL09-03, PR01-03, ET01-L4, ET02-L4, ET03-L4, ET04-L4, ET05-L4 |  | BPL | EPD
113 | 1CB | D05C1.5 | 10.5.06 | 1CB34AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 34 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 474 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV19-02, MV20-02, MV21-02, MV22-02, MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-02, MV62-05, MR06-05, IM02-L5, IM94-L6, IM95-L6, IM96-L6, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-03, IM28-03, IM29-03, IM30-03, IM31-03, IR37-03, IL01-03, IL02-03, IL03-03, IL04-03, IL05-03, IL06-03, IL07-03, IL08-03, IL09-03, PR01-03, ET23-02, ET24-02, ET25-02 |  | BPL | JHS
114 | 1CB | E04V0.5 | 10.7.02 | 1CB34AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 34 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 118 | 14.09.2019 | DR0817_4798-4G-30 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
115 | 1CB | B03Q150 | 10.1.02 | 1CB34AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 34 (O/G T/F FDR) | ETP SERV TRF # 1DET02 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 468 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-R1, MV33-R1, MV32-R1, MV31-R1, MV30-R1, MV29-L1, MV65-01, MV64-01, MV63-01, MV62-02, MR06-02, IM02-L2, IM94-R1, IM95-R1, IM96-R1, IM11-R1, IM12-R1, IM13-R1, IM14-R1, IM15-R1, IM16-R1, IM17-R1, IM18-R1, IM19-R1, IM20-R1, IM21-R1, IM22-01, IM23-01, IM24-01, IM25-01, IM26-01, IM27-01, IM28-01, IM29-01, IM30-01, IM31-01, IR37-01, IL01-01, IL02-01, IL03-01, IL04-01, IL05-01, IL06-01, IL07-01, IL08-01, IL09-01, PR01-01, ET23-01, ET24-01, ET25-01, ZZ99- |  | BPL | JHS
116 | 1CB | D03L2.5 | 10.4.26 | 1CB35AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 35 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 148 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV19-02, MV18-L2, MA01-03, MR02-03, LR02-03, TY15-L4, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | EPD
117 | 1CB | D02C1.5 | 10.5.01 | 1CB35AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 35 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 148 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV19-02, MV18-L2, MA01-03, MR02-03, LR02-03, TY15-L4, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | EPD
118 | 1CB | D05C1.5 | 10.5.06 | 1CB35AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 35 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV19-02, MV18-L2, MA01-03, MR02-03, LR02-03, TY15-L4, TY16-L4, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY33-02 |  | BPL | JHS
119 | 1CB | E04V0.5 | 10.7.02 | 1CB35AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 35 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 109 | 14.09.2019 | DR0817_4798-4G-30 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
120 | 1CB | B03Q150 | 10.1.02 | 1CB35AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 35 (O/G T/F FDR) | SWYD SERV TRF | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 133 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MA01-01, MR02-01, LR02-01, TY15-L1, TY16-L1, TY17-L1, TY18-L1, YR02-01, TY25-01, TY26-01, TY28-01, TY29-01, TY30-01, TY31-01, TY32-01, TY33-01, ZZ99- |  | BPL | JHS
121 | 1CB | D03L2.5 | 10.4.26 | 1CB36AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 36 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 292 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP35-L3, HR01-L3, CT01-L3, CT02-L3, CT03-L3, CT04-L3, CT05-L3 |  | BPL | EPD
122 | 1CB | D02C1.5 | 10.5.01 | 1CB36AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 36 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 292 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP35-L3, HR01-L3, CT01-L3, CT02-L3, CT03-L3, CT04-L3, CT05-L3 |  | BPL | EPD
123 | 1CB | D05C1.5 | 10.5.06 | 1CB36AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 36 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 279 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | MV19-02, MV18-L2, MV35-L2, MA02-03, MR03-03, LR03-03, TY16-L4, TY17-L4, TY18-L3, TY19-L3, IP01-L5, IP02-L5, IR03-L3, IP14-R2, IP15-L3, IP16-L3, IP17-L3, IP18-L3, IP19-L3, IR38-L3, IP23-L4, IP24-L4, IP25-L4, IP26-L4, IP27-L7, IP28-L4, IP29-L4, IP30-L4, IP31-L4, IP32-L4, IP33-L7, IP34-L4, IP36-L4, CT10-02 |  | BPL | JHS
124 | 1CB | E04V0.5 | 10.7.02 | 1CB36AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 36 (O/G T/F FDR) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 110 | 16.09.2019 | DR0817_4798-4G-30 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
125 | 1CB | B03Q150 | 10.1.02 | 1CB36AP01 | 6.6kV UNIT SWBD # 1CB PANEL NO 36 (O/G T/F FDR) | CT SERV TRF # 1DCT02 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 269 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | MV34-L1, MV35-L1, MA02-01, MR03-01, LR03-01, TY16-R1, TY17-R1, TY18-R1, TY19-R1, IP01-R1, IP02-R1, IR03-R1, IP14-L1, IP15-R1, IP16-R1, IP17-R1, IP18-R1, IP19-R1, IR38-R1, IP23-R1, IP24-R1, IP25-R1, IP26-R1, IP27-R1, IP28-R1, IP29-R1, IP30-R1, IP31-R1, IP32-R1, IP33-R1, IP34-R1, IP36-R1, CT10-01, ZZ99- |  | BPL | JHS
126 | 1CB | D05C2.5 | 10.5.07 | 1CB37AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | GRP | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | CT CONNECTION FOR DIFFERENTIAL PROTECTION (87UT) | PVC-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
127 | 1CB | D02C1.5 | 10.5.01 | 1CB37AC02 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | UNIT PROTECTION TRIP (FOR TRIPPING CKT.) | PVC-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
128 | 1CB | D02C1.5 | 10.5.01 | 1CB37AC03 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | UNIT PROTECTION NOT OPTD. (FOR CLOSING CKT.) | PVC-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
129 | 1CB | D02C1.5 | 10.5.01 | 1CB37AC04 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | GT HVCB CLOSED | PVC-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
130 | 1CB | D05C1.5 | 10.5.06 | 1CB37AC05 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | BTS-2 1CB - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 81 | [5 empty] | CLOSE AND TRIP COMMAND TO CB | PVC-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
131 | 1CB | E04V0.5 | 10.7.02 | 1CB37AC06 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | DDCMIS # CRE63 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 89 | 111 | 16.09.2019 | DR0817_4798-4G-30 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV17-R2, MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
132 | 1CB | E04V0.5 | 10.7.02 | 1CB37AC07 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 89 | 111 | 16.09.2019 | DR0817_4798-4G-30 |  |  | LINE PT IN SERVICE | OVERALL SCREENED | MV17-R2, MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
133 | 1CB | D02L2.5 | 10.4.24 | 1CB37AC08 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | BTS-2 1CB - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 81 | [5 empty] | VT SUPPLY FOR BTS (R-Y) | XLPE-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
134 | 1CB | D05C1.5 | 10.5.06 | 1CB37AC09 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | BTS-2 1CB - 0CA | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 81 | [5 empty] | BREAKER OPEN & IN SERVICE, BREAKER CLOSE & IN SERVICE, 86 RE | PVC-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03, CC50-03 |  | BPL | BPL
135 | 1CB | D02C1.5 | 10.5.01 | 1CB37AC10 | 6.6kV UNIT SWBD # 1CB PANEL NO 37 (MAIN I/C) | GRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | 51N FOR REVERSE BLOCKING | PVC-CU UNARMOURED | MV17-L2, MV16-L2, MV02-R1, MV99-04, MR16-05, TR48-05, LV64-05, LV04-L4, LV05-L4, LV06-L4, LV07-L4, LV76-03, LR05-03, CC92-03, CC89-03, CC51-03 |  | BPL | BPL
136 | 1CB | E04V0.5 | 10.7.02 | 1CB37AC11 | BTS-2 1CB - 0CA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 86 | 50 | 19.09.2019 | DR0817_4798-4G-30 |  |  | BTS OUT OPERATED | OVERALL SCREENED | MV17-R2, MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03 |  | BPL | EDN
137 | 1CB | E04V0.5 | 10.7.02 | 1CB38AC01 | 6.6kV UNIT SWBD # 1CB PANEL NO 38 (LV PANEL) | DDCMIS # CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 89 | 112 | 16.09.2019 | DR0817_4798-4G-30 |  |  | DC SUPPLY - 1 & 2 FAILURE (HEALTHY IN SCHEME, INVERT AT DCS) | OVERALL SCREENED | MV17-R2, MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-04, CC45-03, CC46-03 |  | BPL | EDN
1 | 1CC | D05C1.5 | 10.5.06 | 1CC02AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 02 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 22 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CM08-L3, CM09-L3, CM13-02, CM22-04, CM23-03 |  | BPL | EPD
2 | 1CC | D02L2.5 | 10.4.24 | 1CC02AC02 | 6.6kV COMP. SWBD # 1CC PANEL NO 02 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 22 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CM08-L3, CM09-L3, CM13-02, CM22-04, CM23-03 |  | BPL | BPL
3 | 1CC | B03Q150 | 10.1.02 | 1CC02AP01 | 6.6kV COMP. SWBD # 1CC PANEL NO 02 (MOTOR FDR) | IA COMP-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 21 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | CM08-L1, CM09-L1, CM13-01, CM22-01, CM23-01, ZZ99- |  | BPL | BPL
4 | 1CC | D02C1.5 | 10.5.01 | 1CC03AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 03 (I/C-A) | 1CA PANEL NO. 08 | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | UPSTREAM BREAKER TRIP | PVC-CU UNARMOURED | CM08-L3, CM07-L3, CM06-L3, CM05-L3, CM04-L3, NR01-03, TY43-03, TY42-03, TY41-03, TY40-03, YR03-03, TY39-03, TY38-03, TY37-03, TY36-03, TY11-L4, TY12-L4, TY13-L4, LR01-03, MR01-03, MV01-03, MV16-L2, MV15-02, ZZ99- |  | BPL | BPL
5 | 1CC | E04V0.5 | 10.7.02 | 1CC03AC02 | 6.6kV COMP. SWBD # 1CC PANEL NO 03 (I/C-A) | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 206 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | CM08-R3, CM07-R3, CM06-R3, CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
6 | 1CC | E04V0.5 | 10.7.02 | 1CC03AC03 | 6.6kV COMP. SWBD # 1CC PANEL NO 03 (I/C-A) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 206 | [5 empty] | LINE PT IN SERVICE | OVERALL SCREENED | CM08-R3, CM07-R3, CM06-R3, CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
7 | 1CC | D05C1.5 | 10.5.06 | 1CC04AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 04 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CM08-L3, CM09-L3, CM13-02, CM22-04, CM24-04, CM25-03 |  | BPL | EPD
8 | 1CC | D02L2.5 | 10.4.24 | 1CC04AC02 | 6.6kV COMP. SWBD # 1CC PANEL NO 04 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CM08-L3, CM09-L3, CM13-02, CM22-04, CM24-04, CM25-03 |  | BPL | BPL
9 | 1CC | B03Q150 | 10.1.02 | 1CC04AP01 | 6.6kV COMP. SWBD # 1CC PANEL NO 04 (MOTOR FDR) | SA COMP-1A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 26 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | CM08-L1, CM09-L1, CM13-01, CM22-01, CM24-01, CM25-01, ZZ99- |  | BPL | BPL
10 | 1CC | E04V0.5 | 10.7.02 | 1CC06AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 06 (BUS PT-A) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 203 | [5 empty] | BUS PT IN SERVICE, N/V | OVERALL SCREENED | CM07-R3, CM06-R3, CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
11 | 1CC | E04V0.5 | 10.7.02 | 1CC07AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 07 (B/C) | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 203 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | CM07-R3, CM06-R3, CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
12 | 1CC | E04V0.5 | 10.7.02 | 1CC08AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 08 (BUS PT-B) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 201 | [5 empty] | BUS PT IN SERVICE, N/V | OVERALL SCREENED | CM06-R3, CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
13 | 1CC | D05C1.5 | 10.5.06 | 1CC10AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 10 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CM06-L3, CM07-L3, CM12-02, CM21-04, CM22-04, CM24-04, CM26-04, CM27-03 |  | BPL | EPD
14 | 1CC | D02L2.5 | 10.4.24 | 1CC10AC02 | 6.6kV COMP. SWBD # 1CC PANEL NO 10 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CM06-L3, CM07-L3, CM12-02, CM21-04, CM22-04, CM24-04, CM26-04, CM27-03 |  | BPL | BPL
15 | 1CC | B03Q150 | 10.1.02 | 1CC10AP01 | 6.6kV COMP. SWBD # 1CC PANEL NO 10 (MOTOR FDR) | IA COMP-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 35 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | CM06-L1, CM07-L1, CM12-01, CM21-01, CM22-01, CM24-01, CM26-01, CM27-01, ZZ99- |  | BPL | BPL
16 | 1CC | D05C1.5 | 10.5.06 | 1CC11AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 11 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 41 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CM06-L3, CM07-L3, CM12-02, CM21-04, CM22-04, CM24-04, CM26-04, CM28-04, CM29-03 |  | BPL | EPD
17 | 1CC | D02L2.5 | 10.4.24 | 1CC11AC02 | 6.6kV COMP. SWBD # 1CC PANEL NO 11 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 41 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CM06-L3, CM07-L3, CM12-02, CM21-04, CM22-04, CM24-04, CM26-04, CM28-04, CM29-03 |  | BPL | BPL
18 | 1CC | B03Q150 | 10.1.02 | 1CC11AP01 | 6.6kV COMP. SWBD # 1CC PANEL NO 11 (MOTOR FDR) | SA COMP-1B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 40 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | CM06-L1, CM07-L1, CM12-01, CM21-01, CM22-01, CM24-01, CM26-01, CM28-01, CM29-01, ZZ99- |  | BPL | BPL
19 | 1CC | D02C1.5 | 10.5.01 | 1CC12AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 12 (I/C-B) | 1CB PANEL NO. 32 | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 152 | [5 empty] | UPSTREAM BREAKER TRIP | PVC-CU UNARMOURED | CM05-L3, CM04-L3, NR01-03, TY43-03, TY42-03, TY41-03, TY40-03, YR03-03, TY39-03, TY38-03, TY37-03, TY36-03, TY11-L4, TY12-L4, TY13-L4, LR01-03, MR01-03, MV01-03, MV16-L2, MV17-L2, MV19-02 |  | BPL | BPL
20 | 1CC | E04V0.5 | 10.7.02 | 1CC12AC02 | 6.6kV COMP. SWBD # 1CC PANEL NO 12 (I/C-B) | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 197 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
21 | 1CC | E04V0.5 | 10.7.02 | 1CC12AC03 | 6.6kV COMP. SWBD # 1CC PANEL NO 12 (I/C-B) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 197 | [5 empty] | LINE PT IN SERVICE | OVERALL SCREENED | CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
22 | 1CC | E04V0.5 | 10.7.02 | 1CC13AC01 | 6.6kV COMP. SWBD # 1CC PANEL NO 13 (LV PANEL) | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 197 | [5 empty] | DC SUPPLY - 1 & 2 FAILURE (HEALTHY IN SCHEME, INVERT AT DCS) | OVERALL SCREENED | CM05-R3, CM04-R3, NR01-04, TY43-04, TY42-04, TY41-04, TY40-04, YR03-04, TY39-04, TY38-04, TY37-04, TY36-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | BPL | EDN
1 | 0CD | D03L2.5 | 10.4.26 | 0CD01AC01 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | RW TRANSFORMER-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 32 | [5 empty] | CT CONNECTION FOR REF PROTECTION (64R) | XLPE-CU UNARMOURED | RV06-L2, RV05-02, RR01-02, RV01-02, RV02-02, RV03-02, RV04-02 |  | BPL | PEM
2 | 0CD | D03L2.5 | 10.4.26 | 0CD01AC02 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | RW TRANSFORMER-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 32 | [5 empty] | CT CONNECTION FOR LV BACKUP E/F PROTECTION (51N) | XLPE-CU UNARMOURED | RV06-L2, RV05-02, RR01-02, RV01-02, RV02-02, RV03-02, RV04-02 |  | BPL | PEM
3 | 0CD | D02C1.5 | 10.5.01 | 0CD01AC03 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | EXTN. PANEL - 1 | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 200 | [5 empty] | UPSTREAM BREAKER TRIP | PVC-CU UNARMOURED | SITE ROUTING |  | BPL | PEM
4 | 0CD | E04V0.5 | 10.7.02 | 0CD01AC04 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 39 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | RV06-R2, RV07-R2, RV08-R2, RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
5 | 0CD | E04V0.5 | 10.7.02 | 0CD01AC05 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 39 | [5 empty] | LINE PT IN SERVICE | OVERALL SCREENED | RV06-R2, RV07-R2, RV08-R2, RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
6 | 0CD | B01Q400 | 10.1.01 | 0CD01AP01 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | INCOMER-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV06-L1, RV05-01, RR01-01, RV01-01, RV02-01, RV03-01, RV04-01, ZZ99- |  | BPL | BPL
7 | 0CD | B01Q400 | 10.1.01 | 0CD01AP02 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | INCOMER-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV06-L1, RV05-01, RR01-01, RV01-01, RV02-01, RV03-01, RV04-01, ZZ99- |  | BPL | BPL
8 | 0CD | B01Q400 | 10.1.01 | 0CD01AP03 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | INCOMER-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV06-L1, RV05-01, RR01-01, RV01-01, RV02-01, RV03-01, RV04-01, ZZ99- |  | BPL | BPL
9 | 0CD | B01Q400 | 10.1.01 | 0CD01AP04 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | INCOMER-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV06-L1, RV05-01, RR01-01, RV01-01, RV02-01, RV03-01, RV04-01, ZZ99- |  | BPL | BPL
10 | 0CD | B01Q400 | 10.1.01 | 0CD01AP05 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | INCOMER-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV06-L1, RV05-01, RR01-01, RV01-01, RV02-01, RV03-01, RV04-01, ZZ99- |  | BPL | BPL
11 | 0CD | B01Q400 | 10.1.01 | 0CD01AP06 | 6.6kV RW SWBD # 0CD PANEL NO 01 (I/C-A) | INCOMER-A | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 34 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV06-L1, RV05-01, RR01-01, RV01-01, RV02-01, RV03-01, RV04-01, ZZ99- |  | BPL | BPL
12 | 0CD | D05C1.5 | 10.5.06 | 0CD02AC01 | 6.6kV RW SWBD # 0CD PANEL NO 02 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | BPL | EPD
13 | 0CD | D02L2.5 | 10.4.24 | 0CD02AC02 | 6.6kV RW SWBD # 0CD PANEL NO 02 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | SITE ROUTING |  | BPL | BPL
14 | 0CD | B03Q150 | 10.1.02 | 0CD02AP01 | 6.6kV RW SWBD # 0CD PANEL NO 02 (MOTOR FDR) | RW INTAKE PUMP-A | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 105 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | SITE ROUTING |  | BPL | BPL
15 | 0CD | D03L2.5 | 10.4.26 | 0CD03AC01 | 6.6kV RW SWBD # 0CD PANEL NO 03 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 22 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | RV07-L2, RV08-L2, RV09-L2, RV15-L2, RV19-L2 |  | BPL | EPD
16 | 0CD | D02C1.5 | 10.5.01 | 0CD03AC02 | 6.6kV RW SWBD # 0CD PANEL NO 03 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 22 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | RV07-L2, RV08-L2, RV09-L2, RV15-L2, RV19-L2 |  | BPL | EPD
17 | 0CD | D05C1.5 | 10.5.06 | 0CD03AC03 | 6.6kV RW SWBD # 0CD PANEL NO 03 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | RV07-L2, RV08-L2, RV09-L2, RV15-L2, RV19-L2, RV20-L2 |  | BPL | PEM
18 | 0CD | E04V0.5 | 10.7.02 | 0CD03AC04 | 6.6kV RW SWBD # 0CD PANEL NO 03 (O/G T/F FDR) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 36 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | RV07-R2, RV08-R2, RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
19 | 0CD | B03Q150 | 10.1.02 | 0CD03AP01 | 6.6kV RW SWBD # 0CD PANEL NO 03 (O/G T/F FDR) | RW SERV TRF # 0DBT01 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 29 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV07-L1, RV08-L1, RV09-L1, RV15-L1, RV19-L1, RV20-L1, ZZ99- |  | BPL | PEM
20 | 0CD | E04V0.5 | 10.7.02 | 0CD06AC01 | 6.6kV RW SWBD # 0CD PANEL NO 06 (BUS PT-A) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 33 | [5 empty] | BUS PT IN SERVICE, N/V | OVERALL SCREENED | RV08-R2, RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
21 | 0CD | E04V0.5 | 10.7.02 | 0CD07AC01 | 6.6kV RW SWBD # 0CD PANEL NO 07 (DP PANEL) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 33 | [5 empty] | DC SUPPLY - 1 & 2 FAILURE (HEALTHY IN SCHEME, INVERT AT DCS | OVERALL SCREENED | RV08-R2, RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
22 | 0CD | E04V0.5 | 10.7.02 | 0CD08AC01 | 6.6kV RW SWBD # 0CD PANEL NO 08 (B/C) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 33 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | RV08-R2, RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
23 | 0CD | E04V0.5 | 10.7.02 | 0CD09AC01 | 6.6kV RW SWBD # 0CD PANEL NO 09 (BUS PT-B) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 33 | [5 empty] | BUS PT IN SERVICE, N/V | OVERALL SCREENED | RV08-R2, RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
24 | 0CD | D05C1.5 | 10.5.06 | 0CD10AC01 | 6.6kV RW SWBD # 0CD PANEL NO 10 (MOTOR FDR) | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | BPL | EPD
25 | 0CD | D02L2.5 | 10.4.24 | 0CD10AC02 | 6.6kV RW SWBD # 0CD PANEL NO 10 (MOTOR FDR) | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | SITE ROUTING |  | BPL | BPL
26 | 0CD | B03Q150 | 10.1.02 | 0CD10AP01 | 6.6kV RW SWBD # 0CD PANEL NO 10 (MOTOR FDR) | RW INTAKE PUMP-B | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 115 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | SITE ROUTING |  | BPL | BPL
27 | 0CD | D03L2.5 | 10.4.26 | 0CD11AC01 | 6.6kV RW SWBD # 0CD PANEL NO 11 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 16 | [5 empty] | CT INPUT FOR 64R PROT. | XLPE-CU UNARMOURED | RV09-L2, RV15-L2, RV16-L2 |  | BPL | EPD
28 | 0CD | D02C1.5 | 10.5.01 | 0CD11AC02 | 6.6kV RW SWBD # 0CD PANEL NO 11 (O/G T/F FDR) | DOWNSTREAM LV SWGR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 16 | [5 empty] | 51N OPERATED FROM LT SWGR RELAY | PVC-CU UNARMOURED | RV09-L2, RV15-L2, RV16-L2 |  | BPL | EPD
29 | 0CD | D05C1.5 | 10.5.06 | 0CD11AC03 | 6.6kV RW SWBD # 0CD PANEL NO 11 (O/G T/F FDR) | TRF MB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 19 | [5 empty] | WTI ALARM, WTI TRIP OPTD. (49T)/ TRF DOOR OPEN | PVC-CU UNARMOURED | RV09-L2, RV15-L2, RV16-L2, RV17-L2, ZZ99- |  | BPL | PEM
30 | 0CD | E04V0.5 | 10.7.02 | 0CD11AC04 | 6.6kV RW SWBD # 0CD PANEL NO 11 (O/G T/F FDR) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 30 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | RV09-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
31 | 0CD | B03Q150 | 10.1.02 | 0CD11AP01 | 6.6kV RW SWBD # 0CD PANEL NO 11 (O/G T/F FDR) | RW SERV TRF # 0DBT02 | 03C X 150 XLPE-Al FRLS ( 6.6 kV ) | 24 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV09-L1, RV15-L1, RV16-L1, RV17-L1, ZZ99- |  | BPL | PEM
32 | 0CD | D03L2.5 | 10.4.26 | 0CD14AC01 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | RW TRANSFORMER-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | CT CONNECTION FOR REF PROTECTION (64R) | XLPE-CU UNARMOURED | RV10-L2, RV15-L2, RV16-L2, RV17-L2, RV18-L2, RV24-02, RV33-02, RR02-02, RV34-02, RV36-02, RV37-02, RV38-02 |  | BPL | PEM
33 | 0CD | D03L2.5 | 10.4.26 | 0CD14AC02 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | RW TRANSFORMER-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | CT CONNECTION FOR LV BACKUP E/F PROTECTION (51N) | XLPE-CU UNARMOURED | RV10-L2, RV15-L2, RV16-L2, RV17-L2, RV18-L2, RV24-02, RV33-02, RR02-02, RV34-02, RV36-02, RV37-02, RV38-02 |  | BPL | PEM
34 | 0CD | D02C1.5 | 10.5.01 | 0CD14AC03 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | EXTN. PANEL - 2 | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 200 | [5 empty] | UPSTREAM BREAKER TRIP | PVC-CU UNARMOURED | SITE ROUTING |  | BPL | BPL
35 | 0CD | E04V0.5 | 10.7.02 | 0CD14AC04 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 31 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | RV10-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
36 | 0CD | E04V0.5 | 10.7.02 | 0CD14AC05 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 31 | [5 empty] | LINE PT IN SERVICE | OVERALL SCREENED | RV10-R2, RV15-R2, RV45-R2, RV28-02, RV29-02, RV30-02, RV31-02, RV32-02 |  | BPL | EDN
37 | 0CD | B01Q400 | 10.1.01 | 0CD14AP01 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | INCOMER-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 44 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV10-L1, RV15-R1, RV16-R1, RV17-R1, RV18-R1, RV24-01, RV33-01, RR02-01, RV34-01, RV36-01, RV37-01, RV38-01, ZZ99- |  | BPL | BPL
38 | 0CD | B01Q400 | 10.1.01 | 0CD14AP02 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | INCOMER-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 44 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV10-L1, RV15-R1, RV16-R1, RV17-R1, RV18-R1, RV24-01, RV33-01, RR02-01, RV34-01, RV36-01, RV37-01, RV38-01, ZZ99- |  | BPL | BPL
39 | 0CD | B01Q400 | 10.1.01 | 0CD14AP03 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | INCOMER-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 44 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV10-L1, RV15-R1, RV16-R1, RV17-R1, RV18-R1, RV24-01, RV33-01, RR02-01, RV34-01, RV36-01, RV37-01, RV38-01, ZZ99- |  | BPL | BPL
40 | 0CD | B01Q400 | 10.1.01 | 0CD14AP04 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | INCOMER-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 44 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV10-L1, RV15-R1, RV16-R1, RV17-R1, RV18-R1, RV24-01, RV33-01, RR02-01, RV34-01, RV36-01, RV37-01, RV38-01, ZZ99- |  | BPL | BPL
41 | 0CD | B01Q400 | 10.1.01 | 0CD14AP05 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | INCOMER-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 44 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV10-L1, RV15-R1, RV16-R1, RV17-R1, RV18-R1, RV24-01, RV33-01, RR02-01, RV34-01, RV36-01, RV37-01, RV38-01, ZZ99- |  | BPL | BPL
42 | 0CD | B01Q400 | 10.1.01 | 0CD14AP06 | 6.6kV RW SWBD # 0CD PANEL NO 14 (I/C-A) | INCOMER-B | 01C X 400 XLPE-Al FRLS ( 6.6 kV ) | 44 | [5 empty] | POWER CABLE | XLPE-AL UNARMOURED | RV10-L1, RV15-R1, RV16-R1, RV17-R1, RV18-R1, RV24-01, RV33-01, RR02-01, RV34-01, RV36-01, RV37-01, RV38-01, ZZ99- |  | BPL | BPL
43 | 0CD | A03Q120 | 10.2.01 | 0CDTR01P01 | 33kV RSP SWBD # EXTN PANEL-01 | RAW WATER TRF-01 | 03C X 120 XLPE-Al FRLS ( 33 kV ) | 700 | [9 empty] | BPL | PEM
44 | 0CD | A03Q120 | 10.2.01 | 0CDTR01P02 | 33kV RSP SWBD # EXTN PANEL-02 | RAW WATER TRF-02 | 03C X 120 XLPE-Al FRLS ( 33 kV ) | 700 | [9 empty] | BPL | PEM
1 | 1DA | D01Q400 | 10.4.04 | 1DA01BP01 | 415V SWGR O/G MODULE # 1DA01FB | UNIT SERVICE ACDB # 1QA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 62 | 01.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV63-04, MV64-04, MV42-02, MV41-01, MV40-01, MV39-01, MV88-01, MV87-01, MV57-L1, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-02, LV56-02, LV20-R1, ZZ99- |  | EPD | EPD
2 | 1DA | D01Q400 | 10.4.04 | 1DA01BP02 | 415V SWGR O/G MODULE # 1DA01FB | UNIT SERVICE ACDB # 1QA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 62 | 01.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV63-04, MV64-04, MV42-02, MV41-01, MV40-01, MV39-01, MV88-01, MV87-01, MV57-L1, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-02, LV56-02, LV20-R1, ZZ99- |  | EPD | EPD
3 | 1DA | D01Q400 | 10.4.04 | 1DA01BP03 | 415V SWGR O/G MODULE # 1DA01FB | UNIT SERVICE ACDB # 1QA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 62 | 01.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV63-04, MV64-04, MV42-02, MV41-01, MV40-01, MV39-01, MV88-01, MV87-01, MV57-L1, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-02, LV56-02, LV20-R1, ZZ99- |  | EPD | EPD
4 | 1DA | D01Q400 | 10.4.04 | 1DA01BP04 | 415V SWGR O/G MODULE # 1DA01FB | UNIT SERVICE ACDB # 1QA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 61 | 01.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV63-04, MV64-04, MV42-02, MV41-01, MV40-01, MV39-01, MV88-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV36-L1, LV35-L1, LV55-01, LV56-01, LV20-R1, ZZ99- |  | EPD | EPD
5 | 1DA | D03Q240 | 10.4.17 | 1DA01DP01 | 415V SWGR O/G MODULE # 1DA01FD | TURBINE VALVE ACDB # 1KB | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | MV63-04, MV64-04, MV65-04, MV66-01, MV24-01, MV23-01, MV22-01, MV21-01, MV20-01, MV97-02, MV98-02, MV99-02, MR16-02, TR48-02, LV64-02, LV03-L1 |  | EPD | EPD
6 | 1DA | D04Q010 | 10.4.22 | 1DA01EP01 | 415V SWGR O/G MODULE # 1DA01FE | VFD PANEL FOR CEP-1B | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 68 | [5 empty] | POWER SUPPLY (10kVA) | XLPE-AL UNARMOURED | MV47-01, MV46-L2, MV45-L2, MA07-01, MR08-01, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, DR04-02, AC02-02, AC03-02, ZZ99- |  | EPD | EDN
7 | 1DA | D04Q010 | 10.4.22 | 1DA01FP01 | 415V SWGR O/G MODULE # 1DA01FF | VFD PANEL FOR CEP-1A | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 77 | [5 empty] | POWER SUPPLY (10kVA) | XLPE-AL UNARMOURED | MV47-01, MV46-L2, MV45-L2, MA07-01, MR08-01, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, DR06-02, AC10-02, AC11-02, AC12-02, ZZ99- |  | EPD | EDN
8 | 1DA | E04V0.5 | 10.7.02 | 1DA02AC01 | 415V SWGR O/G MODULE # 1DA02FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 62 | 73 | 16.09.2019 | DR0817_4798-4G-30 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
9 | 1DA | D01Q400 | 10.4.04 | 1DA02AP01 | 415V SWGR O/G MODULE # 1DA02FA | TURBINE MCC # 1KA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 66 | 64 | 06.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
10 | 1DA | D01Q400 | 10.4.04 | 1DA02AP02 | 415V SWGR O/G MODULE # 1DA02FA | TURBINE MCC # 1KA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 66 | 63 | 06.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
11 | 1DA | D01Q400 | 10.4.04 | 1DA02AP03 | 415V SWGR O/G MODULE # 1DA02FA | TURBINE MCC # 1KA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 66 | 63 | 06.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
12 | 1DA | D01Q400 | 10.4.04 | 1DA02AP04 | 415V SWGR O/G MODULE # 1DA02FA | TURBINE MCC # 1KA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 68 | 63 | 06.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
13 | 1DA | D01Q400 | 10.4.04 | 1DA02AP05 | 415V SWGR O/G MODULE # 1DA02FA | TURBINE MCC # 1KA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 68 | 63 | 06.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
14 | 1DA | D01Q400 | 10.4.04 | 1DA02AP06 | 415V SWGR O/G MODULE # 1DA02FA | TURBINE MCC # 1KA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 68 | 63 | 06.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
15 | 1DA | D01Q400 | 10.4.04 | 1DA02AP07 | 415V SWGR O/G MODULE # 1DA02FA | TURBINE MCC # 1KA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 74 | 63 | 06.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
16 | 1DA | D05C1.5 | 10.5.06 | 1DA02BC01 | 415V SWGR MOTOR MODULE # 1DA02FB | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV47-02, MV64-05, MV65-05, MV66-05, MV67-05, MV68-05, MA05-03, MR10-03, LV76-03, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, TG39-02 |  | EPD | EPD
17 | 1DA | D02L2.5 | 10.4.24 | 1DA02BC02 | 415V SWGR MOTOR MODULE # 1DA02FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV47-02, MV64-05, MV65-05, MV66-05, MV67-05, MV68-05, MA05-03, MR10-03, LV76-03, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, TG39-02 |  | EPD | PEM
18 | 1DA | D03Q240 | 10.4.17 | 1DA02BP01 | 415V SWGR MOTOR MODULE # 1DA02FB | VACUUM PUMP 1 (MAJ60AN001) | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (110kW) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV65-03, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LV76-01, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG36-01, TG37-01, TG38-01, TR07-01, TG39-01, ZZ99- |  | EPD | PEM
19 | 1DA | E04V0.5 | 10.7.02 | 1DA03AC01 | 415V SWGR O/G MODULE # 1DA03FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 62 | 73 | 16.09.2019 | DR0817_4798-4G-104 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
20 | 1DA | D01Q400 | 10.4.04 | 1DA03AP01 | 415V SWGR O/G MODULE # 1DA03FA | BOILER MCC # 1HA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 66 | 02.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-01, LV56-01, LV57-01, LV13-R1, ZZ99- |  | EPD | EPD
21 | 1DA | D01Q400 | 10.4.04 | 1DA03AP02 | 415V SWGR O/G MODULE # 1DA03FA | BOILER MCC # 1HA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 66 | 02.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-01, LV56-01, LV57-01, LV13-R1, ZZ99- |  | EPD | EPD
22 | 1DA | D01Q400 | 10.4.04 | 1DA03AP03 | 415V SWGR O/G MODULE # 1DA03FA | BOILER MCC # 1HA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 66 | 02.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-01, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-01, LV56-01, LV57-01, LV13-R1, ZZ99- |  | EPD | EPD
23 | 1DA | D01Q400 | 10.4.04 | 1DA03AP04 | 415V SWGR O/G MODULE # 1DA03FA | BOILER MCC # 1HA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 66 | 02.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-02, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-01, LV56-01, LV57-01, LV13-R1, ZZ99- |  | EPD | EPD
24 | 1DA | D01Q400 | 10.4.04 | 1DA03AP05 | 415V SWGR O/G MODULE # 1DA03FA | BOILER MCC # 1HA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 66 | 02.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-02, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-01, LV56-01, LV57-01, LV13-R1, ZZ99- |  | EPD | EPD
25 | 1DA | D01Q400 | 10.4.04 | 1DA03AP06 | 415V SWGR O/G MODULE # 1DA03FA | BOILER MCC # 1HA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 66 | 02.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-04, MV42-02, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-01, LV56-01, LV57-01, LV13-R1, ZZ99- |  | EPD | EPD
26 | 1DA | D01Q400 | 10.4.04 | 1DA03AP07 | 415V SWGR O/G MODULE # 1DA03FA | BOILER MCC # 1HA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 69 | 66 | 02.08.2019 | DR1050_0008 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV42-02, MV41-01, MV40-01, MV78-03, MV77-03, MV76-02, MR05-R1, LR11-R1, LV72-01, LV36-L1, LV35-L1, LV55-01, LV56-01, LV57-01, LV13-R1, ZZ99- |  | EPD | EPD
27 | 1DA | D05C1.5 | 10.5.06 | 1DA03BC01 | 415V SWGR MOTOR MODULE # 1DA03FB | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 67 | 65 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV47-02, MV46-L2, MV45-L2, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MV05-L2, MV04-L2, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03, TG16-L3 |  | EPD | EPD
28 | 1DA | D02L2.5 | 10.4.24 | 1DA03BC02 | 415V SWGR MOTOR MODULE # 1DA03FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 67 | 72 | 07.12.19 | DR3111-11601 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV47-02, MV46-L2, MV45-L2, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MV05-L2, MV04-L2, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03, TG16-L3 |  | EPD | PEM
29 | 1DA | D03Q240 | 10.4.17 | 1DA03BP01 | 415V SWGR MOTOR MODULE # 1DA03FB | DMCW BOOSTER PUMP 1 | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 70 | 58 | 22.02.2020 | DR2685-3 |  |  | POWER SUPPLY (110kW) | XLPE-AL UNARMOURED | MV47-01, MV46-L2, MV45-L2, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MV05-L2, MV04-L2, MV03-L2, MV99-02, MR17-03, TG82-03, TG81-02, TG84-02, TG86-02, TG16-L1 |  | EPD | PEM
30 | 1DA | E04V0.5 | 10.7.02 | 1DA04AC01 | 415V SWGR O/G MODULE # 1DA04FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 62 | 74 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
31 | 1DA | D01Q400 | 10.4.04 | 1DA04AP01 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 35 | 45 | 28.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV47-01, MV61-L2, MA08-02, MR07-02, LV73-01, LV39-R1, LV38-R1, ZZ99- |  | EPD | EPD
32 | 1DA | D01Q400 | 10.4.04 | 1DA04AP02 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 35 | 45 | 28.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV47-01, MV61-L2, MA08-02, MR07-02, LV73-01, LV39-R1, LV38-R1, ZZ99- |  | EPD | EPD
33 | 1DA | D01Q400 | 10.4.04 | 1DA04AP03 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 35 | 45 | 28.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV47-01, MV61-L2, MA08-02, MR07-02, LV73-01, LV39-R1, LV38-R1, ZZ99- |  | EPD | EPD
34 | 1DA | D01Q400 | 10.4.04 | 1DA04AP04 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 45 | 28.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV62-04, MR06-04, IM01-02, IR17-02, LV40-02, LV38-L1, ZZ99- |  | EPD | EPD
35 | 1DA | D01Q400 | 10.4.04 | 1DA04AP05 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 45 | 28.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV62-04, MR06-04, IM01-02, IR17-02, LV40-02, LV38-L1, ZZ99- |  | EPD | EPD
36 | 1DA | D01Q400 | 10.4.04 | 1DA04AP06 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 45 | 28.08.2019 | DR1050_0007 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV62-04, MR06-04, IM01-02, IR17-02, LV40-02, LV38-L1, ZZ99- |  | EPD | EPD
37 | 1DA | D01Q400 | 10.4.04 | 1DA04AP07 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 45 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV62-04, MR06-04, IM01-02, IR17-02, LV40-02, LV38-L1, ZZ99- |  | EPD | EPD
38 | 1DA | D01Q400 | 10.4.04 | 1DA04AP08 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 45 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV62-04, MR06-04, IM01-02, IR17-02, LV40-02, LV38-L1, ZZ99- |  | EPD | EPD
39 | 1DA | D01Q400 | 10.4.04 | 1DA04AP09 | 415V SWGR O/G MODULE # 1DA04FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 45 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV63-04, MV62-04, MR06-04, IM01-02, IR17-02, LV40-02, LV38-L1, ZZ99- |  | EPD | EPD
40 | 1DA | D05C1.5 | 10.5.06 | 1DA04BC01 | 415V SWGR MOTOR MODULE # 1DA04FB | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 172 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV63-05, MV64-05, MV65-05, MV66-05, MV67-05, MV68-05, MA05-03, MR10-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, ZZ99- |  | EPD | EPD
41 | 1DA | D02L2.5 | 10.4.24 | 1DA04BC02 | 415V SWGR MOTOR MODULE # 1DA04FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 172 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV63-05, MV64-05, MV65-05, MV66-05, MV67-05, MV68-05, MA05-03, MR10-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, ZZ99- |  | EPD | PEM
42 | 1DA | D03Q240 | 10.4.17 | 1DA04BP01 | 415V SWGR MOTOR MODULE # 1DA04FB | MOTOR FOR HIGH PRESSURE PUMP | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (110kW) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV65-03, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LV79-01, LR10-R1, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IR07-01, IC50-01, IC51-01, IC52-01, BR16-01, ZZ99- |  | EPD | PEM
43 | 1DA | E04V0.5 | 10.7.02 | 1DA06BC01 | 415V SWGR I/C MODULE # 1DA06FB | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 76 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
44 | 1DA | D02L2.5 | 10.4.24 | 1DA06BC02 | 415V SWGR I/C MODULE # 1DA06FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | MV48-02, MV64-05, MV65-05, MV66-05, MV25-02, MV27-L2, MV44-L2, MV45-L2 |  | EPD | JHS
45 | 1DA | D02L2.5 | 10.4.24 | 1DA06BC03 | 415V SWGR I/C MODULE # 1DA06FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | MV48-02, MV64-05, MV65-05, MV66-05, MV25-02, MV27-L2, MV44-L2, MV45-L2 |  | EPD | JHS
46 | 1DA | D02C1.5 | 10.5.01 | 1DA06BC04 | 415V SWGR I/C MODULE # 1DA06FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 37 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | MV48-02, MV64-05, MV65-05, MV66-05, MV67-05, MV10-02, MV11-02 |  | EPD | BPL
47 | 1DA | E04V0.5 | 10.7.02 | 1DA06BC05 | 415V SWGR I/C MODULE # 1DA06FB | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 77 | 19.09.2019 | DR0817_4798-4G-16 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
48 | 1DA | E04V0.5 | 10.7.02 | 1DA08BC01 | 415V SWGR B/C MODULE # 1DA08FB | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 78 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
49 | 1DA | E04V0.5 | 10.7.02 | 1DA08BC02 | 415V SWGR B/C MODULE # 1DA08FB | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 79 | 19.09.2019 | DR0817_4798-4G-16 |  |  | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
50 | 1DA | E04V0.5 | 10.7.02 | 1DA10BC01 | 415V SWGR I/C MODULE # 1DA10FB | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 81 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
51 | 1DA | D02L2.5 | 10.4.24 | 1DA10BC02 | 415V SWGR I/C MODULE # 1DA10FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | MV48-02, MV64-05, MV42-02, MV71-03 |  | EPD | JHS
52 | 1DA | D02L2.5 | 10.4.24 | 1DA10BC03 | 415V SWGR I/C MODULE # 1DA10FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | MV48-02, MV64-05, MV42-02, MV71-03 |  | EPD | JHS
53 | 1DA | D02C1.5 | 10.5.01 | 1DA10BC04 | 415V SWGR I/C MODULE # 1DA10FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 34 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | MV48-02, MV64-05, MV65-05, MV66-05, MV24-02, MV23-02 |  | EPD | BPL
54 | 1DA | E04V0.5 | 10.7.02 | 1DA10BC05 | 415V SWGR I/C MODULE # 1DA10FB | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 81 | 19.09.2019 | DR0817_4798-4G-16 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
55 | 1DA | E04V0.5 | 10.7.02 | 1DA11AC01 | 415V SWGR O/G MODULE # 1DA11FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 82 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
56 | 1DA | D01Q400 | 10.4.04 | 1DA11AP01 | 415V SWGR O/G MODULE # 1DA11FA | BOILER MCC # 1HA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 78 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV69-03, MV70-03, MV71-02, MV30-L2, MV31-L2, MV32-L2, MV33-L2, MV34-L2, MA01-02, MR02-02, LV71-02, LV17-L1, LV15-L1 |  | EPD | EPD
57 | 1DA | D01Q400 | 10.4.04 | 1DA11AP02 | 415V SWGR O/G MODULE # 1DA11FA | BOILER MCC # 1HA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 78 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV69-03, MV70-03, MV71-02, MV30-L2, MV31-L2, MV32-L2, MV33-L2, MV34-L2, MA01-02, MR02-02, LV71-02, LV17-L1, LV15-L1 |  | EPD | EPD
58 | 1DA | D01Q400 | 10.4.04 | 1DA11AP03 | 415V SWGR O/G MODULE # 1DA11FA | BOILER MCC # 1HA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 78 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV69-03, MV70-03, MV71-02, MV30-L2, MV31-L2, MV32-L2, MV33-L2, MV34-L2, MA01-02, MR02-02, LV71-02, LV17-L1, LV15-L1 |  | EPD | EPD
59 | 1DA | D01Q400 | 10.4.04 | 1DA11AP04 | 415V SWGR O/G MODULE # 1DA11FA | BOILER MCC # 1HA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 78 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV69-03, MV70-03, MV71-02, MV30-L2, MV31-L2, MV32-L2, MV33-L2, MV34-L2, MA01-02, MR02-02, LV71-02, LV17-L1, LV15-L1 |  | EPD | EPD
60 | 1DA | D01Q400 | 10.4.04 | 1DA11AP05 | 415V SWGR O/G MODULE # 1DA11FA | BOILER MCC # 1HA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 78 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV69-03, MV70-03, MV71-02, MV30-L2, MV31-L2, MV32-L2, MV33-L2, MV34-L2, MA01-02, MR02-02, LV71-02, LV17-L1, LV15-L1 |  | EPD | EPD
61 | 1DA | D01Q400 | 10.4.04 | 1DA11AP06 | 415V SWGR O/G MODULE # 1DA11FA | BOILER MCC # 1HA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 62 | 78 | 31.08.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV69-03, MV70-03, MV71-02, MV30-L2, MV31-L2, MV32-L2, MV33-L2, MV34-L2, MA01-02, MR02-02, LV71-02, LV17-L1, LV15-L1 |  | EPD | EPD
62 | 1DA | D01Q400 | 10.4.04 | 1DA11AP07 | 415V SWGR O/G MODULE # 1DA11FA | BOILER MCC # 1HA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 61 | 78 | 31.08.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV69-02, MV70-02, MV71-02, MV30-L2, MV31-L2, MV32-L2, MV33-L2, MV34-L2, MA01-02, MR02-02, LV71-02, LV17-L1, LV15-L1 |  | EPD | EPD
63 | 1DA | D05C1.5 | 10.5.06 | 1DA11BC01 | 415V SWGR MOTOR MODULE # 1DA11FB | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 155 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV48-02, MV64-05, MV65-05, MV66-05, MV67-05, MV68-05, MA05-03, MR10-03, LV76-03, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, TG39-02, TG40-02 |  | EPD | EPD
64 | 1DA | D02L2.5 | 10.4.24 | 1DA11BC02 | 415V SWGR MOTOR MODULE # 1DA11FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 155 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | MV48-02, MV64-05, MV65-05, MV66-05, MV67-05, MV68-05, MA05-03, MR10-03, LV76-03, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, TG39-02, TG40-02 |  | EPD | PEM
65 | 1DA | D03Q240 | 10.4.17 | 1DA11BP01 | 415V SWGR MOTOR MODULE # 1DA11FB | VACUUM PUMP 2 (MAJ70AN001) | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 152 | [5 empty] | POWER SUPPLY (110kW) | XLPE-AL UNARMOURED | MV63-03, MV64-03, MV65-04, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LV76-01, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG36-01, TG37-01, TG38-01, TR07-01, TG39-01, TG40-01 |  | EPD | PEM
66 | 1DA | E04V0.5 | 10.7.02 | 1DA12AC01 | 415V SWGR O/G MODULE # 1DA12FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 72 | 80 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV49-03, MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
67 | 1DA | D01Q400 | 10.4.04 | 1DA12AP01 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 39 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-04, MV63-04, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
68 | 1DA | D01Q400 | 10.4.04 | 1DA12AP02 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 39 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-04, MV63-04, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
69 | 1DA | D01Q400 | 10.4.04 | 1DA12AP03 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 39 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-04, MV63-04, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
70 | 1DA | D01Q400 | 10.4.04 | 1DA12AP04 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-05, MV63-05, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
71 | 1DA | D01Q400 | 10.4.04 | 1DA12AP05 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-05, MV63-05, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
72 | 1DA | D01Q400 | 10.4.04 | 1DA12AP06 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-05, MV63-05, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
73 | 1DA | D01Q400 | 10.4.04 | 1DA12AP07 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-05, MV63-05, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
74 | 1DA | D01Q400 | 10.4.04 | 1DA12AP08 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-05, MV63-05, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
75 | 1DA | D01Q400 | 10.4.04 | 1DA12AP09 | 415V SWGR O/G MODULE # 1DA12FA | TIE TO UNIT EMERGENCY BOARD # 1DG SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 40 | 44 | 29.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | MV69-02, MV70-03, MV42-02, MV64-05, MV63-05, MV60-L2, MA08-02, MR07-02, LV73-01, LV39-L1, LV38-L1, ZZ99- |  | EPD | EPD
76 | 1DA | D05C1.5 | 10.5.06 | 1DA12BC01 | 415V SWGR MOTOR MODULE # 1DA12FB | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 72 | 67 | 06.02.20 | DR1150_17PA011778 |  |  | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | MV69-03, MV49-02, MV50-02, MV88-03, MV89-03, MV90-03, MV91-03, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03, TG16-L3, TG19-02 |  | EPD | EPD
77 | 1DA | D02L2.5 | 10.4.24 | 1DA12BC02 | 415V SWGR MOTOR MODULE # 1DA12FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 72 | 79 | 07.12.19 | DR3111-11601 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | MV69-03, MV49-02, MV50-02, MV88-03, MV89-03, MV90-03, MV91-03, MV92-03, MV03-L2, MV99-04, MR17-05, TG82-03, TG81-03, TG84-03, TG86-03, TG16-L3, TG19-02 |  | EPD | PEM
78 | 1DA | D03Q240 | 10.4.17 | 1DA12BP01 | 415V SWGR MOTOR MODULE # 1DA12FB | DMCW BOOSTER PUMP 2 | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 73 | 70 | 22.02.2020 | DR2685-3 |  |  | POWER SUPPLY (110kW) | XLPE-AL UNARMOURED | MV69-02, MV49-02, MV50-01, MV88-01, MV89-02, MV90-03, MV91-03, MV92-03, MV03-L2, MV99-02, MR17-03, TG82-03, TG81-02, TG84-02, TG86-02, TG16-L1, TG19-01 |  | EPD | PEM
79 | 1DA | E04V0.5 | 10.7.02 | 1DA14BC01 | 415V SWGR O/G MODULE # 1DA14FB | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 72 | 81 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV49-03, MV48-03, MV47-03, MV46-R2, MV45-R2, MV44-R2, MV27-R2, MV26-R2, MV08-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
80 | 1DA | D01Q400 | 10.4.04 | 1DA14BP01 | 415V SWGR O/G MODULE # 1DA14FB | TURBINE MCC # 1KA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 50 | 67 | 30.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV50-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
81 | 1DA | D01Q400 | 10.4.04 | 1DA14BP02 | 415V SWGR O/G MODULE # 1DA14FB | TURBINE MCC # 1KA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 50 | 67 | 30.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV50-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
82 | 1DA | D01Q400 | 10.4.04 | 1DA14BP03 | 415V SWGR O/G MODULE # 1DA14FB | TURBINE MCC # 1KA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 50 | 67 | 30.08.2019 | DR1006_0004 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV50-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
83 | 1DA | D01Q400 | 10.4.04 | 1DA14BP04 | 415V SWGR O/G MODULE # 1DA14FB | TURBINE MCC # 1KA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 50 | 67 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV50-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
84 | 1DA | D01Q400 | 10.4.04 | 1DA14BP05 | 415V SWGR O/G MODULE # 1DA14FB | TURBINE MCC # 1KA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 50 | 67 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV50-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
85 | 1DA | D01Q400 | 10.4.04 | 1DA14BP06 | 415V SWGR O/G MODULE # 1DA14FB | TURBINE MCC # 1KA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 50 | 67 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV50-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
86 | 1DA | D01Q400 | 10.4.04 | 1DA14BP07 | 415V SWGR O/G MODULE # 1DA14FB | TURBINE MCC # 1KA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 48 | 67 | 31.08.2019 | DR1006_0003 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV50-01, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV37-L1, LV46-01, LV47-01, LV48-01, LV49-01, LV06-L1, ZZ99- |  | EPD | EPD
87 | 1DA | D01Q400 | 10.4.04 | 1DA15AP01 | 415V SWGR O/G MODULE # 1DA15FA | UNIT SERVICE ACDB # 1QA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 45 | 82 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV49-02, MV50-02, MV87-01, MV57-R1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV36-L1, LV35-L1, LV55-02, LV56-02, LV20-R1, LV19-R1, LV18-R1, ZZ99- |  | EPD | EPD
88 | 1DA | D01Q400 | 10.4.04 | 1DA15AP02 | 415V SWGR O/G MODULE # 1DA15FA | UNIT SERVICE ACDB # 1QA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 45 | 82 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV49-02, MV50-02, MV87-01, MV57-R1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV36-L1, LV35-L1, LV55-02, LV56-02, LV20-R1, LV19-R1, LV18-R1, ZZ99- |  | EPD | EPD
89 | 1DA | D01Q400 | 10.4.04 | 1DA15AP03 | 415V SWGR O/G MODULE # 1DA15FA | UNIT SERVICE ACDB # 1QA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 45 | 82 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV49-02, MV50-02, MV87-01, MV57-R1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV36-L1, LV35-L1, LV55-02, LV56-02, LV20-R1, LV19-R1, LV18-R1, ZZ99- |  | EPD | EPD
90 | 1DA | D01Q400 | 10.4.04 | 1DA15AP04 | 415V SWGR O/G MODULE # 1DA15FA | UNIT SERVICE ACDB # 1QA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 44 | 82 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV49-01, MV50-02, MV87-01, MV57-L1, MV76-03, MR05-L2, LR11-L2, LV72-02, LV36-L1, LV35-L1, LV55-01, LV56-01, LV20-R1, LV19-R1, LV18-R1, ZZ99- |  | EPD | EPD
91 | 1DA | D3HQ095 | 10.4.20 | 1DA15CP01 | 415V SWGR O/G MODULE # 1DA15FC | OIL PURIFIER (MAV91AT001) | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 65 | 126 | 21.1.20 | DR0968_0001 |  |  | POWER SUPPLY (105kW) | XLPE-AL UNARMOURED | MV58-R1, MV57-R1, MV56-R1, MV93-01, MV94-01, MV95-01, MV96-02, MV97-02, MV98-02, MV99-02, MR16-02, TG71-01, TG72-01, TR16-01, TG73-01 |  | EPD | PEM
92 | 1DA | D04Q010 | 10.4.22 | 1DA15EP01 | 415V SWGR O/G MODULE # 1DA15FE | VFD PANEL FOR CEP-1A | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 78 | [5 empty] | POWER SUPPLY (10kVA) | XLPE-AL UNARMOURED | MV49-01, MV70-03, MV42-01, MV43-02, MV45-L2, MA07-01, MR08-01, DC07-03, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, DR04-02, AC02-02, AC03-02, ZZ99- |  | EPD | EDN
93 | 1DA | D03Q240 | 10.4.17 | 1DA15PP01 | 415V SWGR O/G MODULE # 1DA15RB | BOILER VALVE ACDB # 1HB | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | MV49-02, MV50-01, MV87-01, MV57-L1, MV76-02, MR05-R1, LR11-R1, LV72-01, LV37-L1, LV46-01, LV28-R1, ZZ99- |  | EPD | EPD
94 | 1DA | D04Q010 | 10.4.22 | 1DA15TP01 | 415V SWGR O/G MODULE # 1DA15RF | VFD PANEL FOR CEP-1B | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 87 | [5 empty] | POWER SUPPLY (10kVA) | XLPE-AL UNARMOURED | MV49-01, MV70-03, MV42-01, MV43-02, MV45-L2, MA07-01, MR08-01, DC07-03, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, DR06-02, AC10-02, AC11-02, AC12-02, ZZ99- |  | EPD | EDN
1 | 1DC | D01Q630 | 10.4.05 | 1DC01BP01 | 415V SWGR O/G MODULE # 1DC01FB | CWPH & CHLORINATION MCC # 0SB SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 190 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT08-L1, CT07-L1, CT06-L1, CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L3, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L3, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, ZZ99- |  | EPD | EPD
2 | 1DC | D01Q630 | 10.4.05 | 1DC01BP02 | 415V SWGR O/G MODULE # 1DC01FB | CWPH & CHLORINATION MCC # 0SB SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 190 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT08-L1, CT07-L1, CT06-L1, CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L3, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L3, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, ZZ99- |  | EPD | EPD
3 | 1DC | D01Q630 | 10.4.05 | 1DC01BP03 | 415V SWGR O/G MODULE # 1DC01FB | CWPH & CHLORINATION MCC # 0SB SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 190 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT08-L1, CT07-L1, CT06-L1, CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L3, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L3, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, ZZ99- |  | EPD | EPD
4 | 1DC | D01Q400 | 10.4.04 | 1DC01BP04 | 415V SWGR O/G MODULE # 1DC01FB | CWPH & CHLORINATION MCC # 0SB SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 191 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT08-L1, CT07-L1, CT06-L1, CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L4, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L4, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, ZZ99- |  | EPD | EPD
5 | 1DC | D03L2.5 | 10.4.26 | 1DC01DP01 | 415V SWGR O/G MODULE # 1DC01FD | SUPPLY AIR FAN A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
6 | 1DC | D03L2.5 | 10.4.26 | 1DC01EP01 | 415V SWGR O/G MODULE # 1DC01FE | SUPPLY AIR FAN C | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
7 | 1DC | D3HQ025 | 10.4.18 | 1DC01FP01 | 415V SWGR O/G MODULE # 1DC01FF | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CT08-R1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
8 | 1DC | D3HQ025 | 10.4.18 | 1DC01GP01 | 415V SWGR O/G MODULE # 1DC01FG | PORTABLE SUMP PUMP A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CT08-R1, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
9 | 1DC | D03L2.5 | 10.4.26 | 1DC01HP01 | 415V SWGR O/G MODULE # 1DC01FH | SUPPLY AIR FAN E | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
10 | 1DC | D03Q095 | 10.4.15 | 1DC01PP01 | 415V SWGR O/G MODULE # 1DC01RB | LDB I/C-A | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | CT08-R1, CT07-R1, CT06-R1, CT05-R1, CT04-R1, CT03-R1, CT02-R1, CT09-01, ZZ99- |  | EPD | PEM
11 | 1DC | D02C1.5 | 10.5.01 | 1DC01RC01 | 415V SWGR MOTOR MODULE # 1DC01RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 251 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
12 | 1DC | D03Q025 | 10.4.12 | 1DC01RP01 | 415V SWGR MOTOR MODULE # 1DC01RD | SLUDGE PUMP A | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 251 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | CT08-R1, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
13 | 1DC | D04Q010 | 10.4.22 | 1DC01UP01 | 415V SWGR O/G MODULE # 1DC01RG | LIGHTING | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | CT08-R1, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
14 | 1DC | D3HQ025 | 10.4.18 | 1DC01VP01 | 415V SWGR O/G MODULE # 1DC01RH | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CT08-R1, HR02-02, ZZ99- |  | EPD | EPD
15 | 1DC | D02L2.5 | 10.4.24 | 1DC02RP01 | 415V SWGR O/G MODULE # 1DC02RD | SINGLE PHASE SUPPLY TO CT TRANSFORMER # 1DCT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | CT08-L3, CT07-L3, CT06-L3, CT05-L3, ZZ99- |  | EPD | JHS
16 | 1DC | D02L2.5 | 10.4.24 | 1DC02SP01 | 415V SWGR O/G MODULE # 1DC02RE | NSPBD FOR 1DCT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | JHS
17 | 1DC | D04Q010 | 10.4.22 | 1DC02TP01 | 415V SWGR O/G MODULE # 1DC02RF | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
18 | 1DC | D04Q010 | 10.4.22 | 1DC03GP01 | 415V SWGR O/G MODULE # 1DC03FG | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
19 | 1DC | D07C1.5 | 10.5.08 | 1DC04AC01 | 415V SWGR MOTOR MODULE # 1DC04FA | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 144 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
20 | 1DC | D02L2.5 | 10.4.24 | 1DC04AC02 | 415V SWGR MOTOR MODULE # 1DC04FA | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 144 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
21 | 1DC | D03Q240 | 10.4.17 | 1DC04AP01 | 415V SWGR MOTOR MODULE # 1DC04FA | FAN A | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 143 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
22 | 1DC | D03Q240 | 10.4.17 | 1DC04AP02 | 415V SWGR MOTOR MODULE # 1DC04FA | FAN A | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 143 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
23 | 1DC | D07C1.5 | 10.5.08 | 1DC04BC01 | 415V SWGR MOTOR MODULE # 1DC04FB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 174 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
24 | 1DC | D02L2.5 | 10.4.24 | 1DC04BC02 | 415V SWGR MOTOR MODULE # 1DC04FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 174 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
25 | 1DC | D03Q240 | 10.4.17 | 1DC04BP01 | 415V SWGR MOTOR MODULE # 1DC04FB | FAN C | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 173 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
26 | 1DC | D03Q240 | 10.4.17 | 1DC04BP02 | 415V SWGR MOTOR MODULE # 1DC04FB | FAN C | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 173 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
27 | 1DC | D07C1.5 | 10.5.08 | 1DC05AC01 | 415V SWGR MOTOR MODULE # 1DC05FA | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 204 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
28 | 1DC | D02L2.5 | 10.4.24 | 1DC05AC02 | 415V SWGR MOTOR MODULE # 1DC05FA | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 204 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
29 | 1DC | D03Q240 | 10.4.17 | 1DC05AP01 | 415V SWGR MOTOR MODULE # 1DC05FA | FAN E | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 203 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
30 | 1DC | D03Q240 | 10.4.17 | 1DC05AP02 | 415V SWGR MOTOR MODULE # 1DC05FA | FAN E | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 203 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
31 | 1DC | D07C1.5 | 10.5.08 | 1DC05BC01 | 415V SWGR MOTOR MODULE # 1DC05FB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 234 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
32 | 1DC | D02L2.5 | 10.4.24 | 1DC05BC02 | 415V SWGR MOTOR MODULE # 1DC05FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 234 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
33 | 1DC | D03Q240 | 10.4.17 | 1DC05BP01 | 415V SWGR MOTOR MODULE # 1DC05FB | FAN G | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 233 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
34 | 1DC | D03Q240 | 10.4.17 | 1DC05BP02 | 415V SWGR MOTOR MODULE # 1DC05FB | FAN G | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 233 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
35 | 1DC | D07C1.5 | 10.5.08 | 1DC06AC01 | 415V SWGR MOTOR MODULE # 1DC06FA | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 269 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
36 | 1DC | D02L2.5 | 10.4.24 | 1DC06AC02 | 415V SWGR MOTOR MODULE # 1DC06FA | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 269 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
37 | 1DC | D03Q240 | 10.4.17 | 1DC06AP01 | 415V SWGR MOTOR MODULE # 1DC06FA | FAN J | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 268 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-L1, CT08-L1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
38 | 1DC | D03Q240 | 10.4.17 | 1DC06AP02 | 415V SWGR MOTOR MODULE # 1DC06FA | FAN J | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 269 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT07-R1, CT08-R1, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
39 | 1DC | E04V0.5 | 10.7.02 | 1DC07BC01 | 415V SWGR I/C MODULE # 1DC07FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 198 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | CT07-R3, CT06-R3, CT05-R3, CT04-R3, CT03-R3, CT02-R3, CT01-R3, HR01-R3, IP35-R3, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IP22-L4, WR02-05, CW08-05, CW07-05, CW06-05, CW16-03, CW17-03, ZZ99- |  | EPD | EDN
40 | 1DC | D02L2.5 | 10.4.24 | 1DC07BC02 | 415V SWGR I/C MODULE # 1DC07FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | CT07-L3, CT06-L3, CT05-L3, CT04-L3, CT03-L3, CT02-L3, CT01-L3, HR01-L3, IP35-L3, IP36-R3, IP37-R3, CT11-02, ZZ99- |  | EPD | JHS
41 | 1DC | D02L2.5 | 10.4.24 | 1DC07BC03 | 415V SWGR I/C MODULE # 1DC07FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | CT07-L3, CT06-L3, CT05-L3, CT04-L3, CT03-L3, CT02-L3, CT01-L3, HR01-L3, IP35-L3, IP36-R3, IP37-R3, CT11-02, ZZ99- |  | EPD | JHS
42 | 1DC | D02C1.5 | 10.5.01 | 1DC07BC04 | 415V SWGR I/C MODULE # 1DC07FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 302 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | CT07-L3, CT06-L3, CT05-L3, CT04-L3, CT03-L3, CT02-L3, CT01-L3, HR01-L3, IP35-L3, IP34-L4, IP33-L7, IP32-L4, IP31-L4, IP30-L4, IP29-L4, IP28-L4, IP27-L7, IP26-L4, IP25-L4, IP24-L4, IP23-L4, IR38-L3, IP19-L3, IP18-L3, IP17-L3, IP16-L3, IP15-L3, IP14-R2, IR03-L3, IP02-L5, IP01-L5, TY19-L3, TY18-L3, TY17-L4, TY16-L4, LR03-03, MR03-03, MA02-03, MV35-L2, MV18-L2, MV17-L2, MV15-02, ZZ99- |  | EPD | BPL
43 | 1DC | E04V0.5 | 10.7.02 | 1DC07BC05 | 415V SWGR I/C MODULE # 1DC07FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 198 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | CT07-R3, CT06-R3, CT05-R3, CT04-R3, CT03-R3, CT02-R3, CT01-R3, HR01-R3, IP35-R3, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IP22-L4, WR02-05, CW08-05, CW07-05, CW06-05, CW16-03, CW17-03, ZZ99- |  | EPD | EDN
44 | 1DC | E04V0.5 | 10.7.02 | 1DC09BC01 | 415V SWGR B/C MODULE # 1DC09FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 195 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | CT06-R3, CT05-R3, CT04-R3, CT03-R3, CT02-R3, CT01-R3, HR01-R3, IP35-R3, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IP22-L4, WR02-05, CW08-05, CW07-05, CW06-05, CW16-03, CW17-03, ZZ99- |  | EPD | EDN
45 | 1DC | E04V0.5 | 10.7.02 | 1DC09BC02 | 415V SWGR B/C MODULE # 1DC09FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 195 | [5 empty] | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | CT06-R3, CT05-R3, CT04-R3, CT03-R3, CT02-R3, CT01-R3, HR01-R3, IP35-R3, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IP22-L4, WR02-05, CW08-05, CW07-05, CW06-05, CW16-03, CW17-03, ZZ99- |  | EPD | EDN
46 | 1DC | E04V0.5 | 10.7.02 | 1DC10BC01 | 415V SWGR I/C MODULE # 1DC10FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 195 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | CT06-R3, CT05-R3, CT04-R3, CT03-R3, CT02-R3, CT01-R3, HR01-R3, IP35-R3, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IP22-L4, WR02-05, CW08-05, CW07-05, CW06-05, CW16-03, CW17-03, ZZ99- |  | EPD | EDN
47 | 1DC | D02L2.5 | 10.4.24 | 1DC10BC02 | 415V SWGR I/C MODULE # 1DC10FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | CT06-L3, CT05-L3, CT04-L3, CT03-L3, CT02-L3, CT01-L3, HR01-L3, IP35-L3, IP36-R3, CT10-02, ZZ99- |  | EPD | JHS
48 | 1DC | D02L2.5 | 10.4.24 | 1DC10BC03 | 415V SWGR I/C MODULE # 1DC10FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | CT06-L3, CT05-L3, CT04-L3, CT03-L3, CT02-L3, CT01-L3, HR01-L3, IP35-L3, IP36-R3, CT10-02, ZZ99- |  | EPD | JHS
49 | 1DC | D02C1.5 | 10.5.01 | 1DC10BC04 | 415V SWGR I/C MODULE # 1DC10FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 296 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | CT06-L3, CT05-L3, CT04-L3, CT03-L3, CT02-L3, CT01-L3, HR01-L3, IP35-L3, IP34-L4, IP33-L7, IP32-L4, IP31-L4, IP30-L4, IP29-L4, IP28-L4, IP27-L7, IP26-L4, IP25-L4, IP24-L4, IP23-L4, IR38-L3, IP19-L3, IP18-L3, IP17-L3, IP16-L3, IP15-L3, IP14-R2, IR03-L3, IP02-L5, IP01-L5, TY19-L3, TY18-L3, TY17-L4, TY16-L4, LR03-03, MR03-03, MA02-03, MV35-L2, MV18-L2, MV19-02, ZZ99- |  | EPD | BPL
50 | 1DC | E04V0.5 | 10.7.02 | 1DC10BC05 | 415V SWGR I/C MODULE # 1DC10FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 195 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | CT06-R3, CT05-R3, CT04-R3, CT03-R3, CT02-R3, CT01-R3, HR01-R3, IP35-R3, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IP22-L4, WR02-05, CW08-05, CW07-05, CW06-05, CW16-03, CW17-03, ZZ99- |  | EPD | EDN
51 | 1DC | D07C1.5 | 10.5.08 | 1DC11BC01 | 415V SWGR MOTOR MODULE # 1DC11FB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 295 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
52 | 1DC | D02L2.5 | 10.4.24 | 1DC11BC02 | 415V SWGR MOTOR MODULE # 1DC11FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 295 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
53 | 1DC | D03Q240 | 10.4.17 | 1DC11BP01 | 415V SWGR MOTOR MODULE # 1DC11FB | FAN K | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 297 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-L1, CT06-L1, CT07-L2, CT08-L2, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
54 | 1DC | D03Q240 | 10.4.17 | 1DC11BP02 | 415V SWGR MOTOR MODULE # 1DC11FB | FAN K | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 297 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-L1, CT06-L1, CT07-L2, CT08-L2, HR02-01, IP65-01, IP66-01, IP67-01, IP68-01, IP69-01, ZZ99- |  | EPD | PEM
55 | 1DC | D07C1.5 | 10.5.08 | 1DC12AC01 | 415V SWGR MOTOR MODULE # 1DC12FA | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 260 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
56 | 1DC | D02L2.5 | 10.4.24 | 1DC12AC02 | 415V SWGR MOTOR MODULE # 1DC12FA | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 260 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
57 | 1DC | D03Q240 | 10.4.17 | 1DC12AP01 | 415V SWGR MOTOR MODULE # 1DC12FA | FAN H | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 261 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-L1, CT06-L1, CT07-L2, CT08-L2, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
58 | 1DC | D03Q240 | 10.4.17 | 1DC12AP02 | 415V SWGR MOTOR MODULE # 1DC12FA | FAN H | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 261 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-L1, CT06-L1, CT07-L2, CT08-L2, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
59 | 1DC | D07C1.5 | 10.5.08 | 1DC12BC01 | 415V SWGR MOTOR MODULE # 1DC12FB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 225 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
60 | 1DC | D02L2.5 | 10.4.24 | 1DC12BC02 | 415V SWGR MOTOR MODULE # 1DC12FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 225 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
61 | 1DC | D03Q240 | 10.4.17 | 1DC12BP01 | 415V SWGR MOTOR MODULE # 1DC12FB | FAN F | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 226 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-L1, CT06-L1, CT07-L2, CT08-L2, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
62 | 1DC | D03Q240 | 10.4.17 | 1DC12BP02 | 415V SWGR MOTOR MODULE # 1DC12FB | FAN F | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 226 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-L1, CT06-L1, CT07-L2, CT08-L2, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
63 | 1DC | D07C1.5 | 10.5.08 | 1DC13BC01 | 415V SWGR MOTOR MODULE # 1DC13FB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 195 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
64 | 1DC | D02L2.5 | 10.4.24 | 1DC13BC02 | 415V SWGR MOTOR MODULE # 1DC13FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 195 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
65 | 1DC | D03Q240 | 10.4.17 | 1DC13BP01 | 415V SWGR MOTOR MODULE # 1DC13FB | FAN D | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 195 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-R1, CT06-R1, CT07-R1, CT08-R1, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
66 | 1DC | D03Q240 | 10.4.17 | 1DC13BP02 | 415V SWGR MOTOR MODULE # 1DC13FB | FAN D | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 195 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-R1, CT06-R1, CT07-R1, CT08-R1, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
67 | 1DC | D07C1.5 | 10.5.08 | 1DC13CC01 | 415V SWGR MOTOR MODULE # 1DC13FC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 165 | [5 empty] | EPB START, EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
68 | 1DC | D02L2.5 | 10.4.24 | 1DC13CC02 | 415V SWGR MOTOR MODULE # 1DC13FC | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 165 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | PEM
69 | 1DC | D03Q240 | 10.4.17 | 1DC13CP01 | 415V SWGR MOTOR MODULE # 1DC13FC | FAN B | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 165 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-R1, CT06-R1, CT07-R1, CT08-R1, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
70 | 1DC | D03Q240 | 10.4.17 | 1DC13CP02 | 415V SWGR MOTOR MODULE # 1DC13FC | FAN B | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 165 | [5 empty] | POWER SUPPLY (132kW) | XLPE-AL UNARMOURED | CT05-R1, CT06-R1, CT07-R1, CT08-R1, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
71 | 1DC | D01Q630 | 10.4.05 | 1DC14BP01 | 415V SWGR O/G MODULE # 1DC14FB | CWPH & CHLORINATION MCC # 0SB SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L3, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L3, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, CW04-01, CW03-01, ZZ99- |  | EPD | EPD
72 | 1DC | D01Q630 | 10.4.05 | 1DC14BP02 | 415V SWGR O/G MODULE # 1DC14FB | CWPH & CHLORINATION MCC # 0SB SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L3, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L3, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, CW04-01, CW03-01, ZZ99- |  | EPD | EPD
73 | 1DC | D01Q630 | 10.4.05 | 1DC14BP03 | 415V SWGR O/G MODULE # 1DC14FB | CWPH & CHLORINATION MCC # 0SB SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L3, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L3, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, CW04-01, CW03-01, ZZ99- |  | EPD | EPD
74 | 1DC | D01Q400 | 10.4.04 | 1DC14BP04 | 415V SWGR O/G MODULE # 1DC14FB | CWPH & CHLORINATION MCC # 0SB SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | CT05-L1, CT04-L1, CT03-L1, CT02-L1, CT01-L1, HR01-L1, IP35-L1, IP34-L2, IP33-L4, IP32-L2, IP31-L2, IP30-L2, IP29-L2, IP28-L2, IP27-L4, IP26-L2, IP25-L2, IP24-L2, IP23-L2, IP22-L1, WR02-01, CW08-01, CW07-01, CW06-01, CW05-01, CW04-01, CW03-01, ZZ99- |  | EPD | EPD
75 | 1DC | D3HQ025 | 10.4.18 | 1DC14HP01 | 415V SWGR O/G MODULE # 1DC14FH | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 44 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CT05-R1, CT06-R1, CT07-R1, CT08-R1, HR02-02, ZZ99- |  | EPD | EPD
76 | 1DC | D04Q010 | 10.4.22 | 1DC14TP01 | 415V SWGR O/G MODULE # 1DC14RF | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
77 | 1DC | D04Q010 | 10.4.22 | 1DC15PP01 | 415V SWGR O/G MODULE # 1DC15RB | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
78 | 1DC | D02L2.5 | 10.4.24 | 1DC15RP01 | 415V SWGR O/G MODULE # 1DC15RD | NSPBD FOR 1DCT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | JHS
79 | 1DC | D02L2.5 | 10.4.24 | 1DC15SP01 | 415V SWGR O/G MODULE # 1DC15RE | SINGLE PHASE SUPPLY TO CT TRANSFORMER # 1DCT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | CT04-L3, CT03-L3, CT02-L3, CT01-L3, HR01-L3, IP35-L3, IP36-R3, CT10-02, ZZ99- |  | EPD | JHS
80 | 1DC | D03Q095 | 10.4.15 | 1DC16BP01 | 415V SWGR O/G MODULE # 1DC16FB | LDB I/C-B | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | CT04-L1, CT03-L1, CT02-L1, CT09-01, ZZ99- |  | EPD | PEM
81 | 1DC | D02C1.5 | 10.5.01 | 1DC16HC01 | 415V SWGR MOTOR MODULE # 1DC16FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 263 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CT04-L3, CT05-L3, CT06-L3, CT07-L3, CT08-L3, HR02-03, IP65-03, IP66-03, IP67-03, IP68-03, IP69-03, ZZ99- |  | EPD | EPD
82 | 1DC | D03Q025 | 10.4.12 | 1DC16HP01 | 415V SWGR MOTOR MODULE # 1DC16FH | SLUDGE PUMP B | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 266 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | CT04-L1, CT05-L2, CT06-L1, CT07-L2, CT08-L2, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
83 | 1DC | D03L2.5 | 10.4.26 | 1DC16PP01 | 415V SWGR O/G MODULE # 1DC16RB | SUPPLY AIR FAN F | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
84 | 1DC | D3HQ025 | 10.4.18 | 1DC16QP01 | 415V SWGR O/G MODULE # 1DC16RC | PORTABLE SUMP PUMP B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CT04-L1, CT05-L2, CT06-L1, CT07-L2, CT08-L2, HR02-02, IP65-02, IP66-02, ZZ99- |  | EPD | PEM
85 | 1DC | D03L2.5 | 10.4.26 | 1DC16TP01 | 415V SWGR O/G MODULE # 1DC16RF | SUPPLY AIR FAN D | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
86 | 1DC | D03L2.5 | 10.4.26 | 1DC16UP01 | 415V SWGR O/G MODULE # 1DC16RG | SUPPLY AIR FAN B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
87 | 1DC | D3HQ025 | 10.4.18 | 1DC16VP01 | 415V SWGR O/G MODULE # 1DC16RH | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 166 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CT04-L1, CT05-L2, CT06-L1, CT07-L2, CT08-L2, HR02-02, IP65-02, IP66-02, IP67-02, IP68-02, IP69-02, ZZ99- |  | EPD | PEM
1 | 1DD | E04V0.5 | 10.7.02 | 1DD02AC01 | 415V SWGR I/C MODULE # 1DD02FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 42 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | FP17-R3, FP18-R3, FP19-R3, FP20-R3, FP21-03, FP22-03, FP07-03, FP08-03, FP09-03, FP10-03, FP11-03, ZZ99- |  | EPD | EDN
2 | 1DD | D02L2.5 | 10.4.24 | 1DD02AC02 | 415V SWGR I/C MODULE # 1DD02FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | FP17-L3, FP16-02, FP01-03, FP02-02, ZZ99- |  | EPD | JHS
3 | 1DD | D02L2.5 | 10.4.24 | 1DD02AC03 | 415V SWGR I/C MODULE # 1DD02FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | FP17-L3, FP16-02, FP01-03, FP02-02, ZZ99- |  | EPD | JHS
4 | 1DD | D02C1.5 | 10.5.01 | 1DD02AC04 | 415V SWGR I/C MODULE # 1DD02FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 475 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | FP17-L3, FP16-02, FP01-03, FR01-03, IP52-L7, IP51-L7, IR05-L3, IP50-L3, IP49-L3, IP48-L3, IP47-L3, IP46-L3, IP45-L3, IP44-L3, IP43-L3, IP42-L3, IP41-L3, IP40-L3, IP39-L3, IR04-L3, IP38-L4, IP37-L4, IP36-L4, IP34-L4, IP33-L7, IP32-L4, IP31-L4, IP30-L4, IP29-L4, IP28-L4, IP27-L7, IP26-L4, IP25-L4, IP24-L4, IP23-L4, IR38-L3, IP19-L3, IP18-L3, IP17-L3, IP16-L3, IP15-L3, IP14-R2, IR03-L3, IP02-L5, IP01-L5, TY19-L3, TY18-L3, TY17-L4, TY16-L4, LR03-03, MR03-03, MA02-03, MV35-L2, MV18-L2, MV17-L2, MV15-02, MV14-02, ZZ99- |  | EPD | BPL
5 | 1DD | E04V0.5 | 10.7.02 | 1DD02AC05 | 415V SWGR I/C MODULE # 1DD02FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 42 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | FP17-R3, FP18-R3, FP19-R3, FP20-R3, FP21-03, FP22-03, FP07-03, FP08-03, FP09-03, FP10-03, FP11-03, ZZ99- |  | EPD | EDN
6 | 1DD | D01Q400 | 10.4.04 | 1DD03BP01 | 415V SWGR O/G MODULE # 1DD03FB | FW & CLARIFIED WATER MCC # 0SC SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP17-L1, FP16-01, FP03-L2, FP04-L2, FP05-L2, ZZ99- |  | EPD | EPD
7 | 1DD | D01Q400 | 10.4.04 | 1DD03BP02 | 415V SWGR O/G MODULE # 1DD03FB | FW & CLARIFIED WATER MCC # 0SC SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP17-L1, FP16-01, FP03-L2, FP04-L2, FP05-L2, ZZ99- |  | EPD | EPD
8 | 1DD | D01Q400 | 10.4.04 | 1DD03BP03 | 415V SWGR O/G MODULE # 1DD03FB | FW & CLARIFIED WATER MCC # 0SC SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP17-L1, FP16-01, FP03-L2, FP04-L2, FP05-L2, ZZ99- |  | EPD | EPD
9 | 1DD | D01Q400 | 10.4.04 | 1DD03BP04 | 415V SWGR O/G MODULE # 1DD03FB | FW & CLARIFIED WATER MCC # 0SC SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP17-L1, FP16-01, FP03-L2, FP04-L2, FP05-L2, ZZ99- |  | EPD | EPD
10 | 1DD | D02C1.5 | 10.5.01 | 1DD03DC01 | 415V SWGR MOTOR MODULE # 1DD03FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
11 | 1DD | D03L2.5 | 10.4.26 | 1DD03DP01 | 415V SWGR MOTOR MODULE # 1DD03FD | WASTE WATER TRANSFER PUMP-P5-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
12 | 1DD | D02C1.5 | 10.5.01 | 1DD03EC01 | 415V SWGR MOTOR MODULE # 1DD03FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
13 | 1DD | D03L2.5 | 10.4.26 | 1DD03EP01 | 415V SWGR MOTOR MODULE # 1DD03FE | ALUM DOSING PUMP-DP2-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
14 | 1DD | D02L2.5 | 10.4.24 | 1DD03FP01 | 415V SWGR O/G MODULE # 1DD03FF | PROPELLOR FAN-A | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 44 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | FP17-L3, FP18-L3, FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | PEM
15 | 1DD | D03L2.5 | 10.4.26 | 1DD03GP01 | 415V SWGR O/G MODULE # 1DD03FG | AXIAL EXHAUST AIR FAN-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (1.5 kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
16 | 1DD | D04Q010 | 10.4.22 | 1DD03HP01 | 415V SWGR O/G MODULE # 1DD03FH | HRSCC RECIRCULATOR HRSCCS-A | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | FP17-R1, FP18-R1, FP19-R1, FP20-R1, FR03-01, ZZ99- |  | EPD | PEM
17 | 1DD | D3HQ025 | 10.4.18 | 1DD03PP01 | 415V SWGR O/G MODULE # 1DD03RB | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | FP17-L1, FP18-L1, FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP10-01, FP11-01, ZZ99- |  | EPD | EDN
18 | 1DD | D02C1.5 | 10.5.01 | 1DD03QC01 | 415V SWGR MOTOR MODULE # 1DD03RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
19 | 1DD | D03L2.5 | 10.4.26 | 1DD03QP01 | 415V SWGR MOTOR MODULE # 1DD03RC | SODIUM HYPOCHLORITE DOSING PUMP-DP4-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
20 | 1DD | D02Q010 | 10.4.06 | 1DD03RP01 | 415V SWGR O/G MODULE # 1DD03RD | SPLIT AC FOR CONTROL ROOM-A | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP17-L1, FP18-L1, FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP10-01, ZZ99- |  | EPD | PEM
21 | 1DD | D03L2.5 | 10.4.26 | 1DD03SP01 | 415V SWGR O/G MODULE # 1DD03RE | AXIAL EXHAUST AIR FAN-C | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
22 | 1DD | D03L2.5 | 10.4.26 | 1DD03UP01 | 415V SWGR O/G MODULE # 1DD03RG | AXIAL EXHAUST AIR FAN-E | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
23 | 1DD | D02C1.5 | 10.5.01 | 1DD03VC01 | 415V SWGR MOTOR MODULE # 1DD03RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP17-L3, FP18-L3, FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
24 | 1DD | D03L2.5 | 10.4.26 | 1DD03VP01 | 415V SWGR MOTOR MODULE # 1DD03RH | HRSCC SCRAPPER MECHANISM-HRSCC1-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP17-L3, FP18-L3, FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | PEM
25 | 1DD | D3HQ025 | 10.4.18 | 1DD03WP01 | 415V SWGR O/G MODULE # 1DD03FI | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
26 | 1DD | D02Q010 | 10.4.06 | 1DD04FP01 | 415V SWGR O/G MODULE # 1DD04FF | SPLIT AC FOR CONTROL ROOM-C | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP17-L1, FP18-L1, FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP10-01, FP11-01, ZZ99- |  | EPD | PEM
27 | 1DD | D03Q095 | 10.4.15 | 1DD04GP01 | 415V SWGR O/G MODULE # 1DD04FG | LDB I/C-B | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 34 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | FP17-L1, FP16-01, FP03-R2, FP04-R2, FP05-R2, FP06-R1, ZZ99- |  | EPD | PEM
28 | 1DD | D04Q010 | 10.4.22 | 1DD04PP01 | 415V SWGR O/G MODULE # 1DD04RB | PTP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | FP17-R1, FP18-R1, FP19-R1, FP20-R1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP12-01, FP13-01, ZZ99- |  | EPD | EDN
29 | 1DD | D02C1.5 | 10.5.01 | 1DD04QC01 | 415V SWGR MOTOR MODULE # 1DD04RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
30 | 1DD | D03L2.5 | 10.4.26 | 1DD04QP01 | 415V SWGR MOTOR MODULE # 1DD04RC | POLYMER DOSING PUMP-DP3-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
31 | 1DD | D02Q010 | 10.4.06 | 1DD04RP01 | 415V SWGR O/G MODULE # 1DD04RD | SPLIT AC FOR CONTROL ROOM-E | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP17-R1, FP18-R1, FP19-R1, FP20-R1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP12-01, FP13-01, ZZ99- |  | EPD | PEM
32 | 1DD | D03L2.5 | 10.4.26 | 1DD04SP01 | 415V SWGR O/G MODULE # 1DD04RE | AXIAL EXHAUST AIR FAN-G | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
33 | 1DD | D02C1.5 | 10.5.01 | 1DD04TC01 | 415V SWGR MOTOR MODULE # 1DD04RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
34 | 1DD | D03L2.5 | 10.4.26 | 1DD04TP01 | 415V SWGR MOTOR MODULE # 1DD04RF | LIME SOLUTION PREPARATION TANK-DT1-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
35 | 1DD | D03L2.5 | 10.4.26 | 1DD04UP01 | 415V SWGR O/G MODULE # 1DD04RG | AXIAL EXHAUST AIR FAN-J | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
36 | 1DD | D3HQ025 | 10.4.18 | 1DD04VP01 | 415V SWGR O/G MODULE # 1DD04RH | PORTABLE SUMP PUMP B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
37 | 1DD | D02Q010 | 10.4.06 | 1DD04WP01 | 415V SWGR O/G MODULE # 1DD04RI | SPLIT AC FOR CONTROL ROOM-G | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 55 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP17-R1, FP18-R1, FP19-R1, FP20-R1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP12-01, FP13-01, FP14-01, ZZ99- |  | EPD | PEM
38 | 1DD | D02C1.5 | 10.5.01 | 1DD05BC01 | 415V SWGR MOTOR MODULE # 1DD05FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP18-L3, FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
39 | 1DD | D03Q010 | 10.4.11 | 1DD05BP01 | 415V SWGR MOTOR MODULE # 1DD05FB | FILTER BACKWASH PUMPS-P3-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 64 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | FP18-L1, FP19-L1, FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
40 | 1DD | D04Q010 | 10.4.22 | 1DD05PP01 | 415V SWGR O/G MODULE # 1DD05RB | PTP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 39 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | FP18-L1, FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP12-01, FP13-01, ZZ99- |  | EPD | EDN
41 | 1DD | D02L2.5 | 10.4.24 | 1DD05RP01 | 415V SWGR O/G MODULE # 1DD05RD | SINGLE PHASE SUPPLY TO PTP TRANSFORMER # 1DDT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | FP18-L3, FP19-L3, FP20-L3, FP21-02, FP22-02, FP07-02, FP08-02, ZZ99- |  | EPD | JHS
42 | 1DD | D03L2.5 | 10.4.26 | 1DD05SP01 | 415V SWGR O/G MODULE # 1DD05RE | AXIAL EXHAUST AIR FAN-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 67 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
43 | 1DD | D02C1.5 | 10.5.01 | 1DD05TC01 | 415V SWGR MOTOR MODULE # 1DD05RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP18-L3, FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
44 | 1DD | D03Q025 | 10.4.12 | 1DD05TP01 | 415V SWGR MOTOR MODULE # 1DD05RF | SLUDGE TRANSFER PUMP-P1-A | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | FP18-L1, FP19-L1, FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
45 | 1DD | D02C1.5 | 10.5.01 | 1DD06CC01 | 415V SWGR MOTOR MODULE # 1DD06FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 91 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP18-L3, FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
46 | 1DD | D03Q010 | 10.4.11 | 1DD06CP01 | 415V SWGR MOTOR MODULE # 1DD06FC | BLOWER FOR SLUDGE PIT-B1-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | FP18-L1, FP19-L1, FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
47 | 1DD | D02L2.5 | 10.4.24 | 1DD06DP01 | 415V SWGR O/G MODULE # 1DD06FD | NSPBD FOR 1DDT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 26 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | FP18-L3, FP17-L3, FP16-02, ZZ99- |  | EPD | JHS
48 | 1DD | D02C1.5 | 10.5.01 | 1DD07BC01 | 415V SWGR MOTOR MODULE # 1DD07FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP18-L3, FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
49 | 1DD | D03Q025 | 10.4.12 | 1DD07BP01 | 415V SWGR MOTOR MODULE # 1DD07FB | SLUDGE TRANSFER PUMP-P1-C | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | FP18-L1, FP19-L1, FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
50 | 1DD | D04Q010 | 10.4.22 | 1DD07EP01 | 415V SWGR O/G MODULE # 1DD07FE | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | FP18-L1, FP17-L2, FP16-01, FP01-03, ZZ99- |  | EPD | PEM
51 | 1DD | D3HQ050 | 10.4.19 | 1DD07HP01 | 415V SWGR O/G MODULE # 1DD07FH | PTP FLOAT-CUM-BOOST CHARGER- A | 3.5C X 050 XLPE-Al FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | FP18-L1, FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, ZZ99- |  | EPD | PEM
52 | 1DD | D02C1.5 | 10.5.01 | 1DD07PC01 | 415V SWGR MOTOR MODULE # 1DD07RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
53 | 1DD | D03L2.5 | 10.4.26 | 1DD07PP01 | 415V SWGR MOTOR MODULE # 1DD07RB | LIME DOSING PUMP-DP1-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
54 | 1DD | D3HQ025 | 10.4.18 | 1DD07RP01 | 415V SWGR O/G MODULE # 1DD07RD | ELECTRIC HOIST IN CHEMICAL ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | FP18-L1, FP17-L1, FP16-01, FP01-03, FP02-02, ZZ99- |  | EPD | PEM
55 | 1DD | D02C1.5 | 10.5.01 | 1DD07SC01 | 415V SWGR MOTOR MODULE # 1DD07RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 57 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
56 | 1DD | D03L2.5 | 10.4.26 | 1DD07SP01 | 415V SWGR MOTOR MODULE # 1DD07RE | ALUM SOLUTION PREPARATION TANK-DT2-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 57 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
57 | 1DD | D03L2.5 | 10.4.26 | 1DD07TP01 | 415V SWGR O/G MODULE # 1DD07RF | AXIAL EXHAUST FAN-B2 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 72 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
58 | 1DD | D3HQ025 | 10.4.18 | 1DD07UP01 | 415V SWGR O/G MODULE # 1DD07RG | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | Hold |  | EPD | EPD
59 | 1DD | D05C1.5 | 10.5.06 | 1DD08AC01 | 415V SWGR MOTOR MODULE # 1DD08FA | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | FP18-L3, FP17-L3, FP16-02, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW21-02, ZZ99- |  | EPD | EPD
60 | 1DD | D02L2.5 | 10.4.24 | 1DD08AC02 | 415V SWGR MOTOR MODULE # 1DD08FA | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP18-L3, FP17-L3, FP16-02, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW21-02, ZZ99- |  | EPD | PEM
61 | 1DD | D03Q240 | 10.4.17 | 1DD08AP01 | 415V SWGR MOTOR MODULE # 1DD08FA | APH WASH PUMP-A | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (90kW) | XLPE-AL UNARMOURED | FP18-L1, FP17-L1, FP16-01, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW21-01, ZZ99- |  | EPD | PEM
62 | 1DD | D03Q240 | 10.4.17 | 1DD08AP02 | 415V SWGR MOTOR MODULE # 1DD08FA | APH WASH PUMP-A | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (90kW) | XLPE-AL UNARMOURED | FP18-L1, FP17-L1, FP16-01, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW21-01, ZZ99- |  | EPD | PEM
63 | 1DD | E04V0.5 | 10.7.02 | 1DD09AC01 | 415V SWGR B/C MODULE # 1DD09FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 34 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | FP19-R3, FP20-R3, FP21-03, FP22-03, FP07-03, FP08-03, FP09-03, FP10-03, FP11-03, ZZ99- |  | EPD | EDN
64 | 1DD | E04V0.5 | 10.7.02 | 1DD09AC02 | 415V SWGR B/C MODULE # 1DD09FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 34 | [5 empty] | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | FP19-R3, FP20-R3, FP21-03, FP22-03, FP07-03, FP08-03, FP09-03, FP10-03, FP11-03, ZZ99- |  | EPD | EDN
65 | 1DD | D05C1.5 | 10.5.06 | 1DD10BC01 | 415V SWGR MOTOR MODULE # 1DD10FB | EMERGENCY STOP PB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | EM.STOP OPERATED/NOT OPERATED | PVC-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FP16-02, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW22-02, ZZ99- |  | EPD | EPD
66 | 1DD | D02L2.5 | 10.4.24 | 1DD10BC02 | 415V SWGR MOTOR MODULE # 1DD10FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FP16-02, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW22-02, ZZ99- |  | EPD | PEM
67 | 1DD | D03Q240 | 10.4.17 | 1DD10BP01 | 415V SWGR MOTOR MODULE # 1DD10FB | APH WASH PUMP-B | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (90kW) | XLPE-AL UNARMOURED | FP19-L1, FP18-L1, FP17-L1, FP16-01, FP01-03, FR01-03, IP53-03, IP54-03, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW22-01, ZZ99- |  | EPD | PEM
68 | 1DD | D03Q240 | 10.4.17 | 1DD10BP02 | 415V SWGR MOTOR MODULE # 1DD10FB | APH WASH PUMP-B | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (90kW) | XLPE-AL UNARMOURED | FP19-L1, FP18-L1, FP17-L1, FP16-01, FP01-03, FR01-03, IP53-03, IP54-03, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW22-01, ZZ99- |  | EPD | PEM
69 | 1DD | D04Q010 | 10.4.22 | 1DD11DP01 | 415V SWGR O/G MODULE # 1DD11FD | INLET MOTORIZED CONTROL VALVE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
70 | 1DD | D04Q010 | 10.4.22 | 1DD11EP01 | 415V SWGR O/G MODULE # 1DD11FE | MOTORIZED BUTTERFLY VALVE WITH INTEGRAL STARTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
71 | 1DD | D3HQ025 | 10.4.18 | 1DD11PP01 | 415V SWGR O/G MODULE # 1DD11RB | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP10-01, FP11-01, ZZ99- |  | EPD | EDN
72 | 1DD | D02L2.5 | 10.4.24 | 1DD11QP01 | 415V SWGR O/G MODULE # 1DD11RC | NSPBD FOR 1DDT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 26 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | FP19-L3, FP20-L3, FP21-02, FP22-02, ZZ99- |  | EPD | JHS
73 | 1DD | D02L2.5 | 10.4.24 | 1DD11RP01 | 415V SWGR O/G MODULE # 1DD11RD | SINGLE PHASE SUPPLY TO PTP SERV TRANSFORMER # 1DDT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FP16-02, FP01-03, FP02-02, ZZ99- |  | EPD | JHS
74 | 1DD | D03Q095 | 10.4.15 | 1DD11SP01 | 415V SWGR O/G MODULE # 1DD11RE | LDB I/C-A | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | FP19-L1, FP20-L1, FP21-01, FP22-01, FP06-R1, ZZ99- |  | EPD | PEM
75 | 1DD | D02C1.5 | 10.5.01 | 1DD11UC01 | 415V SWGR MOTOR MODULE # 1DD11RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
76 | 1DD | D03L2.5 | 10.4.26 | 1DD11UP01 | 415V SWGR MOTOR MODULE # 1DD11RG | HRSCC SCRAPPER MECHANISM-HRSCC1-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | PEM
77 | 1DD | D02C1.5 | 10.5.01 | 1DD11VC01 | 415V SWGR MOTOR MODULE # 1DD11RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP19-L3, FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
78 | 1DD | D03Q010 | 10.4.11 | 1DD11VP01 | 415V SWGR MOTOR MODULE # 1DD11RH | FILTER BACKWASH PUMPS-P3-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | FP19-L1, FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
79 | 1DD | D01Q400 | 10.4.04 | 1DD12BP01 | 415V SWGR O/G MODULE # 1DD12FB | FW & CLARIFIED WATER MCC # 0SC SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP19-L1, FP18-L1, FP17-L1, FP16-01, FP03-L2, ZZ99- |  | EPD | EPD
80 | 1DD | D01Q400 | 10.4.04 | 1DD12BP02 | 415V SWGR O/G MODULE # 1DD12FB | FW & CLARIFIED WATER MCC # 0SC SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP19-L1, FP18-L1, FP17-L1, FP16-01, FP03-L2, ZZ99- |  | EPD | EPD
81 | 1DD | D01Q400 | 10.4.04 | 1DD12BP03 | 415V SWGR O/G MODULE # 1DD12FB | FW & CLARIFIED WATER MCC # 0SC SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP19-L1, FP18-L1, FP17-L1, FP16-01, FP03-L2, ZZ99- |  | EPD | EPD
82 | 1DD | D01Q400 | 10.4.04 | 1DD12BP04 | 415V SWGR O/G MODULE # 1DD12FB | FW & CLARIFIED WATER MCC # 0SC SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | FP19-L1, FP18-L1, FP17-L1, FP16-01, FP03-L2, ZZ99- |  | EPD | EPD
83 | 1DD | D3HQ025 | 10.4.18 | 1DD12DP01 | 415V SWGR O/G MODULE # 1DD12FD | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | Hold |  | EPD | EPD
84 | 1DD | D02C1.5 | 10.5.01 | 1DD12GC01 | 415V SWGR MOTOR MODULE # 1DD12FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
85 | 1DD | D03L2.5 | 10.4.26 | 1DD12GP01 | 415V SWGR MOTOR MODULE # 1DD12FG | POLYMER DOSING PUMP-DP3-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
86 | 1DD | D02C1.5 | 10.5.01 | 1DD12HC01 | 415V SWGR MOTOR MODULE # 1DD12FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 61 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
87 | 1DD | D03L2.5 | 10.4.26 | 1DD12HP01 | 415V SWGR MOTOR MODULE # 1DD12FH | ALUM SOLUTION PREPARATION TANK-DT2-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 61 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
88 | 1DD | D04Q010 | 10.4.22 | 1DD12PP01 | 415V SWGR O/G MODULE # 1DD12RB | PTP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP12-01, FP13-01, FP14-01, ZZ99- |  | EPD | EDN
89 | 1DD | D3HQ025 | 10.4.18 | 1DD12QP01 | 415V SWGR O/G MODULE # 1DD12RC | PORTABLE SUMP PUMP A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
90 | 1DD | D03L2.5 | 10.4.26 | 1DD12WP01 | 415V SWGR O/G MODULE # 1DD12RI | AXIAL EXHAUST FAN-C2 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
91 | 1DD | D3HQ025 | 10.4.18 | 1DD13BP01 | 415V SWGR O/G MODULE # 1DD13FB | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
92 | 1DD | D04Q010 | 10.4.22 | 1DD13CP01 | 415V SWGR O/G MODULE # 1DD13FC | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | FP18-L1, FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, ZZ99- |  | EPD | PEM
93 | 1DD | D04Q010 | 10.4.22 | 1DD13PP01 | 415V SWGR O/G MODULE # 1DD13RB | PTP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | FP19-L1, FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP12-01, FP13-01, FP14-01, ZZ99- |  | EPD | EDN
94 | 1DD | D02C1.5 | 10.5.01 | 1DD14BC01 | 415V SWGR MOTOR MODULE # 1DD14FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
95 | 1DD | D03Q025 | 10.4.12 | 1DD14BP01 | 415V SWGR MOTOR MODULE # 1DD14FB | SLUDGE TRANSFER PUMP-P1-B | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
96 | 1DD | D03L2.5 | 10.4.26 | 1DD14DP01 | 415V SWGR O/G MODULE # 1DD14FD | AXIAL EXHAUST FAN-A2 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
97 | 1DD | D02C1.5 | 10.5.01 | 1DD14GC01 | 415V SWGR MOTOR MODULE # 1DD14FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
98 | 1DD | D03L2.5 | 10.4.26 | 1DD14GP01 | 415V SWGR MOTOR MODULE # 1DD14FG | POLYMER SOLUTION PREPARATION TANK-DT3-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | FP20-L3, FR03-02, ZZ99- |  | EPD | PEM
99 | 1DD | D02C1.5 | 10.5.01 | 1DD14PC01 | 415V SWGR MOTOR MODULE # 1DD14RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
100 | 1DD | D03L2.5 | 10.4.26 | 1DD14PP01 | 415V SWGR MOTOR MODULE # 1DD14RB | SODIUM HYPOCHLORITE DOSING PUMP-DP4-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
101 | 1DD | D03L2.5 | 10.4.26 | 1DD14SP01 | 415V SWGR O/G MODULE # 1DD14RE | AXIAL EXHAUST AIR FAN-K | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
102 | 1DD | D02Q010 | 10.4.06 | 1DD14TP01 | 415V SWGR O/G MODULE # 1DD14RF | SPLIT AC FOR CONTROL ROOM-F | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP10-01, FP11-01, ZZ99- |  | EPD | PEM
103 | 1DD | D02Q010 | 10.4.06 | 1DD14UP01 | 415V SWGR O/G MODULE # 1DD14RG | SPLIT AC FOR CONTROL ROOM-D | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 39 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, FP12-01, ZZ99- |  | EPD | PEM
104 | 1DD | D3HQ050 | 10.4.19 | 1DD15CP01 | 415V SWGR O/G MODULE # 1DD15FC | PTP FLOAT-CUM-BOOST CHARGER- B | 3.5C X 050 XLPE-Al FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, ZZ99- |  | EPD | PEM
105 | 1DD | D03L2.5 | 10.4.26 | 1DD15DP01 | 415V SWGR O/G MODULE # 1DD15FD | AXIAL EXHAUST AIR FAN-H | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 54 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
106 | 1DD | D03L2.5 | 10.4.26 | 1DD15EP01 | 415V SWGR O/G MODULE # 1DD15FE | AXIAL EXHAUST AIR FAN-F | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
107 | 1DD | D02Q010 | 10.4.06 | 1DD15FP01 | 415V SWGR O/G MODULE # 1DD15FF | SPLIT AC FOR CONTROL ROOM-B | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP20-L1, FP21-01, FP22-01, FP07-02, FP08-02, FP09-01, ZZ99- |  | EPD | PEM
108 | 1DD | D02C1.5 | 10.5.01 | 1DD15GC01 | 415V SWGR MOTOR MODULE # 1DD15FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
109 | 1DD | D03L2.5 | 10.4.26 | 1DD15GP01 | 415V SWGR MOTOR MODULE # 1DD15FG | LIME DOSING PUMP-DP1-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
110 | 1DD | D02C1.5 | 10.5.01 | 1DD15HC01 | 415V SWGR MOTOR MODULE # 1DD15FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
111 | 1DD | D03L2.5 | 10.4.26 | 1DD15HP01 | 415V SWGR MOTOR MODULE # 1DD15FH | WASTE WATER TRANSFER PUMP-P5-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
112 | 1DD | D04Q010 | 10.4.22 | 1DD15PP01 | 415V SWGR O/G MODULE # 1DD15RB | HRSCC RECIRCULATOR HRSCCS-B | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 57 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
113 | 1DD | D03L2.5 | 10.4.26 | 1DD15QP01 | 415V SWGR O/G MODULE # 1DD15RC | AXIAL EXHAUST AIR FAN-D | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 54 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
114 | 1DD | D03L2.5 | 10.4.26 | 1DD15RP01 | 415V SWGR O/G MODULE # 1DD15RD | AXIAL EXHAUST AIR FAN-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 59 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
115 | 1DD | D02L2.5 | 10.4.24 | 1DD15SP01 | 415V SWGR O/G MODULE # 1DD15RE | PROPELLOR FAN-B | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | FP20-L3, FR03-02, ZZ99- |  | EPD | PEM
116 | 1DD | D02C1.5 | 10.5.01 | 1DD15UC01 | 415V SWGR MOTOR MODULE # 1DD15RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | EPD
117 | 1DD | D03L2.5 | 10.4.26 | 1DD15UP01 | 415V SWGR MOTOR MODULE # 1DD15RG | ALUM DOSING PUMP-DP2-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FR02-02, ZZ99- |  | EPD | PEM
118 | 1DD | D02C1.5 | 10.5.01 | 1DD15VC01 | 415V SWGR MOTOR MODULE # 1DD15RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP20-L3, FR03-02, ZZ99- |  | EPD | EPD
119 | 1DD | D03Q010 | 10.4.11 | 1DD15VP01 | 415V SWGR MOTOR MODULE # 1DD15RH | BLOWER FOR SLUDGE PIT-B1-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | FP20-L1, FR03-01, ZZ99- |  | EPD | PEM
120 | 1DD | E04V0.5 | 10.7.02 | 1DD16AC01 | 415V SWGR I/C MODULE # 1DD16FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 31 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | FP20-R3, FP21-03, FP22-03, FP07-03, FP08-03, FP09-03, FP10-03, FP11-03, ZZ99- |  | EPD | EDN
121 | 1DD | D02L2.5 | 10.4.24 | 1DD16AC02 | 415V SWGR I/C MODULE # 1DD16FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 31 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | FP20-L3, FP21-02, FP22-02, FP07-02, FP08-02, FP09-02, FP10-02, FP11-02, ZZ99- |  | EPD | JHS
122 | 1DD | D02L2.5 | 10.4.24 | 1DD16AC03 | 415V SWGR I/C MODULE # 1DD16FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | FP20-L3, FP21-02, FP22-02, FP07-02, FP08-02, ZZ99- |  | EPD | JHS
123 | 1DD | D02C1.5 | 10.5.01 | 1DD16AC04 | 415V SWGR I/C MODULE # 1DD16FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 476 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | FP20-L3, FP19-L3, FP18-L3, FP17-L3, FP16-02, FP01-03, FR01-03, IP52-L7, IP51-L7, IR05-L3, IP50-L3, IP49-L3, IP48-L3, IP47-L3, IP46-L3, IP45-L3, IP44-L3, IP43-L3, IP42-L3, IP41-L3, IP40-L3, IP39-L3, IR04-L3, IP38-L4, IP37-L4, IP36-L4, IP34-L4, IP33-L7, IP32-L4, IP31-L4, IP30-L4, IP29-L4, IP28-L4, IP27-L7, IP26-L4, IP25-L4, IP24-L4, IP23-L4, IR38-L3, IP19-L3, IP18-L3, IP17-L3, IP16-L3, IP15-L3, IP14-R2, IR03-L3, IP02-L5, IP01-L5, TY19-L3, TY18-L3, TY17-L4, TY16-L4, LR03-03, MR03-03, MA02-03, MV35-L2, MV18-L2, MV19-02, ZZ99- |  | EPD | BPL
124 | 1DD | E04V0.5 | 10.7.02 | 1DD16AC05 | 415V SWGR I/C MODULE # 1DD16FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 31 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | FP20-R3, FP21-03, FP22-03, FP07-03, FP08-03, FP09-03, FP10-03, FP11-03, ZZ99- |  | EPD | EDN
1 | 1DE | D02C1.5 | 10.5.01 | 1DE01BC01 | 415V SWGR MOTOR MODULE # 1DE01FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
2 | 1DE | D03L2.5 | 10.4.26 | 1DE01BP01 | 415V SWGR MOTOR MODULE # 1DE01FB | ALUM DOSING PUMP-DP2-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
3 | 1DE | D02C1.5 | 10.5.01 | 1DE01CC01 | 415V SWGR MOTOR MODULE # 1DE01FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 51 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
4 | 1DE | D03L2.5 | 10.4.26 | 1DE01CP01 | 415V SWGR MOTOR MODULE # 1DE01FC | POLY DOSING PUMP-DP3 B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
5 | 1DE | D02C1.5 | 10.5.01 | 1DE01DC01 | 415V SWGR MOTOR MODULE # 1DE01FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
6 | 1DE | D03L2.5 | 10.4.26 | 1DE01DP01 | 415V SWGR MOTOR MODULE # 1DE01FD | MOTORIZED CONTROL VALVE-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
7 | 1DE | D02C1.5 | 10.5.01 | 1DE01FC01 | 415V SWGR MOTOR MODULE # 1DE01FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 91 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, ZZ99- |  | EPD | EPD
8 | 1DE | D02L2.5 | 10.4.24 | 1DE01FC02 | 415V SWGR MOTOR MODULE # 1DE01FF | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 91 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, ZZ99- |  | EPD | PEM
9 | 1DE | D03Q240 | 10.4.17 | 1DE01FP01 | 415V SWGR MOTOR MODULE # 1DE01FF | BOILER FILL PUMP | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (75kW) | XLPE-AL UNARMOURED | ET07-R1, ET06-R1, ET05-R1, ET04-R1, ET03-R1, ET02-R1, ET01-R1, PR01-02, IL09-02, IL08-02, ZZ99- |  | EPD | PEM
10 | 1DE | D02C1.5 | 10.5.01 | 1DE01PC01 | 415V SWGR MOTOR MODULE # 1DE01RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
11 | 1DE | D03L2.5 | 10.4.26 | 1DE01PP01 | 415V SWGR MOTOR MODULE # 1DE01RB | MOTORIZED CONTROL VALVE-C | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
12 | 1DE | D02C1.5 | 10.5.01 | 1DE01QC01 | 415V SWGR MOTOR MODULE # 1DE01RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 37 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ZZ99- |  | EPD | EPD
13 | 1DE | D03L2.5 | 10.4.26 | 1DE01QP01 | 415V SWGR MOTOR MODULE # 1DE01RC | LIME DOSING PUMP-DP1 B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (0.5kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ZZ99- |  | EPD | PEM
14 | 1DE | D02C1.5 | 10.5.01 | 1DE01RC01 | 415V SWGR MOTOR MODULE # 1DE01RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 470 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, IL07-03, IL06-03, IL05-03, IL04-03, IL03-03, IL02-03, IL01-03, IR37-03, IM31-03, IM30-03, IM29-03, IM28-03, IM27-03, IM26-03, IM25-03, IM24-03, IM23-03, IM22-03, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, IR24-02, ZZ99- |  | EPD | EPD
15 | 1DE | D03Q025 | 10.4.12 | 1DE01RP01 | 415V SWGR MOTOR MODULE # 1DE01RD | FUEL OIL AREA WASTE WATER TRANSFER PUMP-P4 A | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 470 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, IL07-03, IL06-03, IL05-03, IL04-03, IL03-03, IL02-03, IL01-03, IR37-03, IM31-03, IM30-03, IM29-03, IM28-03, IM27-03, IM26-03, IM25-03, IM24-03, IM23-03, IM22-03, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, IR24-02, ZZ99- |  | EPD | PEM
16 | 1DE | D03L2.5 | 10.4.26 | 1DE01SP01 | 415V SWGR O/G MODULE # 1DE01RE | SUPPLY AIR FAN FOR SWITCHGEAR ROOM-B (1.5 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
17 | 1DE | D02C1.5 | 10.5.01 | 1DE01UC01 | 415V SWGR MOTOR MODULE # 1DE01RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 61 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
18 | 1DE | D03Q010 | 10.4.11 | 1DE01UP01 | 415V SWGR MOTOR MODULE # 1DE01RG | CLEAR WATER TRANSFER PUMP-P7 A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | ET07-R1, ET06-R1, ET05-R1, ET04-R1, ET03-R1, ET09-01, ET37-01, ET38-01, ET39-01, ZZ99- |  | EPD | PEM
19 | 1DE | D02C1.5 | 10.5.01 | 1DE01VC01 | 415V SWGR MOTOR MODULE # 1DE01RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET36-02, ET40-02, ET34-02, ZZ99- |  | EPD | EPD
20 | 1DE | D03L2.5 | 10.4.26 | 1DE01VP01 | 415V SWGR MOTOR MODULE # 1DE01RH | LIME DOSING TANK- DT1 B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET36-02, ET40-02, ET34-02, ZZ99- |  | EPD | PEM
21 | 1DE | D02C1.5 | 10.5.01 | 1DE01WC01 | 415V SWGR MOTOR MODULE # 1DE01RI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
22 | 1DE | D03L2.5 | 10.4.26 | 1DE01WP01 | 415V SWGR MOTOR MODULE # 1DE01RI | ACID DOSING PUMP-DP4 B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
23 | 1DE | D03L2.5 | 10.4.26 | 1DE02DP01 | 415V SWGR O/G MODULE # 1DE02FD | SUPPLY AIR FAN FOR SWITCHGEAR ROOM-D (1.5kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
24 | 1DE | D03L2.5 | 10.4.26 | 1DE02EP01 | 415V SWGR O/G MODULE # 1DE02FE | SUPPLY AIR FAN FOR SWITCHGEAR ROOM-F (1.5kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
25 | 1DE | D02C1.5 | 10.5.01 | 1DE02QC01 | 415V SWGR MOTOR MODULE # 1DE02RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET27-02, ET28-02, ET31-02, ET32-02, ET33-02, ZZ99- |  | EPD | EPD
26 | 1DE | D03L2.5 | 10.4.26 | 1DE02QP01 | 415V SWGR MOTOR MODULE # 1DE02RC | ALUM DOSING TANK- DT2 B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET07-L4, ET27-02, ET28-02, ET31-02, ET32-02, ET33-02, ZZ99- |  | EPD | PEM
27 | 1DE | D02C1.5 | 10.5.01 | 1DE02RC01 | 415V SWGR MOTOR MODULE # 1DE02RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
28 | 1DE | D03L2.5 | 10.4.26 | 1DE02RP01 | 415V SWGR MOTOR MODULE # 1DE02RD | COMMON COLLECTION WATER TRANSFER PUMP-P3 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
29 | 1DE | D02Q010 | 10.4.06 | 1DE02TP01 | 415V SWGR O/G MODULE # 1DE02RF | SPLIT AC FOR CONTROL ROOM-B | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | ET07-R1, ET08-R1, ET10-R1, ET11-01, ET12-01, ET13-01, ET14-01, ZZ99- |  | EPD | PEM
30 | 1DE | D02C1.5 | 10.5.01 | 1DE02UC01 | 415V SWGR MOTOR MODULE # 1DE02RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
31 | 1DE | D03Q010 | 10.4.11 | 1DE02UP01 | 415V SWGR MOTOR MODULE # 1DE02RG | BOILER BLOW DOWN PUMP-P8 A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 55 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | ET07-R1, ET06-R1, ET05-R1, ET04-R1, ET03-R1, ET09-01, ET37-01, ET38-01, ET39-01, ZZ99- |  | EPD | PEM
32 | 1DE | D3HQ025 | 10.4.18 | 1DE02VP01 | 415V SWGR O/G MODULE # 1DE02RH | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
33 | 1DE | D03L2.5 | 10.4.26 | 1DE03BP01 | 415V SWGR O/G MODULE # 1DE03FB | EXHAUST AIR FAN FOR BATTERY ROOM-B (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET07-L4, ET08-L4, ET10-L4, ET11-02, ET12-02, ET13-02, ET14-02, ET17-02, ET18-02, ET19-02, ET20-02, ET21-02, ZZ99- |  | EPD | PEM
34 | 1DE | D02Q010 | 10.4.06 | 1DE03CP01 | 415V SWGR O/G MODULE # 1DE03FC | SPLIT AC FOR CONTROL ROOM-D | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | ET07-R1, ET08-R1, ET10-R1, ET11-01, ET12-01, ET13-01, ET14-01, ET17-01, ZZ99- |  | EPD | PEM
35 | 1DE | D02Q010 | 10.4.06 | 1DE03DP01 | 415V SWGR O/G MODULE # 1DE03FD | SPLIT AC FOR CONTROL ROOM-F | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | ET07-R1, ET08-R1, ET10-R1, ET11-01, ET12-01, ET13-01, ET14-01, ET15-01, ET16-01, ZZ99- |  | EPD | PEM
36 | 1DE | D03Q095 | 10.4.15 | 1DE03PP01 | 415V SWGR O/G MODULE # 1DE03RB | LDB I/C-B | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | ET07-R1, ET06-R1, ET05-R1, ET04-R1, ET03-R1, ET02-R1, ET22-01, ZZ99- |  | EPD | PEM
37 | 1DE | D02C1.5 | 10.5.01 | 1DE03QC01 | 415V SWGR MOTOR MODULE # 1DE03RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET27-02, ET28-02, ET31-02, ET32-02, ZZ99- |  | EPD | EPD
38 | 1DE | D03L2.5 | 10.4.26 | 1DE03QP01 | 415V SWGR MOTOR MODULE # 1DE03RC | PE DOSING TANK- DT3 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET07-L4, ET27-02, ET28-02, ET31-02, ET32-02, ZZ99- |  | EPD | PEM
39 | 1DE | D02C1.5 | 10.5.01 | 1DE03RC01 | 415V SWGR MOTOR MODULE # 1DE03RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
40 | 1DE | D03L2.5 | 10.4.26 | 1DE03RP01 | 415V SWGR MOTOR MODULE # 1DE03RD | SLUDGE TRANSFER PUMP-P6 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | ET07-L4, ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
41 | 1DE | D03L2.5 | 10.4.26 | 1DE03SP01 | 415V SWGR O/G MODULE # 1DE03RE | EXHAUST AIR FAN FOR BATTERY ROOM-D (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET07-L4, ET08-L4, ET10-L4, ET11-02, ET12-02, ET13-02, ET14-02, ET17-02, ET18-02, ET19-02, ET20-02, ET21-02, ZZ99- |  | EPD | PEM
42 | 1DE | D3HQ025 | 10.4.18 | 1DE04BP01 | 415V SWGR O/G MODULE # 1DE04FB | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | ET06-R1, ET07-R1, ET08-R1, ET10-R1, ET11-01, ET12-01, ET13-01, ET14-01, ET17-01, ET18-01, ET19-01 |  | EPD | EDN
43 | 1DE | D02C1.5 | 10.5.01 | 1DE04CC01 | 415V SWGR MOTOR MODULE # 1DE04FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
44 | 1DE | D03Q010 | 10.4.11 | 1DE04CP01 | 415V SWGR MOTOR MODULE # 1DE04FC | CLEAR WATER TRANSFER PUMP-P7 A-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
45 | 1DE | D02C1.5 | 10.5.01 | 1DE04DC01 | 415V SWGR MOTOR MODULE # 1DE04FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
46 | 1DE | D03Q010 | 10.4.11 | 1DE04DP01 | 415V SWGR MOTOR MODULE # 1DE04FD | WASTE WATER TRANSFER PUMP-P6 A-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
47 | 1DE | D02C1.5 | 10.5.01 | 1DE04EC01 | 415V SWGR MOTOR MODULE # 1DE04FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
48 | 1DE | D03Q010 | 10.4.11 | 1DE04EP01 | 415V SWGR MOTOR MODULE # 1DE04FE | CLEAR WATER TRANSFER PUMP-P9 A-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
49 | 1DE | D02C1.5 | 10.5.01 | 1DE04FC01 | 415V SWGR MOTOR MODULE # 1DE04FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
50 | 1DE | D03Q010 | 10.4.11 | 1DE04FP01 | 415V SWGR MOTOR MODULE # 1DE04FF | WASTE WATER TRANSFER PUMP-P8 A-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
51 | 1DE | D02C1.5 | 10.5.01 | 1DE05CC01 | 415V SWGR MOTOR MODULE # 1DE05FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, ZZ99- |  | EPD | EPD
52 | 1DE | D03Q025 | 10.4.12 | 1DE05CP01 | 415V SWGR MOTOR MODULE # 1DE05FC | DM MAKEUP PUMP-B | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | ET06-R1, ET05-R1, ET04-R1, ET03-R1, ET02-R1, ET01-R1, PR01-02, IL09-02, IL08-02, ZZ99- |  | EPD | PEM
53 | 1DE | D04Q010 | 10.4.22 | 1DE05FP01 | 415V SWGR O/G MODULE # 1DE05FF | ETP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | ET06-R1, ET07-R1, ET08-R1, ET10-R1, ET11-01, ET12-01, ET13-01, ET14-01, ET15-01, ZZ99- |  | EPD | EDN
54 | 1DE | D02C1.5 | 10.5.01 | 1DE05IC01 | 415V SWGR MOTOR MODULE # 1DE05FI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
55 | 1DE | D03L2.5 | 10.4.26 | 1DE05IP01 | 415V SWGR MOTOR MODULE # 1DE05FI | OIL SKIMMER- A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
56 | 1DE | D3HQ025 | 10.4.18 | 1DE05PP01 | 415V SWGR O/G MODULE # 1DE05RB | PORTABLE SUMP PUMP B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
57 | 1DE | D3HQ025 | 10.4.18 | 1DE05WP01 | 415V SWGR O/G MODULE # 1DE05RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
58 | 1DE | D04Q010 | 10.4.22 | 1DE06CP01 | 415V SWGR O/G MODULE # 1DE06FC | ETP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | ET06-R1, ET07-R1, ET08-R1, ET10-R1, ET11-01, ET12-01, ET13-01, ET14-01, ET15-01, ZZ99- |  | EPD | EDN
59 | 1DE | D02C1.5 | 10.5.01 | 1DE06EC01 | 415V SWGR MOTOR MODULE # 1DE06FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
60 | 1DE | D03Q010 | 10.4.11 | 1DE06EP01 | 415V SWGR MOTOR MODULE # 1DE06FE | AIR BLOWER FOR SLUDGE SUMP- B1 A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | ET06-R1, ET05-R1, ET04-R1, ET03-R1, ET09-01, ET37-01, ET38-01, ET39-01, ZZ99- |  | EPD | PEM
61 | 1DE | D04Q010 | 10.4.22 | 1DE06GP01 | 415V SWGR O/G MODULE # 1DE06FG | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | ET06-R1, ET27-01, ET28-01, ET29-01, ET30-01, ZZ99- |  | EPD | PEM
62 | 1DE | D02L2.5 | 10.4.24 | 1DE06UP01 | 415V SWGR O/G MODULE # 1DE06RG | SINGLE PHASE SUPPLY TO ETP TRANSFORMER # 1DET02 (10A) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ZZ99- |  | EPD | JHS
63 | 1DE | D02L2.5 | 10.4.24 | 1DE06VP01 | 415V SWGR O/G MODULE # 1DE06RH | NSPBD FOR 1DET02 (10A) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | ET06-L4, ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ZZ99- |  | EPD | JHS
64 | 1DE | E04V0.5 | 10.7.02 | 1DE07BC01 | 415V SWGR O/G MODULE # 1DE07FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 34 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
65 | 1DE | D01Q630 | 10.4.05 | 1DE07BP01 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 209 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L1, IL26-L1, IL27-L1, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L1, ZZ99- |  | EPD | EPD
66 | 1DE | D01Q630 | 10.4.05 | 1DE07BP02 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 209 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L1, IL26-L1, IL27-L1, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L1, ZZ99- |  | EPD | EPD
67 | 1DE | D01Q630 | 10.4.05 | 1DE07BP03 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 209 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L1, IL26-L1, IL27-L1, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L1, ZZ99- |  | EPD | EPD
68 | 1DE | D01Q630 | 10.4.05 | 1DE07BP04 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L1, IL26-L1, IL27-L1, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L2, ZZ99- |  | EPD | EPD
69 | 1DE | D01Q630 | 10.4.05 | 1DE07BP05 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L1, IL26-L1, IL27-L1, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L2, ZZ99- |  | EPD | EPD
70 | 1DE | D01Q630 | 10.4.05 | 1DE07BP06 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L1, IL26-L1, IL27-L1, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L2, ZZ99- |  | EPD | EPD
71 | 1DE | D01Q630 | 10.4.05 | 1DE07BP07 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L2, ZZ99- |  | EPD | EPD
72 | 1DE | D01Q630 | 10.4.05 | 1DE07BP08 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L2, ZZ99- |  | EPD | EPD
73 | 1DE | D01Q630 | 10.4.05 | 1DE07BP09 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-L2, IL29-L2, AR01-L2, AD01-L2, AD02-L2, AD03-L2, ZZ99- |  | EPD | EPD
74 | 1DE | D01Q630 | 10.4.05 | 1DE07BP10 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 209 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, ZZ99- |  | EPD | EPD
75 | 1DE | D01Q630 | 10.4.05 | 1DE07BP11 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 209 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, ZZ99- |  | EPD | EPD
76 | 1DE | D01Q630 | 10.4.05 | 1DE07BP12 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 209 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, ZZ99- |  | EPD | EPD
77 | 1DE | D01Q400 | 10.4.04 | 1DE07BP13 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-R1, ET07-R1, ET08-R1, ET10-R1, PR02-L1, IL10-R1, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R2, ZZ99- |  | EPD | EPD
78 | 1DE | D01Q400 | 10.4.04 | 1DE07BP14 | 415V SWGR O/G MODULE # 1DE07FB | ADMIN BUILDING MCC # 0SC SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 209 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET06-R1, ET07-R1, ET08-R1, ET10-R1, PR02-L1, IL10-R2, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R2, IL29-R2, AR01-R2, AD01-R2, AD02-R2, AD03-R2, ZZ99- |  | EPD | EPD
79 | 1DE | E04V0.5 | 10.7.02 | 1DE08BC01 | 415V SWGR I/C MODULE # 1DE08FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 37 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | ET05-R4, ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
80 | 1DE | D02L2.5 | 10.4.24 | 1DE08BC02 | 415V SWGR I/C MODULE # 1DE08FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 39 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ET26-02, ZZ99- |  | EPD | JHS
81 | 1DE | D02L2.5 | 10.4.24 | 1DE08BC03 | 415V SWGR I/C MODULE # 1DE08FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 39 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ET26-02, ZZ99- |  | EPD | JHS
82 | 1DE | D02C1.5 | 10.5.01 | 1DE08BC04 | 415V SWGR I/C MODULE # 1DE08FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 496 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, IL07-03, IL06-03, IL05-03, IL04-03, IL03-03, IL02-03, IL01-03, IR37-03, IM31-03, IM30-03, IM29-03, IM28-03, IM27-03, IM26-03, IM25-03, IM24-03, IM23-03, IM22-03, IM21-L5, IM20-L5, IM19-L5, IM18-L5, IM17-L5, IM16-L5, IM15-L5, IM14-L5, IM13-L5, IM12-L7, IM11-L7, IM10-04, IM09-05, IM07-05, IM05-05, IM04-02, IR18-02, CC03-03, CC62-03, CC63-03, CC64-03, CC65-03, CC66-03, CC67-03, CC34-02, CC93-02, CC84-03, CC86-03, CC88-03, CC92-03, LR05-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV15-02, ZZ99- |  | EPD | BPL
83 | 1DE | E04V0.5 | 10.7.02 | 1DE08BC05 | 415V SWGR I/C MODULE # 1DE08FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 37 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | ET05-R4, ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
84 | 1DE | E04V0.5 | 10.7.02 | 1DE10BC01 | 415V SWGR B/C MODULE # 1DE10FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 37 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | ET05-R4, ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
85 | 1DE | E04V0.5 | 10.7.02 | 1DE10BC02 | 415V SWGR B/C MODULE # 1DE10FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 37 | [5 empty] | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | ET05-R4, ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
86 | 1DE | E04V0.5 | 10.7.02 | 1DE11BC01 | 415V SWGR I/C MODULE # 1DE11FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 37 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | ET05-R4, ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
87 | 1DE | D02L2.5 | 10.4.24 | 1DE11BC02 | 415V SWGR I/C MODULE # 1DE11FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ZZ99- |  | EPD | JHS
88 | 1DE | D02L2.5 | 10.4.24 | 1DE11BC03 | 415V SWGR I/C MODULE # 1DE11FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ZZ99- |  | EPD | JHS
89 | 1DE | D02C1.5 | 10.5.01 | 1DE11BC04 | 415V SWGR I/C MODULE # 1DE11FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 497 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | ET05-L4, ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, IL07-03, IL06-03, IL05-03, IL04-03, IL03-03, IL02-03, IL01-03, IR37-03, IM31-03, IM30-03, IM29-03, IM28-03, IM27-03, IM26-03, IM25-03, IM24-03, IM23-03, IM22-03, IM21-L5, IM20-L5, IM19-L5, IM18-L5, IM17-L5, IM16-L5, IM15-L5, IM14-L5, IM13-L5, IM12-L7, IM11-L7, IM10-04, IM09-05, IM07-05, IM05-05, IM04-02, IR18-02, CC03-03, CC02-03, CC72-03, CC01-03, LR08-03, LV73-03, LV39-L4, LV38-L4, LV37-L4, LV36-L4, LV50-02, LV30-L4, LV31-L4, LV61-05, LV19-L4, LV18-L4, LV71-03, MR02-03, MA01-03, MV18-L2, MV19-02, ZZ99- |  | EPD | BPL
90 | 1DE | E04V0.5 | 10.7.02 | 1DE11BC05 | 415V SWGR I/C MODULE # 1DE11FB | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 37 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | ET05-R4, ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
91 | 1DE | E04V0.5 | 10.7.02 | 1DE12AC01 | 415V SWGR O/G MODULE # 1DE12FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 37 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | ET05-R4, ET06-R4, ET07-R4, ET08-R4, ET10-R4, ET11-03, ET12-03, ET13-03, ET14-03, ET17-03, ET18-03, ZZ99- |  | EPD | EDN
92 | 1DE | D01Q630 | 10.4.05 | 1DE12AP01 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
93 | 1DE | D01Q630 | 10.4.05 | 1DE12AP02 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
94 | 1DE | D01Q630 | 10.4.05 | 1DE12AP03 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L1, ET07-L1, ET08-L1, ET10-L1, PR02-R1, IL10-L1, IL11-L1, IL12-L1, IL13-L1, IL14-L1, IL15-L1, IL16-L1, IL17-L1, IL18-L1, IL19-L1, IL20-L1, IL21-L1, IL22-L1, IL23-L1, IL24-L1, IL25-L2, IL26-L2, IL27-L2, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
95 | 1DE | D01Q630 | 10.4.05 | 1DE12AP04 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R1, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
96 | 1DE | D01Q630 | 10.4.05 | 1DE12AP05 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R1, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
97 | 1DE | D01Q630 | 10.4.05 | 1DE12AP06 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R1, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
98 | 1DE | D01Q630 | 10.4.05 | 1DE12AP07 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R1, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
99 | 1DE | D01Q630 | 10.4.05 | 1DE12AP08 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R1, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
100 | 1DE | D01Q630 | 10.4.05 | 1DE12AP09 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R1, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R1, IL29-R1, AR01-R1, AD01-R1, AD02-R1, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
101 | 1DE | D01Q630 | 10.4.05 | 1DE12AP10 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 218 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R2, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R2, IL29-R2, AR01-R2, AD01-R2, AD02-R2, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
102 | 1DE | D01Q630 | 10.4.05 | 1DE12AP11 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 218 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R2, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R2, IL29-R2, AR01-R2, AD01-R2, AD02-R2, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
103 | 1DE | D01Q630 | 10.4.05 | 1DE12AP12 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 218 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R2, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R2, IL29-R2, AR01-R2, AD01-R2, AD02-R2, AD03-R1, AD04-R1, ZZ99- |  | EPD | EPD
104 | 1DE | D01Q400 | 10.4.04 | 1DE12AP13 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 218 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R2, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R2, IL29-R2, AR01-R2, AD01-R2, AD02-R2, AD03-R2, AD04-R1, ZZ99- |  | EPD | EPD
105 | 1DE | D01Q400 | 10.4.04 | 1DE12AP14 | 415V SWGR O/G MODULE # 1DE12FA | ADMIN BUILDING MCC # 0SC SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 218 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, PR02-L1, IL10-R2, IL11-R1, IL12-R1, IL13-R1, IL14-R1, IL15-R1, IL16-R1, IL17-R1, IL18-R1, IL19-R1, IL20-R1, IL21-R1, IL22-R1, IL23-R1, IL24-R1, IL25-R1, IL26-R1, IL27-R1, IL28-R2, IL29-R2, AR01-R2, AD01-R2, AD02-R2, AD03-R2, AD04-R1, ZZ99- |  | EPD | EPD
106 | 1DE | D02C1.5 | 10.5.01 | 1DE14BC01 | 415V SWGR MOTOR MODULE # 1DE14FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
107 | 1DE | D03Q010 | 10.4.11 | 1DE14BP01 | 415V SWGR MOTOR MODULE # 1DE14FB | CLEAR WATER TRANSFER PUMP-P7 B-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
108 | 1DE | D02C1.5 | 10.5.01 | 1DE14DC01 | 415V SWGR MOTOR MODULE # 1DE14FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET36-02, ET40-02, ET33-02, ET32-02, ET31-02, ZZ99- |  | EPD | EPD
109 | 1DE | D03L2.5 | 10.4.26 | 1DE14DP01 | 415V SWGR MOTOR MODULE # 1DE14FD | PE DOSING TANK- DT3 B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET04-L4, ET36-02, ET40-02, ET33-02, ET32-02, ET31-02, ZZ99- |  | EPD | PEM
110 | 1DE | D02C1.5 | 10.5.01 | 1DE14EC01 | 415V SWGR MOTOR MODULE # 1DE14FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 77 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, ZZ99- |  | EPD | EPD
111 | 1DE | D03Q025 | 10.4.12 | 1DE14EP01 | 415V SWGR MOTOR MODULE # 1DE14FE | DM MAKEUP PUMP-A | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | ET04-L1, ET03-L1, ET02-L1, ET01-L1, PR01-02, IL09-02, IL08-02, ZZ99- |  | EPD | PEM
112 | 1DE | D03L2.5 | 10.4.26 | 1DE14FP01 | 415V SWGR O/G MODULE # 1DE14FF | EXHAUST AIR FAN FOR BATTERY ROOM-A (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET04-L4, ET05-L4, ET06-L4, ET07-L4, ET08-L4, ET10-L4, ET11-02, ET12-02, ET13-02, ET14-02, ET17-02, ET18-02, ET19-02, ET20-02, ET21-02, ZZ99- |  | EPD | PEM
113 | 1DE | D02C1.5 | 10.5.01 | 1DE14PC01 | 415V SWGR MOTOR MODULE # 1DE14RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
114 | 1DE | D03Q010 | 10.4.11 | 1DE14PP01 | 415V SWGR MOTOR MODULE # 1DE14RB | WASTE WATER TRANSFER PUMP-P6 B-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
115 | 1DE | D04Q010 | 10.4.22 | 1DE14RP01 | 415V SWGR O/G MODULE # 1DE14RD | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | ET04-L1, ET05-L2, ET06-L2, ET27-01, ET28-01, ET29-01, ET30-01, ZZ99- |  | EPD | PEM
116 | 1DE | D3HQ025 | 10.4.18 | 1DE14UP01 | 415V SWGR O/G MODULE # 1DE14RG | PORTABLE SUMP PUMP A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
117 | 1DE | D03L2.5 | 10.4.26 | 1DE14VP01 | 415V SWGR O/G MODULE # 1DE14RH | SUPPLY AIR FAN FOR SWITCHGEAR ROOM-A (1.5kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
118 | 1DE | D3HQ025 | 10.4.18 | 1DE15BP01 | 415V SWGR O/G MODULE # 1DE15FB | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 44 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | ET04-L1, ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, ET11-01, ET12-01, ET13-01, ET14-01, ET17-01, ET18-01, ET19-01 |  | EPD | EDN
119 | 1DE | D02C1.5 | 10.5.01 | 1DE15CC01 | 415V SWGR MOTOR MODULE # 1DE15FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 32 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
120 | 1DE | D03L2.5 | 10.4.26 | 1DE15CP01 | 415V SWGR MOTOR MODULE # 1DE15FC | FMFT | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
121 | 1DE | D02L2.5 | 10.4.24 | 1DE15DP01 | 415V SWGR O/G MODULE # 1DE15FD | REPEATER PANEL-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
122 | 1DE | D03L2.5 | 10.4.26 | 1DE15FP01 | 415V SWGR O/G MODULE # 1DE15FF | SUPPLY AIR FAN FOR SWITCHGEAR ROOM-C (1.5 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
123 | 1DE | D03Q095 | 10.4.15 | 1DE15IP01 | 415V SWGR O/G MODULE # 1DE15FI | LDB I/C-A | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 23 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | ET04-L1, ET03-L1, ET02-L1, ET22-01, ZZ99- |  | EPD | PEM
124 | 1DE | D02C1.5 | 10.5.01 | 1DE15PC01 | 415V SWGR MOTOR MODULE # 1DE15RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
125 | 1DE | D03Q010 | 10.4.11 | 1DE15PP01 | 415V SWGR MOTOR MODULE # 1DE15RB | CLEAR WATER TRANSFER PUMP-P9 B-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
126 | 1DE | D02C1.5 | 10.5.01 | 1DE15RC01 | 415V SWGR MOTOR MODULE # 1DE15RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 22 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET36-02, ET40-02, ET33-02, ZZ99- |  | EPD | EPD
127 | 1DE | D03L2.5 | 10.4.26 | 1DE15RP01 | 415V SWGR MOTOR MODULE # 1DE15RD | ALUM DOSING TANK- DT2 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 22 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET04-L4, ET36-02, ET40-02, ET33-02, ZZ99- |  | EPD | PEM
128 | 1DE | D03L2.5 | 10.4.26 | 1DE15TP01 | 415V SWGR O/G MODULE # 1DE15RF | SUPPLY AIR FAN FOR SWITCHGEAR ROOM-E (1.5 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
129 | 1DE | D3HQ025 | 10.4.18 | 1DE15WP01 | 415V SWGR O/G MODULE # 1DE15RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
130 | 1DE | D02L2.5 | 10.4.24 | 1DE16BP01 | 415V SWGR O/G MODULE # 1DE16FB | SINGLE PHASE SUPPLY TO ETP TRANSFORMER # 1DET01 (10A) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | ET04-L4, ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ET26-02, ZZ99- |  | EPD | JHS
131 | 1DE | D02C1.5 | 10.5.01 | 1DE16CC01 | 415V SWGR MOTOR MODULE # 1DE16FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET36-02, ET40-02, ET34-02, ET35-02, ZZ99- |  | EPD | EPD
132 | 1DE | D03L2.5 | 10.4.26 | 1DE16CP01 | 415V SWGR MOTOR MODULE # 1DE16FC | LIME DOSING TANK- DT1 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET04-L4, ET36-02, ET40-02, ET34-02, ET35-02, ZZ99- |  | EPD | PEM
133 | 1DE | D02C1.5 | 10.5.01 | 1DE16DC01 | 415V SWGR MOTOR MODULE # 1DE16FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
134 | 1DE | D03Q010 | 10.4.11 | 1DE16DP01 | 415V SWGR MOTOR MODULE # 1DE16FD | AIR BLOWER FOR SLUDGE SUMP- B1 B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | ET04-L1, ET03-L1, ET09-01, ET37-01, ET38-01, ET39-01, ZZ99- |  | EPD | PEM
135 | 1DE | D02C1.5 | 10.5.01 | 1DE16PC01 | 415V SWGR MOTOR MODULE # 1DE16RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
136 | 1DE | D03Q010 | 10.4.11 | 1DE16PP01 | 415V SWGR MOTOR MODULE # 1DE16RB | WASTE WATER TRANSFER PUMP-P8 B-STP | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
137 | 1DE | D02C1.5 | 10.5.01 | 1DE16SC01 | 415V SWGR MOTOR MODULE # 1DE16RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
138 | 1DE | D03Q010 | 10.4.11 | 1DE16SP01 | 415V SWGR MOTOR MODULE # 1DE16RE | SLUDGE TRANSFER PUMP-P6 B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | ET04-L1, ET03-L1, ET09-01, ET37-01, ET38-01, ET39-01, ZZ99- |  | EPD | PEM
139 | 1DE | D04Q010 | 10.4.22 | 1DE17BP01 | 415V SWGR O/G MODULE # 1DE17FB | ETP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | ET04-L1, ET05-L2, ET06-L2, ET07-L2, ET08-L2, ET10-L2, ET11-01, ET12-01, ET13-01, ET14-01, ET15-01, ET16-01, ZZ99- |  | EPD | EDN
140 | 1DE | D02C1.5 | 10.5.01 | 1DE17CC01 | 415V SWGR MOTOR MODULE # 1DE17FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 44 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
141 | 1DE | D03L2.5 | 10.4.26 | 1DE17CP01 | 415V SWGR MOTOR MODULE # 1DE17FC | ACID DOSING PUMP-DP4 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 44 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
142 | 1DE | D02C1.5 | 10.5.01 | 1DE17DC01 | 415V SWGR MOTOR MODULE # 1DE17FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ZZ99- |  | EPD | EPD
143 | 1DE | D03L2.5 | 10.4.26 | 1DE17DP01 | 415V SWGR MOTOR MODULE # 1DE17FD | LIME DOSING PUMP-DP1 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (0.5kW) | XLPE-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ZZ99- |  | EPD | PEM
144 | 1DE | D03L2.5 | 10.4.26 | 1DE17FP01 | 415V SWGR O/G MODULE # 1DE17FF | EXHAUST AIR FAN FOR BATTERY ROOM-C (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET04-L4, ET05-L4, ET06-L4, ET07-L4, ET08-L4, ET10-L4, ET11-02, ET12-02, ET13-02, ET14-02, ET17-02, ET18-02, ET19-02, ET20-02, ET21-02, ZZ99- |  | EPD | PEM
145 | 1DE | D02C1.5 | 10.5.01 | 1DE17HC01 | 415V SWGR MOTOR MODULE # 1DE17FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
146 | 1DE | D03Q010 | 10.4.11 | 1DE17HP01 | 415V SWGR MOTOR MODULE # 1DE17FH | BOILER BLOW DOWN PUMP-P8 B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | ET04-L1, ET03-L1, ET09-01, ET37-01, ET38-01, ET39-01, ZZ99- |  | EPD | PEM
147 | 1DE | D02C1.5 | 10.5.01 | 1DE17IC01 | 415V SWGR MOTOR MODULE # 1DE17FI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 77 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, ZZ99- |  | EPD | EPD
148 | 1DE | D03Q025 | 10.4.12 | 1DE17IP01 | 415V SWGR MOTOR MODULE # 1DE17FI | DM MAKEUP PUMP-C | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | ET04-L1, ET03-L1, ET02-L1, ET01-L1, PR01-02, IL09-02, IL08-02, ZZ99- |  | EPD | PEM
149 | 1DE | D02C1.5 | 10.5.01 | 1DE17RC01 | 415V SWGR MOTOR MODULE # 1DE17RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 42 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
150 | 1DE | D03L2.5 | 10.4.26 | 1DE17RP01 | 415V SWGR MOTOR MODULE # 1DE17RD | POLY DOSING PUMP-DP3 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
151 | 1DE | D02C1.5 | 10.5.01 | 1DE17SC01 | 415V SWGR MOTOR MODULE # 1DE17RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 34 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
152 | 1DE | D03L2.5 | 10.4.26 | 1DE17SP01 | 415V SWGR MOTOR MODULE # 1DE17RE | COMMON COLLECTION WATER TRANSFER PUMP-P3 B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 34 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | ET04-L4, ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
153 | 1DE | D02Q010 | 10.4.06 | 1DE17TP01 | 415V SWGR O/G MODULE # 1DE17RG | SPLIT AC FOR CONTROL ROOM-E | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | ET04-L1, ET05-L1, ET06-L2, ET07-L2, ET08-L2, ET10-L2, ET11-01, ET12-01, ET13-01, ET14-01, ET17-01, ET18-01, ET19-01, ET20-01, ZZ99- |  | EPD | PEM
154 | 1DE | D3HQ025 | 10.4.18 | 1DE17VP01 | 415V SWGR O/G MODULE # 1DE17RH | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
155 | 1DE | D04Q010 | 10.4.22 | 1DE18BP01 | 415V SWGR O/G MODULE # 1DE18FB | ETP AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | ET03-L1, ET04-L1, ET05-L2, ET06-L2, ET07-L2, ET08-L2, ET10-L2, ET11-01, ET12-01, ET13-01, ET14-01, ET15-01, ET16-01, ZZ99- |  | EPD | EDN
156 | 1DE | D02C1.5 | 10.5.01 | 1DE18EC01 | 415V SWGR MOTOR MODULE # 1DE18FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 457 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, IL07-03, IL06-03, IL05-03, IL04-03, IL03-03, IL02-03, IL01-03, IR37-03, IM31-03, IM30-03, IM29-03, IM28-03, IM27-03, IM26-03, IM25-03, IM24-03, IM23-03, IM22-03, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, IR24-02, ZZ99- |  | EPD | EPD
157 | 1DE | D03Q025 | 10.4.12 | 1DE18EP01 | 415V SWGR MOTOR MODULE # 1DE18FE | FUEL OIL AREA WASTE WATER TRANSFER PUMP- P4 B | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 457 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | ET03-L4, ET02-L4, ET01-L4, PR01-03, IL09-03, IL08-03, IL07-03, IL06-03, IL05-03, IL04-03, IL03-03, IL02-03, IL01-03, IR37-03, IM31-03, IM30-03, IM29-03, IM28-03, IM27-03, IM26-03, IM25-03, IM24-03, IM23-03, IM22-03, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, IR23-02, IM54-02, IM55-02, IM56-02, IR24-02, ZZ99- |  | EPD | PEM
158 | 1DE | D02Q010 | 10.4.06 | 1DE18GP01 | 415V SWGR O/G MODULE # 1DE18FG | SPLIT AC FOR CONTROL ROOM-C | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | ET03-L1, ET04-L1, ET05-L2, ET06-L2, ET07-L2, ET08-L2, ET10-L2, ET11-01, ET12-01, ET13-01, ET14-01, ET17-01, ET18-01, ZZ99- |  | EPD | PEM
159 | 1DE | D02C1.5 | 10.5.01 | 1DE18HC01 | 415V SWGR MOTOR MODULE # 1DE18FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
160 | 1DE | D03Q010 | 10.4.11 | 1DE18HP01 | 415V SWGR MOTOR MODULE # 1DE18FH | CLEAR WATER TRANSFER PUMP-P7 B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | ET03-L1, ET09-01, ET37-01, ET38-01, ET39-01, ZZ99- |  | EPD | PEM
161 | 1DE | D02C1.5 | 10.5.01 | 1DE18IC01 | 415V SWGR MOTOR MODULE # 1DE18FI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
162 | 1DE | D03L2.5 | 10.4.26 | 1DE18IP01 | 415V SWGR MOTOR MODULE # 1DE18FI | MOTORIZED CONTROL VALVE-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
163 | 1DE | D02L2.5 | 10.4.24 | 1DE18QP01 | 415V SWGR O/G MODULE # 1DE18RC | NSPBD FOR 1DET01 (10A) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | ET03-L4, ET02-L4, ET01-L4, ET23-02, ET24-02, ET25-02, ET26-02 |  | EPD | JHS
164 | 1DE | D02C1.5 | 10.5.01 | 1DE18RC01 | 415V SWGR MOTOR MODULE # 1DE18RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | EPD
165 | 1DE | D03L2.5 | 10.4.26 | 1DE18RP01 | 415V SWGR MOTOR MODULE # 1DE18RD | ALUM DOSING PUMP-DP2 A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | ET03-L4, ET09-02, ET37-02, ET38-02, ET39-02, ZZ99- |  | EPD | PEM
166 | 1DE | D02C1.5 | 10.5.01 | 1DE18SC01 | 415V SWGR MOTOR MODULE # 1DE18RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
167 | 1DE | D03L2.5 | 10.4.26 | 1DE18SP01 | 415V SWGR MOTOR MODULE # 1DE18RE | OIL SKIMMER- B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
168 | 1DE | D02Q010 | 10.4.06 | 1DE18TP01 | 415V SWGR O/G MODULE # 1DE18RF | SPLIT AC FOR CONTROL ROOM-A | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 54 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | ET03-L1, ET04-L1, ET05-L2, ET06-L2, ET07-L2, ET08-L2, ET10-L2, ET11-01, ET12-01, ET13-01, ET14-01, ET17-01, ET18-01, ET19-01, ZZ99- |  | EPD | PEM
1 | 1DG | D03Q095 | 10.4.15 | 1DG01BP01 | 415V SWGR O/G MODULE # 1DG01FB | DG AUX PANEL | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 155 | [5 empty] | POWER SUPPLY (100A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L1, LV72-02, LR11-L2, TY24-L2, TY23-L2, TY22-L2, TY21-L2, TY20-L2, IP01-R3, IP02-R3, IR02-02, IP07-02, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
2 | 1DG | D02C1.5 | 10.5.01 | 1DG01CC01 | 415V SWGR MOTOR MODULE # 1DG01FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 232 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IR13-02, IC30-03, IC31-03, ZZ99- |  | EPD | EPD
3 | 1DG | D03Q025 | 10.4.12 | 1DG01CP01 | 415V SWGR MOTOR MODULE # 1DG01FC | MILL - A LUB OIL PUMP - 2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 228 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-R1, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IC07-R1, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IR13-02, IC30-02, IC31-01, ZZ99- |  | EPD | RPT
4 | 1DG | D03L2.5 | 10.4.26 | 1DG01DP01 | 415V SWGR O/G MODULE # 1DG01FD | SUPPLY FAN | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, ZZ99- |  | EPD | PEM
5 | 1DG | D02C1.5 | 10.5.01 | 1DG01PC01 | 415V SWGR MOTOR MODULE # 1DG01RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 108 | 102 | 03.03.20 | DR1150_17PA011786 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV59-02, TR50-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, ZZ99- |  | EPD | EPD
6 | 1DG | D03Q010 | 10.4.11 | 1DG01PP01 | 415V SWGR MOTOR MODULE # 1DG01RB | BFP-A AOP (LAC10AP002) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 107 | 130 | 03.03.20 | 20 |  |  | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV36-R1, LV35-R1, LV55-02, LV56-02, LV57-01, LV58-01, LV59-01, TR50-01, MR15-01, TR02-01, TG85-01, TG86-02, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, ZZ99- |  | EPD | HYD
7 | 1DG | D02C1.5 | 10.5.01 | 1DG01QC01 | 415V SWGR MOTOR MODULE # 1DG01RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 72 | 106 | 03.03.20 | DR1150_17PA011786 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV59-02, TR50-02, TG66-02, TR18-02, TG64-02, ZZ99- |  | EPD | EPD
8 | 1DG | D03L2.5 | 10.4.26 | 1DG01QP01 | 415V SWGR MOTOR MODULE # 1DG01RC | OIL VAPOUR EXTRACTOR - 2 (MAV82AN002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 72 | 117 | 04.03.20 | DR2450_N-466 |  |  | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV59-02, TR50-02, TG66-02, TR18-02, TG64-02, ZZ99- |  | EPD | PEM
9 | 1DG | D02C1.5 | 10.5.01 | 1DG01RC01 | 415V SWGR MOTOR MODULE # 1DG01RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 361 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | EPD
10 | 1DG | D03Q010 | 10.4.11 | 1DG01RP01 | 415V SWGR MOTOR MODULE # 1DG01RD | ID FAN - A LUB OIL PUMP - 2 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 361 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | RPT
11 | 1DG | D02C1.5 | 10.5.01 | 1DG01SC01 | 415V SWGR MOTOR MODULE # 1DG01RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 171 | 197 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC19-L2, IC20-02, IC21-02, ZZ99- |  | EPD | EPD
12 | 1DG | D03Q010 | 10.4.11 | 1DG01SP01 | 415V SWGR MOTOR MODULE # 1DG01RE | FD FAN - A LUB OIL PUMP - 2 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 171 | 187 | 03.03.20 | 0 |  |  | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC19-L2, IC20-02, IC21-02, ZZ99- |  | EPD | RPT
13 | 1DG | D02C1.5 | 10.5.01 | 1DG01TC01 | 415V SWGR MOTOR MODULE # 1DG01RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 258 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IR15-02, IC41-03, IC42-03, ZZ99- |  | EPD | EPD
14 | 1DG | D03Q025 | 10.4.12 | 1DG01TP01 | 415V SWGR MOTOR MODULE # 1DG01RF | MILL - C LUB OIL PUMP - 2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 254 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-R1, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IC07-R1, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IC33-02, IC34-02, IC38-02, IC39-02, IC40-02, IR15-02, IC41-02, IC42-01, ZZ99- |  | EPD | RPT
15 | 1DG | D01Q400 | 10.4.04 | 1DG02BP01 | 415V SWGR O/G MODULE # 1DG02FB | 220V FCBC-1A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 37 | 38 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-R1, LV46-01, LV47-01, LV48-01, LV49-01, LV07-L1, ZZ99- |  | EPD | PEM
16 | 1DG | D01Q400 | 10.4.04 | 1DG02BP02 | 415V SWGR O/G MODULE # 1DG02FB | 220V FCBC-1A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 37 | 38 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-R1, LV46-01, LV47-01, LV48-01, LV49-01, LV07-L1, ZZ99- |  | EPD | PEM
17 | 1DG | D01Q400 | 10.4.04 | 1DG02BP03 | 415V SWGR O/G MODULE # 1DG02FB | 220V FCBC-1A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 37 | 38 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-R1, LV46-01, LV47-01, LV48-01, LV49-01, LV07-L1, ZZ99- |  | EPD | PEM
18 | 1DG | D02C1.5 | 10.5.01 | 1DG02EC01 | 415V SWGR MOTOR MODULE # 1DG02FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 79 | 110 | 03.03.20 | DR1150_17PA011786 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, ZZ99- |  | EPD | EPD
19 | 1DG | D02L2.5 | 10.4.24 | 1DG02EC02 | 415V SWGR MOTOR MODULE # 1DG02FE | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | 118 | 16.01.20 | DR1095_0045 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, ZZ99- |  | EPD | PEM
20 | 1DG | D03Q095 | 10.4.15 | 1DG02EP01 | 415V SWGR MOTOR MODULE # 1DG02FE | AUXILARY OIL PUMP - 2 (MAV23AP001) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 75 | 112 | 4.03.20 | DR0822_0005 |  |  | POWER SUPPLY (75kW) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV36-R1, LV35-R1, LV55-02, LV31-L1, LV61-01, LV62-01, LV63-02, LV64-02, TR48-02, TG71-01, TG72-01, TR16-01, TG73-01, ZZ99- |  | EPD | PEM
21 | 1DG | D03Q240 | 10.4.17 | 1DG02PP01 | 415V SWGR O/G MODULE # 1DG02RB | BOILER VALVE ACDB # 1HB | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | LV38-R1, LV41-01, LV28-R1, ZZ99- |  | EPD | EPD
22 | 1DG | D02C1.5 | 10.5.01 | 1DG02RC01 | 415V SWGR MOTOR MODULE # 1DG02RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 238 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IR34-02, IM97-02, IM98-02, IM99-02, ZZ99- |  | EPD | EPD
23 | 1DG | D03Q025 | 10.4.12 | 1DG02RP01 | 415V SWGR MOTOR MODULE # 1DG02RD | MILL - E LUB OIL PUMP - 2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 239 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-R1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM64-02, IM65-02, IM66-02, IM67-02, IM68-02, IM72-02, IM75-02, IR28-02, IM76-02, IM77-02, IM78-02, IR32-02, IM79-02, IM80-02, IM85-02, IM86-02, IM87-02, IR34-02, IM97-02, IM98-02, IM99-01, ZZ99- |  | EPD | RPT
24 | 1DG | D03L2.5 | 10.4.26 | 1DG02SP01 | 415V SWGR O/G MODULE # 1DG02RE | EXHAUST FAN | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV43-03, LV44-03, LV45-03, TR52-03, ZZ99- |  | EPD | PEM
25 | 1DG | D03Q025 | 10.4.12 | 1DG02TP01 | 415V SWGR O/G MODULE # 1DG02RF | FEEDER FOR BOILER PASSENGER CUM GOODS ELEVATOR | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 134 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | LV38-L2, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, BR15-01, ZZ99- |  | EPD | PEM
26 | 1DG | D3HQ185 | 10.4.21 | 1DG03BP01 | 415V SWGR O/G MODULE # 1DG03FB | UPS FEEDER | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 49 | 47 | 22.12.2019 | DR2687-1 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-L2, LV39-L1, LV73-01, LR08-02, CC01-02, CC72-02, CC12-01, CC11-01, CC10-01, CC09-01, ZZ99- |  | EPD | EDN
27 | 1DG | D3HQ185 | 10.4.21 | 1DG03BP02 | 415V SWGR O/G MODULE # 1DG03FB | UPS FEEDER | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 49 | 47 | 22.12.2019 | DR2687-1 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-L2, LV39-L1, LV73-01, LR08-02, CC01-02, CC72-02, CC12-01, CC11-01, CC10-01, CC09-01, ZZ99- |  | EPD | EDN
28 | 1DG | D03Q050 | 10.4.14 | 1DG03HP01 | 415V SWGR O/G MODULE # 1DG03FH | 24V BATTERY CHARGER (UNIT) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 53 | 49 | 03.012.2019 | DR0822_0001 |  |  | POWER SUPPLY (36A) | XLPE-AL UNARMOURED | LV38-R1, LV39-R1, LV73-01, LR08-02, CC01-02, CC72-02, CC12-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-01, ZZ99- |  | EPD | EDN
29 | 1DG | D03Q095 | 10.4.15 | 1DG03PP01 | 415V SWGR O/G MODULE # 1DG03RB | FEEDER TO LDB - TGB LV SWGR ROOM (1UF) (50kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (50kVA) | XLPE-AL UNARMOURED | LV38-R1, LV37-R1, LV36-R1, LV35-R1, LV34-R1, LV33-R1, ZZ99- |  | EPD | PEM
30 | 1DG | D02C1.5 | 10.5.01 | 1DG03QC01 | 415V SWGR MOTOR MODULE # 1DG03RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 131 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV43-03, LV44-03, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG31-03, TR06-02, TG32-02, TG33-02, ZZ99- |  | EPD | EPD
31 | 1DG | D03Q010 | 10.4.11 | 1DG03QP01 | 415V SWGR MOTOR MODULE # 1DG03RC | SEAL OIL PUMP - 2 (MKW12AP001) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 131 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV38-L3, LV41-01, LV42-01, LV43-01, LV44-01, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG31-01, TR06-01, TG32-01, TG33-01, ZZ99- |  | EPD | HWR
32 | 1DG | D02C1.5 | 10.5.01 | 1DG03RC01 | 415V SWGR MOTOR MODULE # 1DG03RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 161 | 199 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC15-02, IC16-02, ZZ99- |  | EPD | EPD
33 | 1DG | D03Q010 | 10.4.11 | 1DG03RP01 | 415V SWGR MOTOR MODULE # 1DG03RD | PA FAN - A LUB OIL PUMP - 2 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 161 | 185 | 03.03.20 | 0 |  |  | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC15-02, IC16-02, ZZ99- |  | EPD | RPT
34 | 1DG | D03Q050 | 10.4.14 | 1DG03UP01 | 415V SWGR O/G MODULE # 1DG03RG | 24V BATTERY CHARGER (UNIT) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 53 | 49 | 03.012.2019 | DR0822_0001 |  |  | POWER SUPPLY (36A) | XLPE-AL UNARMOURED | LV38-L2, LV39-L1, LV73-01, LR08-02, CC01-02, CC72-02, CC12-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-01, ZZ99- |  | EPD | EDN
35 | 1DG | D03Q095 | 10.4.15 | 1DG03VP01 | 415V SWGR O/G MODULE # 1DG03RH | FEEDER TO LDB - TGB ESP SWGR ROOM (1UG) (50kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 269 | [5 empty] | POWER SUPPLY (50kVA) | XLPE-AL UNARMOURED | LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES02-02, ES30-02, ER01-02, ES76-02, ES79-R1, ES64-01, ZZ99- |  | EPD | PEM
36 | 1DG | D02C1.5 | 10.5.01 | 1DG04BC01 | 415V SWGR MOTOR MODULE # 1DG04FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
37 | 1DG | D03Q025 | 10.4.12 | 1DG04BP01 | 415V SWGR MOTOR MODULE # 1DG04FB | AIR PREHEATER - B MAIN DRIVE MOTOR | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 163 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | LV38-R2, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-01, BA15-01, BR39-01, ZZ99- |  | EPD | RPT
38 | 1DG | D03L2.5 | 10.4.26 | 1DG04CP01 | 415V SWGR O/G MODULE # 1DG04FC | FURNACE MAINTENANCE PF2 WALL COVERAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (6kVA) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, ZZ99- |  | EPD | PEM
39 | 1DG | D03L2.5 | 10.4.26 | 1DG04DP01 | 415V SWGR O/G MODULE # 1DG04FD | FURNACE MAINTENANCE PF2 WALL COVERAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (6kVA) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, ZZ99- |  | EPD | PEM
40 | 1DG | D03L2.5 | 10.4.26 | 1DG04FP01 | 415V SWGR O/G MODULE # 1DG04FF | FURNACE MAINTENANCE PF2 WALL COVERAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 134 | [5 empty] | POWER SUPPLY (6kVA) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, ZZ99- |  | EPD | PEM
41 | 1DG | D02C1.5 | 10.5.01 | 1DG04GC01 | 415V SWGR MOTOR MODULE # 1DG04FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
42 | 1DG | D03Q025 | 10.4.12 | 1DG04GP01 | 415V SWGR MOTOR MODULE # 1DG04FG | AIR PREHEATER - A MAIN DRIVE MOTOR | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 163 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | LV38-R2, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-01, BA15-01, BR39-01, ZZ99- |  | EPD | RPT
43 | 1DG | D02C1.5 | 10.5.01 | 1DG04PC01 | 415V SWGR RDOL MODULE # 1DG04RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV53-02, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | EPD
44 | 1DG | D03L2.5 | 10.4.26 | 1DG04PP01 | 415V SWGR RDOL MODULE # 1DG04RB | SPEEDER GEAR MOTOR (MAX46BY001M) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY (0.12kW) | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV53-02, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HWR
45 | 1DG | D02C1.5 | 10.5.01 | 1DG04RC01 | 415V SWGR MOTOR MODULE # 1DG04RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
46 | 1DG | D03L2.5 | 10.4.26 | 1DG04RP01 | 415V SWGR MOTOR MODULE # 1DG04RD | AIR PREHEATER - A LUB. OIL PUMP - 2 SUPPORT BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | RPT
47 | 1DG | D02C1.5 | 10.5.01 | 1DG04SC01 | 415V SWGR MOTOR MODULE # 1DG04RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
48 | 1DG | D03L2.5 | 10.4.26 | 1DG04SP01 | 415V SWGR MOTOR MODULE # 1DG04RE | AIR PREHEATER - A LUB. OIL PUMP - 2 GUIDE BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | RPT
49 | 1DG | E04V0.5 | 10.7.02 | 1DG05AC01 | 415V SWGR DG I/C MODULE # 1DG05FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 66 | 27.09.2019 | DR0817_4798-4G-13 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
50 | 1DG | D02C1.5 | 10.5.01 | 1DG05AC02 | 415V SWGR DG I/C MODULE # 1DG05FA | ECD | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | VOLTAGE SIGNAL FOR SYNCHRONISATION (R-Y) | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LR06-03, ZZ99- |  | EPD | EDN
51 | 1DG | D05C2.5 | 10.5.07 | 1DG05AC03 | 415V SWGR DG I/C MODULE # 1DG05FA | DG ALTERNATOR TB | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | DIFFERENTIAL PROTECTION | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EPD | ISG
52 | 1DG | D05C2.5 | 10.5.07 | 1DG05AC04 | 415V SWGR DG I/C MODULE # 1DG05FA | DGCP | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | REMOTE METERING (CL-1 CTs) | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EPD | ISG
53 | 1DG | D03L2.5 | 10.4.26 | 1DG05AC05 | 415V SWGR DG I/C MODULE # 1DG05FA | DGCP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | 415V SUPPLY | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EPD | ISG
54 | 1DG | D02L2.5 | 10.4.24 | 1DG05AC06 | 415V SWGR DG I/C MODULE # 1DG05FA | DGCP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | NEUTRAL DISPLACMENT E/F PROTECTION | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EPD | ISG
55 | 1DG | D05C1.5 | 10.5.06 | 1DG05AC07 | 415V SWGR DG I/C MODULE # 1DG05FA | DGCP | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | OPEN (TRIP) COMMAND, BKR ON STATUS | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EPD | ISG
56 | 1DG | D05C1.5 | 10.5.06 | 1DG05AC08 | 415V SWGR DG I/C MODULE # 1DG05FA | DGCP | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | DIFFERENTIAL TRIP, E/F TRIP FEEDBACK | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EPD | ISG
57 | 1DG | D02C1.5 | 10.5.01 | 1DG05AC09 | 415V SWGR DG I/C MODULE # 1DG05FA | DGCP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | BUS-A & BUS-B VOLTAGE STATUS | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EPD | ISG
58 | 1DG | E04V0.5 | 10.7.02 | 1DG05AC10 | 415V SWGR DG I/C MODULE # 1DG05FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 66 | 27.09.2019 | DR0817_4798-4G-13 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
59 | 1DG | D01Q630 | 10.4.05 | 1DG05AP01 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-02, LR11-L2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
60 | 1DG | D01Q630 | 10.4.05 | 1DG05AP02 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-02, LR11-L2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
61 | 1DG | D01Q630 | 10.4.05 | 1DG05AP03 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-02, LR11-L2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
62 | 1DG | D01Q630 | 10.4.05 | 1DG05AP04 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
63 | 1DG | D01Q630 | 10.4.05 | 1DG05AP05 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
64 | 1DG | D01Q630 | 10.4.05 | 1DG05AP06 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
65 | 1DG | D01Q630 | 10.4.05 | 1DG05AP07 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
66 | 1DG | D01Q630 | 10.4.05 | 1DG05AP08 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
67 | 1DG | D01Q630 | 10.4.05 | 1DG05AP09 | 415V SWGR DG I/C MODULE # 1DG05FA | DG-1 | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-L2, LV37-L2, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP09-01, IP10-01, IP11-01, IP12-01, IP13-01, ZZ99- |  | EPD | ISG
68 | 1DG | D02C1.5 | 10.5.01 | 1DG05CC01 | 415V SWGR BUS PT MODULE # 1DG05FC | ECD | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | VOLTAGE SIGNAL FOR SYNCHRONISATION (R-Y) | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LR06-03, ZZ99- |  | EPD | EDN
69 | 1DG | E04V0.5 | 10.7.02 | 1DG06AC01 | 415V SWGR TIE MODULE # 1DG06FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 67 | 27.09.2019 | DR0817_4798-4G-13 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
70 | 1DG | D02C1.5 | 10.5.01 | 1DG06AC02 | 415V SWGR TIE MODULE # 1DG06FA | ECD | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | VOLTAGE SIGNAL FOR SYNCHRONISATION (R-Y) | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LR06-03, ZZ99- |  | EPD | EDN
71 | 1DG | D02C1.5 | 10.5.01 | 1DG06AC03 | 415V SWGR TIE MODULE # 1DG06FA | DGCP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | BKR ON STATUS | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
72 | 1DG | D02C1.5 | 10.5.01 | 1DG06AC04 | 415V SWGR TIE MODULE # 1DG06FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV38-L4, LV39-L4, LV73-03, MR07-03, MA08-03, MV60-L2, MV63-05, ZZ99- |  | EPD | EPD
73 | 1DG | E04V0.5 | 10.7.02 | 1DG07AC01 | 415V SWGR DG B/C MODULE # 1DG07FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 67 | 27.09.2019 | DR0817_4798-4G-13 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
74 | 1DG | E04V0.5 | 10.7.02 | 1DG07AC02 | 415V SWGR DG B/C MODULE # 1DG07FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 67 | 27.09.2019 | DR0817_4798-4G-13 |  |  | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
75 | 1DG | E04V0.5 | 10.7.02 | 1DG09AC01 | 415V SWGR TIE MODULE # 1DG09FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 66 | 28.09.2019 | DR0817_4798-4G-34 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
76 | 1DG | D02C1.5 | 10.5.01 | 1DG09AC02 | 415V SWGR TIE MODULE # 1DG09FA | ECD | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | VOLTAGE SIGNAL FOR SYNCHRONISATION (R-Y) | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LR06-03, ZZ99- |  | EPD | EDN
77 | 1DG | D02C1.5 | 10.5.01 | 1DG09AC03 | 415V SWGR TIE MODULE # 1DG09FA | DGCP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | BKR ON STATUS | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
78 | 1DG | D02C1.5 | 10.5.01 | 1DG09AC04 | 415V SWGR TIE MODULE # 1DG09FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 41 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV38-L4, LV39-L4, LV73-03, MR07-03, MA08-03, MV60-L2, MV59-R1, MV69-03, ZZ99- |  | EPD | EPD
79 | 1DG | E04V0.5 | 10.7.02 | 1DG10AC01 | 415V SWGR DG I/C MODULE # 1DG10FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 66 | 28.09.2019 | DR0817_4798-4G-13 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
80 | 1DG | D02C1.5 | 10.5.01 | 1DG10AC02 | 415V SWGR DG I/C MODULE # 1DG10FA | ECD | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | VOLTAGE SIGNAL FOR SYNCHRONISATION (R-Y) | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LR06-03, ZZ99- |  | EPD | EDN
81 | 1DG | D05C2.5 | 10.5.07 | 1DG10AC03 | 415V SWGR DG I/C MODULE # 1DG10FA | DG ALTERNATOR TB | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | DIFFERENTIAL PROTECTION | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
82 | 1DG | D05C2.5 | 10.5.07 | 1DG10AC04 | 415V SWGR DG I/C MODULE # 1DG10FA | DGCP | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | REMOTE METERING (CL-1 CTs) | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
83 | 1DG | D03L2.5 | 10.4.26 | 1DG10AC05 | 415V SWGR DG I/C MODULE # 1DG10FA | DGCP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | 415V SUPPLY | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
84 | 1DG | D02L2.5 | 10.4.24 | 1DG10AC06 | 415V SWGR DG I/C MODULE # 1DG10FA | DGCP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | NEUTRAL DISPLACMENT E/F PROTECTION | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
85 | 1DG | D05C1.5 | 10.5.06 | 1DG10AC07 | 415V SWGR DG I/C MODULE # 1DG10FA | DGCP | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | OPEN (TRIP) COMMAND, BKR ON STATUS | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
86 | 1DG | D05C1.5 | 10.5.06 | 1DG10AC08 | 415V SWGR DG I/C MODULE # 1DG10FA | DGCP | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | DIFFERENTIAL TRIP, E/F TRIP FEEDBACK | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
87 | 1DG | D02C1.5 | 10.5.01 | 1DG10AC09 | 415V SWGR DG I/C MODULE # 1DG10FA | DGCP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | BUS-A & BUS-B VOLTAGE STATUS | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, ZZ99- |  | EPD | ISG
88 | 1DG | E04V0.5 | 10.7.02 | 1DG10AC10 | 415V SWGR DG I/C MODULE # 1DG10FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | 66 | 28.09.2019 | DR0817_4798-4G-13 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV38-R4, LV41-04, LV42-04, LV24-R4, LV75-04, LV77-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
89 | 1DG | D01Q630 | 10.4.05 | 1DG10AP01 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP08-01, ZZ99- |  | EPD | ISG
90 | 1DG | D01Q630 | 10.4.05 | 1DG10AP02 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP08-01, ZZ99- |  | EPD | ISG
91 | 1DG | D01Q630 | 10.4.05 | 1DG10AP03 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP08-01, ZZ99- |  | EPD | ISG
92 | 1DG | D01Q630 | 10.4.05 | 1DG10AP04 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP08-01, ZZ99- |  | EPD | ISG
93 | 1DG | D01Q630 | 10.4.05 | 1DG10AP05 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP08-01, ZZ99- |  | EPD | ISG
94 | 1DG | D01Q630 | 10.4.05 | 1DG10AP06 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L1, TY23-L1, TY22-L1, TY21-L1, TY20-L1, IP01-R2, IP02-R2, IR02-01, IP07-01, IP08-01, ZZ99- |  | EPD | ISG
95 | 1DG | D01Q630 | 10.4.05 | 1DG10AP07 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L2, TY23-L2, TY22-L2, TY21-L2, TY20-L2, IP01-R3, IP02-R3, IR02-02, IP07-02, IP08-01, ZZ99- |  | EPD | ISG
96 | 1DG | D01Q630 | 10.4.05 | 1DG10AP08 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L2, TY23-L2, TY22-L2, TY21-L2, TY20-L2, IP01-R3, IP02-R3, IR02-02, IP07-02, IP08-01, ZZ99- |  | EPD | ISG
97 | 1DG | D01Q630 | 10.4.05 | 1DG10AP09 | 415V SWGR DG I/C MODULE # 1DG10FA | STANDBY DG | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1600A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV72-03, LR11-R2, TY24-L2, TY23-L2, TY22-L2, TY21-L2, TY20-L2, IP01-R3, IP02-R3, IR02-02, IP07-02, IP08-01, ZZ99- |  | EPD | ISG
98 | 1DG | D02C1.5 | 10.5.01 | 1DG10CC01 | 415V SWGR BUS PT MODULE # 1DG10FC | ECD | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | VOLTAGE SIGNAL FOR SYNCHRONISATION (R-Y) | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LR06-03, ZZ99- |  | EPD | EDN
99 | 1DG | D02C1.5 | 10.5.01 | 1DG11PC01 | 415V SWGR MOTOR MODULE # 1DG11RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 69 | 90 | 03.03.20 | DR1150_17PA011786 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV43-03, LV44-03, LV76-03, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, ZZ99- |  | EPD | EPD
100 | 1DG | D03Q010 | 10.4.11 | 1DG11PP01 | 415V SWGR MOTOR MODULE # 1DG11RB | BFP-C AOP (LAC30AP002) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 67 | 88 | 03.03.20 | 20 |  |  | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-L3, LV41-01, LV42-01, LV43-01, LV44-01, LV76-01, MR10-01, MA05-01, MV68-01, MV10-01, MV74-01, MV75-02, TR51-02, TG69-02, ZZ99- |  | EPD | HYD
101 | 1DG | D02C1.5 | 10.5.01 | 1DG12CC01 | 415V SWGR MOTOR MODULE # 1DG12FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 85 | 118 | 03.03.20 | DR1150_17PA011786 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, ZZ99- |  | EPD | EPD
102 | 1DG | D02L2.5 | 10.4.24 | 1DG12CC02 | 415V SWGR MOTOR MODULE # 1DG12FC | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 85 | 128 | 16.01.20 | DR1095_0045 |  |  | SPACE HEATER | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, ZZ99- |  | EPD | PEM
103 | 1DG | D03Q095 | 10.4.15 | 1DG12CP01 | 415V SWGR MOTOR MODULE # 1DG12FC | JACKING OIL PUMP - 1 (MAV31AP001) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 80 | 115 | 02.03.20 | DR0822_0005 |  |  | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV36-R1, LV50-01, LV30-L1, LV31-L1, LV61-01, LV62-01, LV63-02, LV64-02, TR48-02, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, ZZ99- |  | EPD | PEM
104 | 1DG | D3HQ185 | 10.4.21 | 1DG12QP01 | 415V SWGR O/G MODULE # 1DG12RC | CHIMNEY AVIATION LIGHTING | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 413 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99- |  | EPD | PEM
105 | 1DG | D3HQ185 | 10.4.21 | 1DG12QP02 | 415V SWGR O/G MODULE # 1DG12RC | CHIMNEY AVIATION LIGHTING | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 414 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, IM44-03, IM46-02, IM47-02, IM48-02, IM49-02, IM50-02, ZZ99- |  | EPD | PEM
106 | 1DG | D02C1.5 | 10.5.01 | 1DG12SC01 | 415V SWGR MOTOR MODULE # 1DG12RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM69-03, IR26-02, IM70-03, IM71-03, ZZ99- |  | EPD | EPD
107 | 1DG | D03Q010 | 10.4.11 | 1DG12SP01 | 415V SWGR MOTOR MODULE # 1DG12RE | PA FAN - B LUB OIL PUMP - 2 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM69-03, IR26-02, IM70-03, IM71-03, ZZ99- |  | EPD | RPT
108 | 1DG | D02C1.5 | 10.5.01 | 1DG12VC01 | 415V SWGR MOTOR MODULE # 1DG12RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 160 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03 |  | EPD | EPD
109 | 1DG | D03Q025 | 10.4.12 | 1DG12VP01 | 415V SWGR MOTOR MODULE # 1DG12RH | AIR PREHEATER - B MAIN DRIVE MOTOR | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 163 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | LV38-R2, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-01, BA15-01, BR39-01, ZZ99- |  | EPD | RPT
110 | 1DG | D02C1.5 | 10.5.01 | 1DG13DC01 | 415V SWGR RDOL MODULE # 1DG13FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV53-02, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | EPD
111 | 1DG | D03L2.5 | 10.4.26 | 1DG13DP01 | 415V SWGR RDOL MODULE # 1DG13FD | STARTING DEVICE MOTOR (MAX47BY001M) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY (0.12kW) | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV53-02, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | PEM
112 | 1DG | D02C1.5 | 10.5.01 | 1DG13QC01 | 415V SWGR MOTOR MODULE # 1DG13RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD10-02, BD11-02, ZZ99- |  | EPD | EPD
113 | 1DG | D03Q010 | 10.4.11 | 1DG13QP01 | 415V SWGR MOTOR MODULE # 1DG13RC | SCANNER AIR FAN AC MOTOR (HHQ11AN001) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 98 | 110 | 03.03.20 | 0 |  |  | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-R2, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BD10-01, BD11-01, ZZ99- |  | EPD | RPT
114 | 1DG | D02C1.5 | 10.5.01 | 1DG13SC01 | 415V SWGR MOTOR MODULE # 1DG13RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 311 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | EPD
115 | 1DG | D03Q010 | 10.4.11 | 1DG13SP01 | 415V SWGR MOTOR MODULE # 1DG13RE | ID FAN - B LUB OIL PUMP - 2 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 311 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | RPT
116 | 1DG | D03Q095 | 10.4.15 | 1DG13TP01 | 415V SWGR O/G MODULE # 1DG13RF | FEEDER FOR SWITCHYARD | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY (100A) | XLPE-AL UNARMOURED | LV38-R2, LV37-R1, LV36-R1, LV35-R1, LV34-R1, LV33-R1, LV70-01, LR04-01, TY17-L2, TY18-R2, YR02-02, TY25-02, TY26-02, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-01, TY35-01, ZZ99- |  | EPD | PEM
117 | 1DG | D03Q050 | 10.4.14 | 1DG13UP01 | 415V SWGR O/G MODULE # 1DG13RG | 24V BATTERY CHARGER (UNIT) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 53 | 53 | 03.012.2019 | DR0822_0001 |  |  | POWER SUPPLY (36A) | XLPE-AL UNARMOURED | LV38-L2, LV39-L1, LV73-02, LR08-02, CC01-02, CC72-02, CC12-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-01, ZZ99- |  | EPD | EDN
118 | 1DG | D03Q050 | 10.4.14 | 1DG14DP01 | 415V SWGR O/G MODULE # 1DG14FD | 24V BATTERY CHARGER (UNIT) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 53 | 53 | 03.012.2019 | DR0822_0001 |  |  | POWER SUPPLY (36A) | XLPE-AL UNARMOURED | LV38-L2, LV39-L1, LV73-02, LR08-02, CC01-02, CC72-02, CC12-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-01, ZZ99- |  | EPD | EDN
119 | 1DG | D02C1.5 | 10.5.01 | 1DG14EC01 | 415V SWGR MOTOR MODULE # 1DG14FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 223 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IR33-02, IM81-02, IM82-02, IM83-02, ZZ99- |  | EPD | EPD
120 | 1DG | D03Q025 | 10.4.12 | 1DG14EP01 | 415V SWGR MOTOR MODULE # 1DG14FE | MILL - F LUB OIL PUMP - 2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 224 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-L3, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM64-02, IM65-02, IM66-02, IM67-02, IM68-02, IM72-02, IM75-02, IR28-02, IM76-02, IM77-02, IM78-02, IR32-02, IM79-02, IM80-02, IR33-02, IM81-02, IM82-02, IM83-01, ZZ99- |  | EPD | RPT
121 | 1DG | D03L2.5 | 10.4.26 | 1DG14FP01 | 415V SWGR O/G MODULE # 1DG14FF | FURNACE MAINTENANCE PF2 WALL COVERAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (6kVA) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, ZZ99- |  | EPD | PEM
122 | 1DG | D02C1.5 | 10.5.01 | 1DG14HC01 | 415V SWGR MOTOR MODULE # 1DG14FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM73-03, IR27-03, IM74-03, ZZ99- |  | EPD | EPD
123 | 1DG | D03Q010 | 10.4.11 | 1DG14HP01 | 415V SWGR MOTOR MODULE # 1DG14FH | FD FAN - B LUB OIL PUMP - 2 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM73-03, IR27-03, IM74-03, ZZ99- |  | EPD | RPT
124 | 1DG | D02C1.5 | 10.5.01 | 1DG15BC01 | 415V SWGR MOTOR MODULE # 1DG15FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 98 | 103 | 03.03.20 | DR1150_17PA011786 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV59-02, TR50-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, ZZ99- |  | EPD | EPD
125 | 1DG | D03Q010 | 10.4.11 | 1DG15BP01 | 415V SWGR MOTOR MODULE # 1DG15FB | BFP-B AOP (LAC20AP002) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 98 | 128 | 03.03.20 | 20 |  |  | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-L3, LV37-L1, LV36-L1, LV50-01, LV30-L1, LV56-02, LV57-01, LV58-01, LV59-01, TR50-01, MR15-01, TR02-01, TG85-01, TG86-02, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, ZZ99- |  | EPD | HYD
126 | 1DG | D02C1.5 | 10.5.01 | 1DG15CC01 | 415V SWGR MOTOR MODULE # 1DG15FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 98 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV53-02, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, ZZ99- |  | EPD | EPD
127 | 1DG | D03L2.5 | 10.4.26 | 1DG15CP01 | 415V SWGR MOTOR MODULE # 1DG15FC | SIREN (MOTOR OPERATED) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 98 | [5 empty] | POWER SUPPLY (0.19kW) | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV53-02, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, ZZ99- |  | EPD | PEM
128 | 1DG | D02C1.5 | 10.5.01 | 1DG15DC01 | 415V SWGR MOTOR MODULE # 1DG15FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 246 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IR14-02, IC35-03, IC36-03, ZZ99- |  | EPD | EPD
129 | 1DG | D03Q025 | 10.4.12 | 1DG15DP01 | 415V SWGR MOTOR MODULE # 1DG15FD | MILL - B LUB OIL PUMP - 2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 241 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-R1, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IC07-R1, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IC33-02, IC34-02, IR14-02, IC35-02, IC36-01, ZZ99- |  | EPD | RPT
130 | 1DG | D03L2.5 | 10.4.26 | 1DG15EP01 | 415V SWGR O/G MODULE # 1DG15FE | SUPPLY FAN | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV38-L4, LV37-L4, LV36-L4, LV50-02, LV51-02, LV52-02, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, ZZ99- |  | EPD | PEM
131 | 1DG | D03Q095 | 10.4.15 | 1DG15HP01 | 415V SWGR O/G MODULE # 1DG15FH | FEEDER TO LDB - TGB ESP SWGR ROOM (1UG) (50kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 269 | [5 empty] | POWER SUPPLY (50kVA) | XLPE-AL UNARMOURED | LV38-L1, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L2, ES01-L2, ES02-02, ES30-02, ER01-02, ES76-02, ES79-R1, ES64-01, ZZ99- |  | EPD | PEM
132 | 1DG | D02C1.5 | 10.5.01 | 1DG15RC01 | 415V SWGR MOTOR MODULE # 1DG15RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
133 | 1DG | D03L2.5 | 10.4.26 | 1DG15RP01 | 415V SWGR MOTOR MODULE # 1DG15RD | AIR PREHEATER - B LUB. OIL PUMP - 2 GUIDE BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | RPT
134 | 1DG | D02C1.5 | 10.5.01 | 1DG15SC01 | 415V SWGR MOTOR MODULE # 1DG15RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
135 | 1DG | D03L2.5 | 10.4.26 | 1DG15SP01 | 415V SWGR MOTOR MODULE # 1DG15RE | AIR PREHEATER - B LUB. OIL PUMP - 2 SUPPORT BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | RPT
136 | 1DG | D03Q095 | 10.4.15 | 1DG15TP01 | 415V SWGR O/G MODULE # 1DG15RF | FEEDER TO LDB - TGB LV SWGR ROOM (1UF) (50kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (50kVA) | XLPE-AL UNARMOURED | LV38-R1, LV37-R1, LV36-R1, LV35-R1, LV34-R1, LV33-R1, ZZ99- |  | EPD | PEM
137 | 1DG | D03L2.5 | 10.4.26 | 1DG15UP01 | 415V SWGR O/G MODULE # 1DG15RG | EXHAUST FAN | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV43-03, LV44-03, LV45-03, TR52-03, ZZ99- |  | EPD | PEM
138 | 1DG | D03Q095 | 10.4.15 | 1DG15VP01 | 415V SWGR O/G MODULE # 1DG15RH | DG AUX PANEL | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 121 | [5 empty] | POWER SUPPLY (100A) | XLPE-AL UNARMOURED | LV38-L3, LV37-L1, LV72-02, LR11-L2, TY24-L2, TY23-L2, TY22-L2, TY21-L2, TY20-L2, IP01-R3, IP02-R3, IR02-02, IP07-02, IP09-01, IP10-01, ZZ99- |  | EPD | ISG
139 | 1DG | D02C1.5 | 10.5.01 | 1DG16BC01 | 415V SWGR MOTOR MODULE # 1DG16FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
140 | 1DG | D03Q025 | 10.4.12 | 1DG16BP01 | 415V SWGR MOTOR MODULE # 1DG16FB | AIR PREHEATER - A MAIN DRIVE MOTOR | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 163 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | LV38-R2, LV41-01, LV42-01, LV24-L1, LV75-01, LV77-02, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-01, BA15-01, BR39-01, ZZ99- |  | EPD | RPT
141 | 1DG | D03Q240 | 10.4.17 | 1DG16CP01 | 415V SWGR O/G MODULE # 1DG16FC | TURBINE VALVE ACDB # 1KB | 03C X 240 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | LV38-R1, LV37-R1, LV36-R1, LV35-R1, LV55-02, LV31-L1, LV61-01, LV62-01, LV63-02, LV03-L1, ZZ99- |  | EPD | EPD
142 | 1DG | D01Q400 | 10.4.04 | 1DG16PP01 | 415V SWGR O/G MODULE # 1DG16RB | 220V FCBC-1B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 33 | 44 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-R1, LV41-01, LV42-01, LV43-01, LV10-L1, ZZ99- |  | EPD | PEM
143 | 1DG | D01Q400 | 10.4.04 | 1DG16PP02 | 415V SWGR O/G MODULE # 1DG16RB | 220V FCBC-1B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 33 | 44 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-R1, LV41-01, LV42-01, LV43-01, LV10-L1, ZZ99- |  | EPD | PEM
144 | 1DG | D01Q400 | 10.4.04 | 1DG16PP03 | 415V SWGR O/G MODULE # 1DG16RB | 220V FCBC-1B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 33 | 44 | 06.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | LV38-R1, LV41-01, LV42-01, LV43-01, LV10-L1, ZZ99- |  | EPD | PEM
145 | 1DG | D03L2.5 | 10.4.26 | 1DG16RP01 | 415V SWGR O/G MODULE # 1DG16RD | FURNACE MAINTENANCE PF2 WALL COVERAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 138 | [5 empty] | POWER SUPPLY (6kVA) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, BR21-04, ZZ99- |  | EPD | PEM
146 | 1DG | D02C1.5 | 10.5.01 | 1DG16TC01 | 415V SWGR MOTOR MODULE # 1DG16RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 248 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM92-02, ZZ99- |  | EPD | EPD
147 | 1DG | D03Q025 | 10.4.12 | 1DG16TP01 | 415V SWGR MOTOR MODULE # 1DG16RF | MILL - D LUB OIL PUMP - 2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 250 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM64-02, IM65-02, IM66-02, IM67-02, IM68-02, IM72-02, IM75-02, IR28-02, IM76-02, IM77-02, IM78-02, IR32-02, IM79-02, IM80-02, IM85-02, IM86-02, IM87-02, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM92-01, ZZ99- |  | EPD | RPT
148 | 1DG | D03L2.5 | 10.4.26 | 1DG16VP01 | 415V SWGR O/G MODULE # 1DG16RH | FURNACE MAINTENANCE PF2 WALL COVERAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | POWER SUPPLY (6kVA) | XLPE-CU UNARMOURED | LV38-L4, LV41-03, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, ZZ99- |  | EPD | PEM
1 | 1HA | D02C1.5 | 10.5.01 | 1HA01BC01 | 415V SWGR MOTOR MODULE # 1HA01FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 412 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, ZZ99- |  | EPD | EPD
2 | 1HA | D03Q025 | 10.4.12 | 1HA01BP01 | 415V SWGR MOTOR MODULE # 1HA01FB | SEAL AIR BLOWER MOTOR1 OF FGD OUTLET GATE | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 418 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R2, LV48-02, LV47-02, LV46-02, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IR21-02, ZZ99- |  | EPD | PEM
3 | 1HA | D03Q010 | 10.4.11 | 1HA01CP01 | 415V SWGR O/G MODULE # 1HA01FC | LUB OIL HEATER FOR MILL - A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 247 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IR13-02, IC30-03, IC32-03, ZZ99- |  | EPD | PEM
4 | 1HA | D02C1.5 | 10.5.01 | 1HA01DC01 | 415V SWGR MOTOR MODULE # 1HA01FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 182 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB12-02, ZZ99- |  | EPD | EPD
5 | 1HA | D03Q010 | 10.4.11 | 1HA01DP01 | 415V SWGR MOTOR MODULE # 1HA01FD | SEAL AIR BLOWER MOTOR1 OF AIR HEATER - A SECONDARY AIR OUTLE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (9.3kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R1, LV10-R1, LV44-01, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-01, BA15-01, BR39-01, BB12-01, ZZ99- |  | EPD | PEM
6 | 1HA | D02C1.5 | 10.5.01 | 1HA01EC01 | 415V SWGR MOTOR MODULE # 1HA01FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 182 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB13-02, ZZ99- |  | EPD | EPD
7 | 1HA | D03Q010 | 10.4.11 | 1HA01EP01 | 415V SWGR MOTOR MODULE # 1HA01FE | SEAL AIR BLOWER MOTOR1 OF AIR HEATER - B SECONDARY AIR OUTLE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 182 | [5 empty] | POWER SUPPLY (9.3kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R1, LV10-R1, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-02, BA15-02, BR39-01, BB13-01, ZZ99- |  | EPD | PEM
8 | 1HA | D02C1.5 | 10.5.01 | 1HA01FC01 | 415V SWGR MOTOR MODULE # 1HA01FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 299 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IC44-02, IR16-02, IC45-02, ZZ99- |  | EPD | EPD
9 | 1HA | D02L2.5 | 10.4.24 | 1HA01FC02 | 415V SWGR MOTOR MODULE # 1HA01FF | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 299 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IC44-02, IR16-02, IC45-02, ZZ99- |  | EPD | PEM
10 | 1HA | D03Q150 | 10.4.16 | 1HA01FP01 | 415V SWGR MOTOR MODULE # 1HA01FF | SEAL AIR FAN - A | 03C X 150 XLPE-Al FRLS ( 1.1 kV ) | 293 | [5 empty] | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R1, LV10-R1, LV44-01, LV76-01, LV79-01, LR10-R1, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IC07-R1, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IC33-02, IC34-02, IC38-02, IC39-02, IC40-02, IC44-01, IR16-01, IC45-01, ZZ99- |  | EPD | PEM
11 | 1HA | D02C1.5 | 10.5.01 | 1HA01PC01 | 415V SWGR MOTOR MODULE # 1HA01RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 401 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | EPD
12 | 1HA | D03Q010 | 10.4.11 | 1HA01PP01 | 415V SWGR MOTOR MODULE # 1HA01RB | SEAL AIR BLOWER MOTOR1 OF ID FAN - A OUTLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 410 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R2, LV48-03, LV47-02, LV46-02, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, IM44-03, IM45-03, ZZ99- |  | EPD | PEM
13 | 1HA | D02C1.5 | 10.5.01 | 1HA01QC01 | 415V SWGR MOTOR MODULE # 1HA01RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 346 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | EPD
14 | 1HA | D03Q010 | 10.4.11 | 1HA01QP01 | 415V SWGR MOTOR MODULE # 1HA01RC | SEAL AIR BLOWER MOTOR1 OF ID FAN - B OUTLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 352 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R3, LV48-03, LV47-02, LV46-02, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IR21-02, IM57-02, IM58-02, IM59-02, ZZ99- |  | EPD | PEM
15 | 1HA | D02C1.5 | 10.5.01 | 1HA01RC01 | 415V SWGR MOTOR MODULE # 1HA01RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 182 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB12-02, ZZ99- |  | EPD | EPD
16 | 1HA | D03L2.5 | 10.4.26 | 1HA01RP01 | 415V SWGR MOTOR MODULE # 1HA01RD | AIR PREHEATER - A LUB. OIL PUMP - 1 SUPPORT BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 180 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB12-02, ZZ99- |  | EPD | PEM
17 | 1HA | D03Q010 | 10.4.11 | 1HA01SP01 | 415V SWGR O/G MODULE # 1HA01RE | LUB OIL HEATER FOR MILL - C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 273 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IR15-02, IC41-03, IC43-03, ZZ99- |  | EPD | PEM
18 | 1HA | D02C1.5 | 10.5.01 | 1HA01TC01 | 415V SWGR MOTOR MODULE # 1HA01RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 391 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | EPD
19 | 1HA | D03Q025 | 10.4.12 | 1HA01TP01 | 415V SWGR MOTOR MODULE # 1HA01RF | ID FAN - A LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 391 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | PEM
20 | 1HA | D02C1.5 | 10.5.01 | 1HA01UC01 | 415V SWGR MOTOR MODULE # 1HA01RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 248 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IR13-02, IC30-03, IC31-03, ZZ99- |  | EPD | EPD
21 | 1HA | D03Q025 | 10.4.12 | 1HA01UP01 | 415V SWGR MOTOR MODULE # 1HA01RG | MILL - A LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 242 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R1, LV10-R1, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IC07-L2, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IR13-02, IC30-02, IC31-01, ZZ99- |  | EPD | PEM
22 | 1HA | D02C1.5 | 10.5.01 | 1HA01VC01 | 415V SWGR MOTOR MODULE # 1HA01RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 182 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB12-02, ZZ99- |  | EPD | EPD
23 | 1HA | D03Q050 | 10.4.14 | 1HA01VP01 | 415V SWGR MOTOR MODULE # 1HA01RH | SEAL AIR BLOWER MOTOR1 OF AIR HEATER - A PRIMARY AIR OUTLET | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 177 | [5 empty] | POWER SUPPLY (22kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R1, LV10-R1, LV44-01, LV76-01, LV79-01, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-01, BA15-01, BR39-01, BB12-01, ZZ99- |  | EPD | PEM
24 | 1HA | D02C1.5 | 10.5.01 | 1HA02BC01 | 415V SWGR MOTOR MODULE # 1HA02FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 412 | 202 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, ZZ99- |  | EPD | EPD
25 | 1HA | D03Q025 | 10.4.12 | 1HA02BP01 | 415V SWGR MOTOR MODULE # 1HA02FB | SEAL AIR BLOWER MOTOR1 OF FGD BYPASS DAMPER | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 418 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R3, LV48-03, LV47-02, LV46-02, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IR21-02, ZZ99- |  | EPD | PEM
26 | 1HA | D02C1.5 | 10.5.01 | 1HA02CC01 | 415V SWGR MOTOR MODULE # 1HA02FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, ZZ99- |  | EPD | EPD
27 | 1HA | D03Q010 | 10.4.11 | 1HA02CP01 | 415V SWGR MOTOR MODULE # 1HA02FC | DRAIN OIL PUMP (BOILER HOUSE) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 101 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R1, LV10-R1, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR01-01, ZZ99- |  | EPD | PEM
28 | 1HA | D02C1.5 | 10.5.01 | 1HA02DC01 | 415V SWGR MOTOR MODULE # 1HA02FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 274 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IR15-02, IC41-03, IC42-03, ZZ99- |  | EPD | EPD
29 | 1HA | D03Q025 | 10.4.12 | 1HA02DP01 | 415V SWGR MOTOR MODULE # 1HA02FD | MILL - C LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 270 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-L2, LV12-L2, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IC07-L2, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IC33-02, IC34-02, IC38-02, IC39-02, IC40-02, IR15-02, IC41-02, IC42-01, ZZ99- |  | EPD | PEM
30 | 1HA | D02C1.5 | 10.5.01 | 1HA02PC01 | 415V SWGR MOTOR MODULE # 1HA02RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 180 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | EPD
31 | 1HA | D03L2.5 | 10.4.26 | 1HA02PP01 | 415V SWGR MOTOR MODULE # 1HA02RB | AIR PREHEATER - A CLEANING DEVICE MOTOR - GAS OUT | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 179 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, ZZ99- |  | EPD | PEM
32 | 1HA | D03Q010 | 10.4.11 | 1HA02QP01 | 415V SWGR O/G MODULE # 1HA02RC | LUB OIL HEATER FOR MILL - E | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 264 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IR34-02, IM97-02, IM98-02, ZZ99- |  | EPD | PEM
33 | 1HA | D02C1.5 | 10.5.01 | 1HA02RC01 | 415V SWGR MOTOR MODULE # 1HA02RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 186 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC19-L2, IC20-02, IC21-02, ZZ99- |  | EPD | EPD
34 | 1HA | D03Q010 | 10.4.11 | 1HA02RP01 | 415V SWGR MOTOR MODULE # 1HA02RD | FD FAN - A LUB OIL PUMP - 1 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 185 | 191 | 03.03.20 | 0 |  |  | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC19-L2, IC20-02, IC21-02, ZZ99- |  | EPD | PEM
35 | 1HA | D02C1.5 | 10.5.01 | 1HA02SC01 | 415V SWGR MOTOR MODULE # 1HA02RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 266 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IR34-02, IM97-02, IM98-02, IM99-02, ZZ99- |  | EPD | EPD
36 | 1HA | D03Q025 | 10.4.12 | 1HA02SP01 | 415V SWGR MOTOR MODULE # 1HA02RE | MILL - E LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 272 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-L2, LV12-L2, LV11-L3, LV48-03, LV47-02, LV46-02, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM64-02, IM65-02, IM66-02, IM67-02, IM68-02, IM72-02, IM75-02, IR28-02, IM76-02, IM77-02, IM78-02, IR32-02, IM79-02, IM80-02, IM85-02, IM86-02, IM87-02, IR34-02, IM97-02, IM98-02, IM99-01, ZZ99- |  | EPD | PEM
37 | 1HA | D02C1.5 | 10.5.01 | 1HA02TC01 | 415V SWGR MOTOR MODULE # 1HA02RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 152 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, ZZ99- |  | EPD | EPD
38 | 1HA | D03Q050 | 10.4.14 | 1HA02TP01 | 415V SWGR MOTOR MODULE # 1HA02RF | SEAL AIR BLOWER MOTOR1 OF AIR HEATER - B PRIMARY AIR OUTLET | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 147 | [5 empty] | POWER SUPPLY (22kW) | XLPE-AL UNARMOURED | LV13-R1, LV12-R1, LV11-R1, LV10-R1, LV44-01, LV76-01, LV79-01, LR10-R1, IC01-R1, IC02-R1, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC09-01, ZZ99- |  | EPD | PEM
39 | 1HA | D02C1.5 | 10.5.01 | 1HA03BC01 | 415V SWGR MOTOR MODULE # 1HA03FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 179 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, BI17-02, BI04-02, BI05-02, ZZ99- |  | EPD | EPD
40 | 1HA | D03Q010 | 10.4.11 | 1HA03BP01 | 415V SWGR MOTOR MODULE # 1HA03FB | SEAL AIR BLOWER MOTOR1 OF SCR - A BYPASS DAMPER | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 177 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, BI17-02, BI04-02, BI05-02, ZZ99- |  | EPD | PEM
41 | 1HA | D02C1.5 | 10.5.01 | 1HA03CC01 | 415V SWGR MOTOR MODULE # 1HA03FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 160 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI16-02, BI15-02, ZZ99- |  | EPD | EPD
42 | 1HA | D03Q010 | 10.4.11 | 1HA03CP01 | 415V SWGR MOTOR MODULE # 1HA03FC | SEAL AIR BLOWER MOTOR1 OF SCR - B BYPASS DAMPER | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 159 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI16-02, BI15-02, ZZ99- |  | EPD | PEM
43 | 1HA | D02C1.5 | 10.5.01 | 1HA03EC01 | 415V SWGR MOTOR MODULE # 1HA03FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 138 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, ZZ99- |  | EPD | EPD
44 | 1HA | D03Q010 | 10.4.11 | 1HA03EP01 | 415V SWGR MOTOR MODULE # 1HA03FE | PENT HOUSE FAN MOTOR - A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 137 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-L2, LV12-L2, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, ZZ99- |  | EPD | PEM
45 | 1HA | D02C1.5 | 10.5.01 | 1HA03PC01 | 415V SWGR MOTOR MODULE # 1HA03RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 161 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, ZZ99- |  | EPD | EPD
46 | 1HA | D03Q010 | 10.4.11 | 1HA03PP01 | 415V SWGR MOTOR MODULE # 1HA03RB | PENT HOUSE FAN MOTOR - C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 160 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BG23-01, BG24-01, BG22-01, BR22-01, BR23-01, BR24-01, BR25-01, BR26-01, BR27-01, BR28-01, BR29-01, ZZ99- |  | EPD | PEM
47 | 1HA | D04Q010 | 10.4.22 | 1HA03QP01 | 415V SWGR O/G MODULE # 1HA03RC | SOOT BLOWER MCC | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 72 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ06-01, ZZ99- |  | EPD | TRY
48 | 1HA | D03Q010 | 10.4.11 | 1HA03SP01 | 415V SWGR O/G MODULE # 1HA03RE | FAN LUB OIL HEATER FOR ID FAN - A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 391 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | PEM
49 | 1HA | D02C1.5 | 10.5.01 | 1HA03TC01 | 415V SWGR MOTOR MODULE # 1HA03RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 176 | 207 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC15-02, IC16-02, ZZ99- |  | EPD | EPD
50 | 1HA | D03Q010 | 10.4.11 | 1HA03TP01 | 415V SWGR MOTOR MODULE # 1HA03RF | PA FAN - A LUB OIL PUMP - 1 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 175 | 193 | 03.03.20 | 0 |  |  | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC15-02, IC16-02, ZZ99- |  | EPD | PEM
51 | 1HA | D02C1.5 | 10.5.01 | 1HA03WC01 | 415V SWGR MOTOR MODULE # 1HA03RI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 412 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, ZZ99- |  | EPD | EPD
52 | 1HA | D03Q010 | 10.4.11 | 1HA03WP01 | 415V SWGR MOTOR MODULE # 1HA03RI | SEAL AIR BLOWER MOTOR1 OF FGD INLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 419 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV13-L2, LV12-L3, LV11-L3, LV48-03, LV47-02, LV46-02, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IR21-02, ZZ99- |  | EPD | PEM
53 | 1HA | D02C1.5 | 10.5.01 | 1HA04BC01 | 415V SWGR MOTOR MODULE # 1HA04FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, BD27-02, BD26-02, BD25-02, ZZ99- |  | EPD | EPD
54 | 1HA | D03L2.5 | 10.4.26 | 1HA04BP01 | 415V SWGR MOTOR MODULE # 1HA04FB | AIR PREHEATER - A LUB. OIL PUMP - 1 GUIDE BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, BD27-02, BD26-02, BD25-02, ZZ99- |  | EPD | PEM
55 | 1HA | D03L2.5 | 10.4.26 | 1HA04CP01 | 415V SWGR O/G MODULE # 1HA04FC | FAN LUB OIL HEATER FOR FD FAN - A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 185 | 190 | 14.02.20 | DR1006_0001 |  |  | POWER SUPPLY (3kW) | XLPE-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC17-L2, IC19-L2, IC20-02, IC21-02, ZZ99- |  | EPD | PEM
56 | 1HA | D03L2.5 | 10.4.26 | 1HA04DP01 | 415V SWGR O/G MODULE # 1HA04FD | FAN LUB OIL HEATER FOR PA FAN - A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 175 | 188 | 14.02.20 | DR1006_0001 |  |  | POWER SUPPLY (3kW) | XLPE-CU UNARMOURED | LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR10-03, IC14-L2, IC15-02, IC16-02, ZZ99- |  | EPD | PEM
57 | 1HA | E04V0.5 | 10.7.02 | 1HA06AC01 | 415V SWGR I/C MODULE # 1HA06FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 83 | 28.09.2019 | DR0817_4798-4G-13 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV13-R4, LV12-R4, LV11-R4, LV10-R4, LV44-04, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
58 | 1HA | D02C1.5 | 10.5.01 | 1HA06AC02 | 415V SWGR I/C MODULE # 1HA06FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 77 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV13-L4, LV63-05, LV64-05, TR48-05, MR16-05, MV99-04, MV98-04, MV14-02, MV13-02, MV12-02, MV85-02, MV23-02, MV24-02, MV66-05, MV65-05, MV64-02, MV63-05, ZZ99- |  | EPD | EPD
59 | 1HA | E04V0.5 | 10.7.02 | 1HA06AC03 | 415V SWGR I/C MODULE # 1HA06FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 83 | 28.09.2019 | DR0817_4798-4G-13 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV13-R4, LV12-R4, LV11-R4, LV10-R4, LV44-04, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
60 | 1HA | E04V0.5 | 10.7.02 | 1HA07AC01 | 415V SWGR B/C MODULE # 1HA07FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 85 | 28.09.2019 | DR0817_4798-4G-13 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV13-R4, LV12-R4, LV11-R4, LV10-R4, LV44-04, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
61 | 1HA | E04V0.5 | 10.7.02 | 1HA07AC02 | 415V SWGR B/C MODULE # 1HA07FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 85 | 28.09.2019 | DR0817_4798-4G-13 |  |  | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | LV13-R4, LV12-R4, LV11-R4, LV10-R4, LV44-04, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
62 | 1HA | E04V0.5 | 10.7.02 | 1HA08AC01 | 415V SWGR I/C MODULE # 1HA08FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 68 | 84 | 28.09.2019 | DR0817_4798-4G-13 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV14-R4, LV13-R4, LV12-R4, LV11-R4, LV10-R4, LV44-04, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
63 | 1HA | D02C1.5 | 10.5.01 | 1HA08AC02 | 415V SWGR I/C MODULE # 1HA08FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV72-04, LR11-L3, MR05-L3, MV76-03, MV58-L2, MV69-03, ZZ99- |  | EPD | EPD
64 | 1HA | E04V0.5 | 10.7.02 | 1HA08AC03 | 415V SWGR I/C MODULE # 1HA08FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 68 | 84 | 28.09.2019 | DR0817_4798-4G-13 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV14-R4, LV13-R4, LV12-R4, LV11-R4, LV10-R4, LV44-04, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
65 | 1HA | D02C1.5 | 10.5.01 | 1HA09DC01 | 415V SWGR MOTOR MODULE # 1HA09FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, ZZ99- |  | EPD | EPD
66 | 1HA | D03Q010 | 10.4.11 | 1HA09DP01 | 415V SWGR MOTOR MODULE # 1HA09FD | SEAL AIR BLOWER MOTOR2 OF AIR HEATER - B SECONDARY AIR OUTLE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY (9.3kW) | XLPE-AL UNARMOURED | LV14-L1, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BR43-01, BD29-01, ZZ99- |  | EPD | PEM
67 | 1HA | D02C1.5 | 10.5.01 | 1HA09QC01 | 415V SWGR MOTOR MODULE # 1HA09RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 155 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, ZZ99- |  | EPD | EPD
68 | 1HA | D03L2.5 | 10.4.26 | 1HA09QP01 | 415V SWGR MOTOR MODULE # 1HA09RC | AIR PREHEATER - B LUB. OIL PUMP - 1 GUIDE BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, ZZ99- |  | EPD | PEM
69 | 1HA | D02C1.5 | 10.5.01 | 1HA10BC01 | 415V SWGR MOTOR MODULE # 1HA10FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, ZZ99- |  | EPD | EPD
70 | 1HA | D03Q010 | 10.4.11 | 1HA10BP01 | 415V SWGR MOTOR MODULE # 1HA10FB | PENT HOUSE FAN MOTOR - D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV14-L1, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BG23-01, BG24-01, BG22-01, BR22-01, BR23-01, BR24-01, BR25-01, BR26-01, BR27-01, BR28-01, BR29-01, ZZ99- |  | EPD | PEM
71 | 1HA | D02C1.5 | 10.5.01 | 1HA10PC01 | 415V SWGR MOTOR MODULE # 1HA10RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, ZZ99- |  | EPD | EPD
72 | 1HA | D03Q010 | 10.4.11 | 1HA10PP01 | 415V SWGR MOTOR MODULE # 1HA10RB | PENT HOUSE FAN MOTOR - B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 142 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV14-L1, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, ZZ99- |  | EPD | PEM
73 | 1HA | D03L2.5 | 10.4.26 | 1HA10QP01 | 415V SWGR O/G MODULE # 1HA10RC | FAN LUB OIL HEATER FOR PA FAN - B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 199 | [5 empty] | POWER SUPPLY (3kW) | XLPE-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM73-03, IR27-03, IM74-03, ZZ99- |  | EPD | PEM
74 | 1HA | D03L2.5 | 10.4.26 | 1HA10SP01 | 415V SWGR O/G MODULE # 1HA10RE | FAN LUB OIL HEATER FOR FD FAN - B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 201 | [5 empty] | POWER SUPPLY (3kW) | XLPE-CU UNARMOURED | LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM69-03, IR26-02, IM70-03, IM71-03, ZZ99- |  | EPD | PEM
75 | 1HA | D02C1.5 | 10.5.01 | 1HA11BC01 | 415V SWGR MOTOR MODULE # 1HA11FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 202 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM73-03, IR27-03, IM74-03, ZZ99- |  | EPD | EPD
76 | 1HA | D03Q010 | 10.4.11 | 1HA11BP01 | 415V SWGR MOTOR MODULE # 1HA11FB | PA FAN - B LUB OIL PUMP - 1 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 202 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM73-03, IR27-03, IM74-03, ZZ99- |  | EPD | PEM
77 | 1HA | D02C1.5 | 10.5.01 | 1HA11CC01 | 415V SWGR MOTOR MODULE # 1HA11FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 203 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM69-03, IR26-02, IM70-03, IM71-03, ZZ99- |  | EPD | EPD
78 | 1HA | D03Q010 | 10.4.11 | 1HA11CP01 | 415V SWGR MOTOR MODULE # 1HA11FC | FD FAN - B LUB OIL PUMP - 1 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 203 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM69-03, IR26-02, IM70-03, IM71-03, ZZ99- |  | EPD | PEM
79 | 1HA | D02C1.5 | 10.5.01 | 1HA11EC01 | 415V SWGR MOTOR MODULE # 1HA11FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 352 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | EPD
80 | 1HA | D03Q010 | 10.4.11 | 1HA11EP01 | 415V SWGR MOTOR MODULE # 1HA11FE | SEAL AIR BLOWER MOTOR2 OF ID FAN - B OUTLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 357 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV62-01, LV61-01, LV31-L1, LV30-L1, LV50-01, LV36-L1, LV37-L2, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IR21-02, IM57-02, IM58-02, IM59-02, ZZ99- |  | EPD | PEM
81 | 1HA | D02C1.5 | 10.5.01 | 1HA11FC01 | 415V SWGR MOTOR MODULE # 1HA11FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 305 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IC44-02, IR16-02, IC45-02, ZZ99- |  | EPD | EPD
82 | 1HA | D02L2.5 | 10.4.24 | 1HA11FC02 | 415V SWGR MOTOR MODULE # 1HA11FF | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 305 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IC44-02, IR16-02, IC45-02, ZZ99- |  | EPD | PEM
83 | 1HA | D03Q150 | 10.4.16 | 1HA11FP01 | 415V SWGR MOTOR MODULE # 1HA11FF | SEAL AIR FAN - B | 03C X 150 XLPE-Al FRLS ( 1.1 kV ) | 300 | [5 empty] | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV13-L2, LV12-L2, LV11-L2, LV10-L2, LV44-01, LV76-01, LV79-01, LR10-R1, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IC07-R1, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IC33-02, IC34-02, IC38-02, IC39-02, IC40-02, IC44-01, IR16-01, IC45-01, ZZ99- |  | EPD | PEM
84 | 1HA | D02C1.5 | 10.5.01 | 1HA11PC01 | 415V SWGR MOTOR MODULE # 1HA11RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, ZZ99- |  | EPD | EPD
85 | 1HA | D03L2.5 | 10.4.26 | 1HA11PP01 | 415V SWGR MOTOR MODULE # 1HA11RB | AIR PREHEATER - B CLEANING DEVICE MOTOR - GAS OUT | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, ZZ99- |  | EPD | PEM
86 | 1HA | D03Q010 | 10.4.11 | 1HA11QP01 | 415V SWGR O/G MODULE # 1HA11RC | FAN LUB OIL HEATER FOR ID FAN - B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 347 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | PEM
87 | 1HA | D02C1.5 | 10.5.01 | 1HA11RC01 | 415V SWGR MOTOR MODULE # 1HA11RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI16-02, BI15-02, ZZ99- |  | EPD | EPD
88 | 1HA | D03Q010 | 10.4.11 | 1HA11RP01 | 415V SWGR MOTOR MODULE # 1HA11RD | SEAL AIR BLOWER MOTOR2 OF SCR - B BYPASS DAMPER | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI16-02, BI15-02, ZZ99- |  | EPD | PEM
89 | 1HA | D02C1.5 | 10.5.01 | 1HA11SC01 | 415V SWGR MOTOR MODULE # 1HA11RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 440 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, ZZ99- |  | EPD | EPD
90 | 1HA | D03Q025 | 10.4.12 | 1HA11SP01 | 415V SWGR MOTOR MODULE # 1HA11RE | SEAL AIR BLOWER MOTOR2 OF FGD BYPASS DAMPER | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 444 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV62-01, LV61-01, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, ZZ99- |  | EPD | PEM
91 | 1HA | D02C1.5 | 10.5.01 | 1HA11TC01 | 415V SWGR MOTOR MODULE # 1HA11RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 257 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IR33-02, IM81-02, IM82-02, IM83-02, ZZ99- |  | EPD | EPD
92 | 1HA | D03Q025 | 10.4.12 | 1HA11TP01 | 415V SWGR MOTOR MODULE # 1HA11RF | MILL - F LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 262 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV62-01, LV61-01, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM64-02, IM65-02, IM66-02, IM67-02, IM68-02, IM72-02, IM75-02, IR28-02, IM76-02, IM77-02, IM78-02, IR32-02, IM79-02, IM80-02, IR33-02, IM81-02, IM82-02, IM83-01, ZZ99- |  | EPD | PEM
93 | 1HA | D02C1.5 | 10.5.01 | 1HA11UC01 | 415V SWGR MOTOR MODULE # 1HA11RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 440 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, ZZ99- |  | EPD | EPD
94 | 1HA | D03Q010 | 10.4.11 | 1HA11UP01 | 415V SWGR MOTOR MODULE # 1HA11RG | SEAL AIR BLOWER MOTOR2 OF FGD INLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 444 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV62-01, LV61-01, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, ZZ99- |  | EPD | PEM
95 | 1HA | D02C1.5 | 10.5.01 | 1HA11VC01 | 415V SWGR MOTOR MODULE # 1HA11RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, ZZ99- |  | EPD | EPD
96 | 1HA | D03Q050 | 10.4.14 | 1HA11VP01 | 415V SWGR MOTOR MODULE # 1HA11RH | SEAL AIR BLOWER MOTOR2 OF AIR HEATER - B PRIMARY AIR OUTLET | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 156 | [5 empty] | POWER SUPPLY (22kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV13-L2, LV12-L2, LV11-L2, LV10-L2, LV44-01, LV76-01, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC09-01, ZZ99- |  | EPD | PEM
97 | 1HA | D03Q010 | 10.4.11 | 1HA12BP01 | 415V SWGR O/G MODULE # 1HA12FB | LUB OIL HEATER FOR MILL - F | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 258 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IR33-02, IM81-02, IM82-02, IM84-02, ZZ99- |  | EPD | PEM
98 | 1HA | D03Q010 | 10.4.11 | 1HA12CP01 | 415V SWGR O/G MODULE # 1HA12FC | LUB OIL HEATER FOR MILL - D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 283 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM93-02, ZZ99- |  | EPD | PEM
99 | 1HA | D03Q010 | 10.4.11 | 1HA12DP01 | 415V SWGR O/G MODULE # 1HA12FD | LUB OIL HEATER FOR MILL - B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 266 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-03, LV79-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IR14-02, IC35-03, IC36-03, ZZ99- |  | EPD | PEM
100 | 1HA | D02C1.5 | 10.5.01 | 1HA12EC01 | 415V SWGR MOTOR MODULE # 1HA12FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 342 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | EPD
101 | 1HA | D03Q025 | 10.4.12 | 1HA12EP01 | 415V SWGR MOTOR MODULE # 1HA12FE | ID FAN - B LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 342 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | PEM
102 | 1HA | D02C1.5 | 10.5.01 | 1HA12FC01 | 415V SWGR MOTOR MODULE # 1HA12FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 282 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM92-02, ZZ99- |  | EPD | EPD
103 | 1HA | D03Q025 | 10.4.12 | 1HA12FP01 | 415V SWGR MOTOR MODULE # 1HA12FF | MILL - D LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 286 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV62-01, LV61-01, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM64-02, IM65-02, IM66-02, IM67-02, IM68-02, IM72-02, IM75-02, IR28-02, IM76-02, IM77-02, IM78-02, IR32-02, IM79-02, IM80-02, IM85-02, IM86-02, IM87-02, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM92-01, ZZ99- |  | EPD | PEM
104 | 1HA | D02C1.5 | 10.5.01 | 1HA12GC01 | 415V SWGR MOTOR MODULE # 1HA12FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 397 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | EPD
105 | 1HA | D03Q010 | 10.4.11 | 1HA12GP01 | 415V SWGR MOTOR MODULE # 1HA12FG | SEAL AIR BLOWER MOTOR2 OF ID FAN - A OUTLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV62-01, LV61-01, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, IM44-03, IM45-03, ZZ99- |  | EPD | PEM
106 | 1HA | D02C1.5 | 10.5.01 | 1HA12HC01 | 415V SWGR MOTOR MODULE # 1HA12FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, ZZ99- |  | EPD | EPD
107 | 1HA | D03Q050 | 10.4.14 | 1HA12HP01 | 415V SWGR MOTOR MODULE # 1HA12FH | SEAL AIR BLOWER MOTOR2 OF AIR HEATER - A PRIMARY AIR OUTLET | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY (22kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV13-L2, LV12-L2, LV11-L2, LV10-L2, LV44-01, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC09-01, BC10-01, ZZ99- |  | EPD | PEM
108 | 1HA | D04Q010 | 10.4.22 | 1HA12PP01 | 415V SWGR O/G MODULE # 1HA12RB | SOOT BLOWER MCC | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 86 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LR05-01, CC92-01, CC89-01, CC71-02, QR03-L1, BQ20-L1, BQ19-L1, BQ06-01, BQ05-01, ZZ99- |  | EPD | TRY
109 | 1HA | D02C1.5 | 10.5.01 | 1HA12QC01 | 415V SWGR MOTOR MODULE # 1HA12RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 188 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB12-02, ZZ99- |  | EPD | EPD
110 | 1HA | D03Q010 | 10.4.11 | 1HA12QP01 | 415V SWGR MOTOR MODULE # 1HA12RC | SEAL AIR BLOWER MOTOR2 OF AIR HEATER - A SECONDARY AIR OUTLE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 191 | [5 empty] | POWER SUPPLY (9.3kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-02, BA15-02, BR39-01, BB12-01, ZZ99- |  | EPD | PEM
111 | 1HA | D02C1.5 | 10.5.01 | 1HA12RC01 | 415V SWGR MOTOR MODULE # 1HA12RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 188 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB13-02, ZZ99- |  | EPD | EPD
112 | 1HA | D03L2.5 | 10.4.26 | 1HA12RP01 | 415V SWGR MOTOR MODULE # 1HA12RD | AIR PREHEATER - B LUB. OIL PUMP - 1 SUPPORT BEARING | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 188 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR39-03, BB13-02, ZZ99- |  | EPD | PEM
113 | 1HA | D02C1.5 | 10.5.01 | 1HA12SC01 | 415V SWGR MOTOR MODULE # 1HA12RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 185 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, BI17-02, BI04-02, BI05-02, ZZ99- |  | EPD | EPD
114 | 1HA | D03Q010 | 10.4.11 | 1HA12SP01 | 415V SWGR MOTOR MODULE # 1HA12RE | SEAL AIR BLOWER MOTOR2 OF SCR - A BYPASS DAMPER | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 185 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, BI17-02, BI04-02, BI05-02, ZZ99- |  | EPD | PEM
115 | 1HA | D02C1.5 | 10.5.01 | 1HA12TC01 | 415V SWGR MOTOR MODULE # 1HA12RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 440 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV52-02, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, ZZ99- |  | EPD | EPD
116 | 1HA | D03Q025 | 10.4.12 | 1HA12TP01 | 415V SWGR MOTOR MODULE # 1HA12RF | SEAL AIR BLOWER MOTOR2 OF FGD OUTLET GATE | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 445 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV62-01, LV61-01, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, ZZ99- |  | EPD | PEM
117 | 1HA | D02C1.5 | 10.5.01 | 1HA12UC01 | 415V SWGR MOTOR MODULE # 1HA12RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 280 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV15-L4, LV14-L4, LV13-L4, LV12-L4, LV11-L4, LV48-04, LV23-L4, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IC07-L4, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IR15-02, IC41-03, IC42-03, ZZ99- |  | EPD | EPD
118 | 1HA | D03Q025 | 10.4.12 | 1HA12UP01 | 415V SWGR MOTOR MODULE # 1HA12RG | MILL - B LUB OIL PUMP - 1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 277 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | LV15-L1, LV14-L1, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IC07-L2, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IC33-02, IC34-02, IC38-02, IC39-02, IC40-02, IR15-02, IC41-02, IC42-01, ZZ99- |  | EPD | PEM
1 | 1HB | D03Q025 | 10.4.12 | 1HB01DP01 | 415V SWGR MODULE # 1HB01FD | ID FAN - A OUTLET GATE | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 389 | [5 empty] | POWER SUPPLY (7.6kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | PEM
2 | 1HB | D03L2.5 | 10.4.26 | 1HB01EP01 | 415V SWGR MODULE # 1HB01FE | AIR PREHEATER - A GAS OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (2.5kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
3 | 1HB | D03L2.5 | 10.4.26 | 1HB01QP01 | 415V SWGR MODULE # 1HB01RC | INLET ISOLATION VALVES FOR MILL-A (ASV-09) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 225 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
4 | 1HB | D03L2.5 | 10.4.26 | 1HB01RP01 | 415V SWGR MODULE # 1HB01RD | INLET ISOLATION VALVES FOR MILL-B (ASV-10) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
5 | 1HB | D03L2.5 | 10.4.26 | 1HB01SP01 | 415V SWGR MODULE # 1HB01RE | INLET ISOLATION VALVES FOR MILL-C (ASV-11) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 205 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
6 | 1HB | D03L2.5 | 10.4.26 | 1HB01TP01 | 415V SWGR MODULE # 1HB01RF | INLET ISOLATION VALVES FOR MILL-D (ASV-12) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
7 | 1HB | D03Q025 | 10.4.12 | 1HB01UP01 | 415V SWGR MODULE # 1HB01RG | ESP - A INLET GATE1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 204 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV42-01, LV24-R1, LV75-02, LV77-02, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC09-01, BC10-01, BC11-01, BC12-01, BC13-01, ZZ99- |  | EPD | PEM
8 | 1HB | D03L2.5 | 10.4.26 | 1HB01VP01 | 415V SWGR MODULE # 1HB01RH | INLET ISOLATION VALVES FOR MILL-E (ASV-13) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 191 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
9 | 1HB | D03Q025 | 10.4.12 | 1HB01WP01 | 415V SWGR MODULE # 1HB01RI | ESP - A INLET GATE2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 204 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV42-01, LV24-R1, LV75-02, LV77-02, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC09-01, BC10-01, BC11-01, BC12-01, BC13-01, ZZ99- |  | EPD | PEM
10 | 1HB | D03L2.5 | 10.4.26 | 1HB02BP01 | 415V SWGR MODULE # 1HB02FB | LDO RETURN LINE PCV ISOLATION VALVE (HJF75AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 582 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV28-L4, LV41-03, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, ZZ99- |  | EPD | PEM
11 | 1HB | D03L2.5 | 10.4.26 | 1HB02CP01 | 415V SWGR MODULE # 1HB02FC | PA FAN-A VANE REGN. (HFE01AA151) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA05-02, BA07-02, BA08-02, BA09-02, BR35-02, ZZ99- |  | EPD | PEM
12 | 1HB | D03L2.5 | 10.4.26 | 1HB02DP01 | 415V SWGR MODULE # 1HB02FD | PA FAN-B VANE REGN. (HFE02AA151) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-02, BA21-02, BA22-02, BA23-02, BR33-02, ZZ99- |  | EPD | PEM
13 | 1HB | D03L2.5 | 10.4.26 | 1HB02EP01 | 415V SWGR MODULE # 1HB02FE | FD FAN-A VANE REGN. (HLB01AA151) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 197 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA05-02, BA07-02, BA08-02, BA09-02, BR35-02, BA35-01, ZZ99- |  | EPD | PEM
14 | 1HB | D03L2.5 | 10.4.26 | 1HB02FP01 | 415V SWGR MODULE # 1HB02FF | FD FAN-B VANE REGN. (HLB02AA151) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 182 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-02, BA15-02, BR34-02, BA30-02, BA33-01, ZZ99- |  | EPD | PEM
15 | 1HB | D03L2.5 | 10.4.26 | 1HB02PP01 | 415V SWGR MODULE # 1HB02RB | ECO INLET ISOLATION INTEGRAL BYPASS VALVE (HAC10AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, ZZ99- |  | EPD | PEM
16 | 1HB | D03L2.5 | 10.4.26 | 1HB02QP01 | 415V SWGR MODULE # 1HB02RC | DRUM TO SAT LINK AIR VENT ISO. VALVE (HAN20AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP01-02, ZZ99- |  | EPD | PEM
17 | 1HB | D03L2.5 | 10.4.26 | 1HB02RP01 | 415V SWGR MODULE # 1HB02RD | RH INLET HEADER VENT ISOL. VALVE (HAN35AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP01-02, ZZ99- |  | EPD | PEM
18 | 1HB | D03L2.5 | 10.4.26 | 1HB02SP01 | 415V SWGR MODULE # 1HB02RE | RH OUTLET HEADER VENT ISOL. VALVE (HAN35AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP01-02, ZZ99- |  | EPD | PEM
19 | 1HB | D03L2.5 | 10.4.26 | 1HB03BP01 | 415V SWGR MODULE # 1HB03FB | AIR HEATER - A SECONDARY AIR OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (1.2kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
20 | 1HB | D03L2.5 | 10.4.26 | 1HB03CP01 | 415V SWGR MODULE # 1HB03FC | AIR HEATER - B SECONDARY AIR OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 176 | [5 empty] | POWER SUPPLY (1.2kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
21 | 1HB | D03L2.5 | 10.4.26 | 1HB03DP01 | 415V SWGR MODULE # 1HB03FD | AIR HEATER - A FGAS TRISECTOR INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 196 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA10-02, BA11-02, BA12-02, BR37-02, ZZ99- |  | EPD | PEM
22 | 1HB | D03L2.5 | 10.4.26 | 1HB03EP01 | 415V SWGR MODULE # 1HB03FE | AIR HEATER - B FGAS TRISECTOR INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 146 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BR38-02, ZZ99- |  | EPD | PEM
23 | 1HB | D03Q025 | 10.4.12 | 1HB03FP01 | 415V SWGR MODULE # 1HB03FF | ESP - B OUTLET GATE1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 360 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, ZZ99- |  | EPD | PEM
24 | 1HB | D03Q025 | 10.4.12 | 1HB03GP01 | 415V SWGR MODULE # 1HB03FG | ESP - B OUTLET GATE2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 360 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R3, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, ZZ99- |  | EPD | PEM
25 | 1HB | D03Q095 | 10.4.15 | 1HB03IP01 | 415V SWGR MODULE # 1HB03FI | ID FAN - A INLET GATE | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 401 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, IM44-03, IM45-03, ZZ99- |  | EPD | PEM
26 | 1HB | D03L2.5 | 10.4.26 | 1HB03PP01 | 415V SWGR MODULE # 1HB03RB | ECONOMIZER - B BYPASS BIPLANE DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 152 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH10-02, ZZ99- |  | EPD | PEM
27 | 1HB | D03L2.5 | 10.4.26 | 1HB03QP01 | 415V SWGR MODULE # 1HB03RC | ECONOMIZER - A BYPASS BIPLANE CONTROL DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 177 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH02-02, ZZ99- |  | EPD | PEM
28 | 1HB | D03L2.5 | 10.4.26 | 1HB03RP01 | 415V SWGR MODULE # 1HB03RD | ECONOMIZER - B BYPASS BIPLANE CONTROL DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 152 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH10-02, ZZ99- |  | EPD | PEM
29 | 1HB | D03L2.5 | 10.4.26 | 1HB03SP01 | 415V SWGR MODULE # 1HB03RE | RH START UP VENT ISOL. VALVE (HAJ35AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 184 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, BO08-02, BO09-02, BR72-02, BP09-02, ZZ99- |  | EPD | PEM
30 | 1HB | D03L2.5 | 10.4.26 | 1HB03TP01 | 415V SWGR MODULE # 1HB03RF | DRUM AIR VENT ISO. VALVE-LEFT (HAN15AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP01-02, ZZ99- |  | EPD | PEM
31 | 1HB | D03L2.5 | 10.4.26 | 1HB04BP01 | 415V SWGR MODULE # 1HB04FB | SH EXTN SIDE WALL OUTLET PIPE VENT ISO. VALVE-LEFT (HAN20AA0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP01-02, ZZ99- |  | EPD | PEM
32 | 1HB | D03L2.5 | 10.4.26 | 1HB04CP01 | 415V SWGR MODULE # 1HB04FC | SH EXTN SIDE WALL OUTLET PIPE VENT ISO. VALVE-RIGHT (HAN20AA | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP01-02, ZZ99- |  | EPD | PEM
33 | 1HB | D03L2.5 | 10.4.26 | 1HB04DP01 | 415V SWGR MODULE # 1HB04FD | PLATEN SH INLET HEADER DRAIN ISO. VALVE (HAN20AA005) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 179 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, BO08-02, BO09-02, BR72-02, BP09-02, ZZ99- |  | EPD | PEM
34 | 1HB | D03L2.5 | 10.4.26 | 1HB04EP01 | 415V SWGR MODULE # 1HB04FE | PLATEN TO FINAL SH LINK VENT ISOLATION VALVE (HAN20AA006) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 179 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, BO08-02, BO09-02, BR72-02, BP09-02, ZZ99- |  | EPD | PEM
35 | 1HB | D03Q010 | 10.4.11 | 1HB04FP01 | 415V SWGR MODULE # 1HB04FF | SH START UP VENT INCHING VALVE (HAH20AA051) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 158 | [5 empty] | POWER SUPPLY (5.2kW) | XLPE-AL UNARMOURED | LV28-R1, LV42-01, LV24-R1, LV75-02, LV77-02, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, BO05-01, BR71-01, BR69-01, BO08-01, BO09-01, BR72-01, BP09-01, ZZ99- |  | EPD | PEM
36 | 1HB | D03Q010 | 10.4.11 | 1HB04GP01 | 415V SWGR MODULE # 1HB04FG | PA FAN - A OUTLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 148 | 195 | 9.03.20 | 20 |  |  | POWER SUPPLY (4.8kW) | XLPE-AL UNARMOURED | LV28-R1, LV42-01, LV24-R1, LV75-02, LV77-02, LR10-L2, IC01-L2, IC02-L2, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR16-01, BA01-01, BA02-01, BA03-01, BA04-01, BA05-01, BA06-01, ZZ99- |  | EPD | PEM
37 | 1HB | D03Q050 | 10.4.14 | 1HB04IP01 | 415V SWGR MODULE # 1HB04FI | ID FAN - B INLET GATE | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 336 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IR21-02, IM57-02, IM58-02, IM59-02, ZZ99- |  | EPD | PEM
38 | 1HB | D03Q010 | 10.4.11 | 1HB04UP01 | 415V SWGR MODULE # 1HB04RG | PA FAN - B OUTLET GATE | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 121 | [5 empty] | POWER SUPPLY (4.8kW) | XLPE-AL UNARMOURED | LV28-R1, LV42-01, LV24-R1, LV75-02, LV77-02, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA20-01, BA24-01, ZZ99- |  | EPD | PEM
39 | 1HB | D03Q010 | 10.4.11 | 1HB04WP01 | 415V SWGR MODULE # 1HB04RI | ID FAN-A INLET CONTROL DAMPER (HNC01AA151) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 401 | [5 empty] | POWER SUPPLY (4kW) | XLPE-AL UNARMOURED | LV28-L4, LV41-03, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM45-03, ZZ99- |  | EPD | PEM
40 | 1HB | D03L2.5 | 10.4.26 | 1HB05BP01 | 415V SWGR MODULE # 1HB05FB | RH START UP VENT INCHING VALVE (HAJ35AA051) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 179 | [5 empty] | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, BO08-02, BO09-02, BR72-02, BP09-02, ZZ99- |  | EPD | PEM
41 | 1HB | D03L2.5 | 10.4.26 | 1HB05CP01 | 415V SWGR MODULE # 1HB05FC | EMERGENCY DRAIN ISO. VALVE (HAN15AA004) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | 108 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, ZZ99- |  | EPD | PEM
42 | 1HB | D03L2.5 | 10.4.26 | 1HB05DP01 | 415V SWGR MODULE # 1HB05FD | CONTINUOUS BLOWDOWN ISO. VALVE (HAN15AA005) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | 105 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, ZZ99- |  | EPD | PEM
43 | 1HB | D03L2.5 | 10.4.26 | 1HB05EP01 | 415V SWGR MODULE # 1HB05FE | CONTINUOUS BLOWDOWN ISO. VALVE (HAN15AA006) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | 102 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L6, IC02-L6, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, ZZ99- |  | EPD | PEM
44 | 1HB | D03Q010 | 10.4.11 | 1HB05FP01 | 415V SWGR MODULE # 1HB05FF | ID FAN-B INLET CONTROL DAMPER (HNC02AA151) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 336 | [5 empty] | POWER SUPPLY (4kW) | XLPE-AL UNARMOURED | LV28-L4, LV41-03, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, IM57-03, IM58-03, IM59-03, ZZ99- |  | EPD | PEM
45 | 1HB | D03L2.5 | 10.4.26 | 1HB05GP01 | 415V SWGR MODULE # 1HB05FG | SCHAPH- A FCV-BYPASS VALVE (ASV-06) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 187 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA10-02, BA11-02, BA12-02, BR37-02, ZZ99- |  | EPD | PEM
46 | 1HB | D03Q095 | 10.4.15 | 1HB05IP01 | 415V SWGR MODULE # 1HB05FI | FGD INLET GATE | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 397 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IR21-02, ZZ99- |  | EPD | PEM
47 | 1HB | D03L2.5 | 10.4.26 | 1HB05PP01 | 415V SWGR MODULE # 1HB05RB | SH ERV ISOLATION VALVE-LEFT (LBA25AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, ZZ99- |  | EPD | PEM
48 | 1HB | D03L2.5 | 10.4.26 | 1HB05QP01 | 415V SWGR MODULE # 1HB05RC | SH ERV ISOLATION VALVE-RIGHT (LBA25AA003) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 155 | [5 empty] | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, ZZ99- |  | EPD | PEM
49 | 1HB | D03L2.5 | 10.4.26 | 1HB05RP01 | 415V SWGR MODULE # 1HB05RD | SH ERV ISOLATION VALVE-RIGHT (LBA25AA005) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 155 | [5 empty] | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, ZZ99- |  | EPD | PEM
50 | 1HB | D03L2.5 | 10.4.26 | 1HB05SP01 | 415V SWGR MODULE # 1HB05RE | RH ERV ISOLATION VALVE-LEFT (LBB50AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 183 | [5 empty] | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, ZZ99- |  | EPD | PEM
51 | 1HB | D03L2.5 | 10.4.26 | 1HB05UP01 | 415V SWGR MODULE # 1HB05RG | SCHAPH- B FCV-BYPASS VALVE (ASV-05) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BR38-02, ZZ99- |  | EPD | PEM
52 | 1HB | D03L2.5 | 10.4.26 | 1HB06BP01 | 415V SWGR MODULE # 1HB06FB | DOWNCOMER INTERMITTANT BLOW DOWN-ISO. VALVE (HAN15AA003) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BR31-02, ZZ99- |  | EPD | PEM
53 | 1HB | D03L2.5 | 10.4.26 | 1HB06CP01 | 415V SWGR MODULE # 1HB06FC | DOWNCOMER INTERMITTANT BLOW DOWN-INCHING VALVE (HAN15AA051) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BR31-02, ZZ99- |  | EPD | PEM
54 | 1HB | D03L2.5 | 10.4.26 | 1HB06DP01 | 415V SWGR MODULE # 1HB06FD | EMERGENCY DRAIN INCHING VALVE (HAN15AA052) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | 110 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, ZZ99- |  | EPD | PEM
55 | 1HB | D03L2.5 | 10.4.26 | 1HB06EP01 | 415V SWGR MODULE # 1HB06FE | RAD. ROOF SH OUTLET HDR VENT ISO. VALVE (HAN20AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, ZZ99- |  | EPD | PEM
56 | 1HB | D03L2.5 | 10.4.26 | 1HB06GP01 | 415V SWGR MODULE # 1HB06FG | SCR - A INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 187 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, BI17-02, BI04-02, BI05-02, ZZ99- |  | EPD | PEM
57 | 1HB | D03Q095 | 10.4.15 | 1HB06IP01 | 415V SWGR MODULE # 1HB06FI | FGD OUTLET GATE | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 397 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-01, IR17-02, IM01-02, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IR21-02, ZZ99- |  | EPD | PEM
58 | 1HB | D03L2.5 | 10.4.26 | 1HB06PP01 | 415V SWGR MODULE # 1HB06RB | BACKPASS SCW DRAIN REG. VALVE-REAR (HAN20AA052) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | 110 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, ZZ99- |  | EPD | PEM
59 | 1HB | D03L2.5 | 10.4.26 | 1HB06QP01 | 415V SWGR MODULE # 1HB06RC | RH SPRAY WATER ISO. VALVE BYPASS LINE -LEFT (LAE40AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
60 | 1HB | D03L2.5 | 10.4.26 | 1HB06RP01 | 415V SWGR MODULE # 1HB06RD | RH SPRAY WATER ISO. VALVE MAIN LINE -LEFT (LAE40AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
61 | 1HB | D03L2.5 | 10.4.26 | 1HB06SP01 | 415V SWGR MODULE # 1HB06RE | RH SPRAY WATER ISO. VALVE MAIN LINE -RIGHT (LAE40AA003) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
62 | 1HB | D03L2.5 | 10.4.26 | 1HB06UP01 | 415V SWGR MODULE # 1HB06RG | SCR - B INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 169 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI16-02, BI15-02, ZZ99- |  | EPD | PEM
63 | 1HB | D03L2.5 | 10.4.26 | 1HB06VP01 | 415V SWGR MODULE # 1HB06RH | SCR - A OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 192 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, BI17-02, BI04-02, BI05-02, BI06-02, ZZ99- |  | EPD | PEM
64 | 1HB | D03L2.5 | 10.4.26 | 1HB07BP01 | 415V SWGR MODULE # 1HB07FB | SCAPH - A INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 192 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA10-02, BA11-02, BA12-02, BA13-02, ZZ99- |  | EPD | PEM
65 | 1HB | D03L2.5 | 10.4.26 | 1HB07CP01 | 415V SWGR MODULE # 1HB07FC | SCAPH - B INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 148 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, ZZ99- |  | EPD | PEM
66 | 1HB | D03L2.5 | 10.4.26 | 1HB07DP01 | 415V SWGR MODULE # 1HB07FD | SCAPH - A OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 185 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA10-02, BA11-02, BA12-02, BR37-02, ZZ99- |  | EPD | PEM
67 | 1HB | D03L2.5 | 10.4.26 | 1HB07EP01 | 415V SWGR MODULE # 1HB07FE | SCAPH - B OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BR38-02, ZZ99- |  | EPD | PEM
68 | 1HB | D03L2.5 | 10.4.26 | 1HB07FP01 | 415V SWGR MODULE # 1HB07FF | SCR - B OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI16-02, BI15-02, BI14-02, ZZ99- |  | EPD | PEM
69 | 1HB | D03L2.5 | 10.4.26 | 1HB07GP01 | 415V SWGR MODULE # 1HB07FG | FD FAN - A OUTLET GATE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 187 | 190 | 04.03.20 | DR2450_N-466 |  |  | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-L4, LV75-03, LR06-03, CC91-03, CC83-03, CC84-03, CC86-03, CC87-02, CC52-03, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA05-02, BA07-02, BA08-02, BA09-02, ZZ99- |  | EPD | PEM
70 | 1HB | D03L2.5 | 10.4.26 | 1HB07PP01 | 415V SWGR MODULE # 1HB07RB | SCAPH - B BYPASS DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 180 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-03, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA10-02, BA11-02, BA12-02, BR37-02, ZZ99- |  | EPD | PEM
71 | 1HB | D03L2.5 | 10.4.26 | 1HB07QP01 | 415V SWGR MODULE # 1HB07RC | AIR HEATER - A PRIMARY AIR INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-03, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA10-02, BA11-02, BA12-02, BR37-02, ZZ99- |  | EPD | PEM
72 | 1HB | D03L2.5 | 10.4.26 | 1HB07RP01 | 415V SWGR MODULE # 1HB07RD | AIR HEATER - B PRIMARY AIR INLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 146 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-R3, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BR38-02, ZZ99- |  | EPD | PEM
73 | 1HB | D03L2.5 | 10.4.26 | 1HB07SP01 | 415V SWGR MODULE # 1HB07RE | AIR HEATER - A PRIMARY AIR OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 195 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-03, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
74 | 1HB | D03L2.5 | 10.4.26 | 1HB07VP01 | 415V SWGR MODULE # 1HB07RH | SH START UP VENT ISO VALVE (HAH20AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, BO08-02, BO09-02, BR72-02, BP09-02, ZZ99- |  | EPD | PEM
75 | 1HB | D03L2.5 | 10.4.26 | 1HB08BP01 | 415V SWGR MODULE # 1HB08FB | CBD TANK LCV-BYPASS VALVE (CBD-03) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, ZZ99- |  | EPD | PEM
76 | 1HB | D03L2.5 | 10.4.26 | 1HB08CP01 | 415V SWGR MODULE # 1HB08FC | CONTINUOUS BLOWDOWN IINCHING VALVE (HAN15AA053) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, ZZ99- |  | EPD | PEM
77 | 1HB | D03L2.5 | 10.4.26 | 1HB08DP01 | 415V SWGR MODULE # 1HB08FD | CONTINUOUS BLOWDOWN IINCHING VALVE (HAN15AA054) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, ZZ99- |  | EPD | PEM
78 | 1HB | D03L2.5 | 10.4.26 | 1HB08GP01 | 415V SWGR MODULE # 1HB08FG | SH SPRAY WATER ISO. VALVE MAIN LINE -LEFT (LAE30AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
79 | 1HB | D03L2.5 | 10.4.26 | 1HB08UP01 | 415V SWGR MODULE # 1HB08RG | SH SPRAY WATER ISO. VALVE MAIN LINE -RIGHT (LAE30AA003) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
80 | 1HB | D03L2.5 | 10.4.26 | 1HB08VP01 | 415V SWGR MODULE # 1HB08RH | SH SPRAY WATER ISO. VALVE BYPASS LINE -RIGHT (LAE30AA004) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
81 | 1HB | D03Q025 | 10.4.12 | 1HB09DP01 | 415V SWGR MODULE # 1HB09FD | ESP - B INLET GATE1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 213 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV42-01, LV24-R1, LV75-02, LR06-01, CC91-01, CC83-01, CC84-01, CC86-02, CC87-01, CC52-01, CC71-02, CR01-L1, IC01-L3, IC02-L3, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC09-01, BC10-01, BC11-01, BC12-01, BC13-01, ZZ99- |  | EPD | PEM
82 | 1HB | D03L2.5 | 10.4.26 | 1HB09EP01 | 415V SWGR MODULE # 1HB09FE | INLET ISOLATION VALVES FOR MILL-F (ASV-14) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 197 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
83 | 1HB | D03Q025 | 10.4.12 | 1HB09FP01 | 415V SWGR MODULE # 1HB09FF | ESP - B INLET GATE1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 218 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV42-01, LV24-R1, LV75-02, LR06-01, CC91-01, CC83-01, CC84-01, CC86-02, CC87-01, CC52-01, CC71-02, CR01-L1, IC01-L3, IC02-L3, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR17-01, BC01-01, BC02-01, BC03-01, BC29-01, BC30-01, BC31-01, BC11-01, BC12-01, BC13-01, ZZ99- |  | EPD | PEM
84 | 1HB | D03L2.5 | 10.4.26 | 1HB09PP01 | 415V SWGR MODULE # 1HB09RB | BUNKER - A OUTLET GATE (HFB01AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 220 | [5 empty] | POWER SUPPLY (1.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
85 | 1HB | D03L2.5 | 10.4.26 | 1HB09QP01 | 415V SWGR MODULE # 1HB09RC | BUNKER - AB OUTLET GATE (HFB02AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 210 | [5 empty] | POWER SUPPLY (1.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
86 | 1HB | D03L2.5 | 10.4.26 | 1HB09RP01 | 415V SWGR MODULE # 1HB09RD | BUNKER - C OUTLET GATE (HFB03AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (1.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC09-02, BC10-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | EPD | PEM
87 | 1HB | D03L2.5 | 10.4.26 | 1HB09SP01 | 415V SWGR MODULE # 1HB09RE | BUNKER - D OUTLET GATE (HFB04AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 177 | [5 empty] | POWER SUPPLY (1.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
88 | 1HB | D03L2.5 | 10.4.26 | 1HB09TP01 | 415V SWGR MODULE # 1HB09RF | BUNKER - E OUTLET GATE (HFB05AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 187 | [5 empty] | POWER SUPPLY (1.3kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
89 | 1HB | D03Q025 | 10.4.12 | 1HB09UP01 | 415V SWGR MODULE # 1HB09RG | ESP - A OUTLET GATE1 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 370 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R4, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, ZZ99- |  | EPD | PEM
90 | 1HB | D03Q025 | 10.4.12 | 1HB09WP01 | 415V SWGR MODULE # 1HB09RI | ESP - A OUTLET GATE2 | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 370 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R4, IM32-R3, IM33-R3, IR31-R2, IM34-R3, IM35-R3, IM36-R3, IM37-R3, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IM51-02, IM52-02, IM53-02, ZZ99- |  | EPD | PEM
91 | 1HB | D03L2.5 | 10.4.26 | 1HB10BP01 | 415V SWGR MODULE # 1HB10FB | SH ERV ISOLATION VALVE-RIGHT BYPASS (LBA25AA004) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, ZZ99- |  | EPD | PEM
92 | 1HB | D03L2.5 | 10.4.26 | 1HB10CP01 | 415V SWGR MODULE # 1HB10FC | SH ERV ISOLATION VALVE BYPASS-RIGHT (LBA25AA006) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, ZZ99- |  | EPD | PEM
93 | 1HB | D03L2.5 | 10.4.26 | 1HB10DP01 | 415V SWGR MODULE # 1HB10FD | RH ERV ISOLATION VALVE BYPASS-LEFT (LBB50AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, BR21-04, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, ZZ99- |  | EPD | PEM
94 | 1HB | D03L2.5 | 10.4.26 | 1HB10EP01 | 415V SWGR MODULE # 1HB10FE | RH ERV ISOLATION VALVE BYPASS-RIGHT (LBB50AA004) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 145 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-R3, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, ZZ99- |  | EPD | PEM
95 | 1HB | D03L2.5 | 10.4.26 | 1HB10PP01 | 415V SWGR MODULE # 1HB10RB | LDO FCV ISOLATION VALVE FOR MAIN CV (HJF80AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 582 | [5 empty] | POWER SUPPLY (0.09kW) | XLPE-CU UNARMOURED | LV28-L4, LV41-03, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, ZZ99- |  | EPD | PEM
96 | 1HB | D03L2.5 | 10.4.26 | 1HB10QP01 | 415V SWGR MODULE # 1HB10RC | LDO FCV ISOLATION VALVE FOR STANDBY CV (HJF82AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 582 | [5 empty] | POWER SUPPLY (0.09kW) | XLPE-CU UNARMOURED | LV28-L4, LV41-03, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, ZZ99- |  | EPD | PEM
97 | 1HB | D03L2.5 | 10.4.26 | 1HB10RP01 | 415V SWGR MODULE # 1HB10RD | SPRAY TO IBD TANK (IBD-06) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 131 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV28-L4, LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, ZZ99- |  | EPD | PEM
98 | 1HB | D03L2.5 | 10.4.26 | 1HB10SP01 | 415V SWGR MODULE # 1HB10RE | FINAL SH OUTLET HEADER DRAIN REG. VALVE (HAN20AA054) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 98 | 108 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV28-L4, LV42-03, LV24-R3, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, ZZ99- |  | EPD | PEM
99 | 1HB | D03Q025 | 10.4.12 | 1HB10UP01 | 415V SWGR MODULE # 1HB10RG | ID FAN - B OUTLET GATE | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 350 | [5 empty] | POWER SUPPLY (7.6kW) | XLPE-AL UNARMOURED | LV28-R1, LV41-01, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R4, IM32-R4, IM33-R4, IR31-R2, IM34-R4, IM35-R4, IM36-R4, IM37-R4, IR21-02, IM57-02, IM58-02, IM59-02, ZZ99- |  | EPD | PEM
100 | 1HB | D03L2.5 | 10.4.26 | 1HB11BP01 | 415V SWGR MODULE # 1HB11FB | AIR PREHEATER - B GAS OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | POWER SUPPLY (2.5kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
101 | 1HB | D03L2.5 | 10.4.26 | 1HB11CP01 | 415V SWGR MODULE # 1HB11FC | BUNKER - F OUTLET GATE (HFB06AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (1.3kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
102 | 1HB | D03L2.5 | 10.4.26 | 1HB11DP01 | 415V SWGR MODULE # 1HB11FD | ECONOMIZER - A BYPASS BIPLANE DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, BR21-04, BG01-02, BG02-02, BG03-02, BR49-02, BH02-02, ZZ99- |  | EPD | PEM
103 | 1HB | D03L2.5 | 10.4.26 | 1HB11EP01 | 415V SWGR MODULE # 1HB11FE | DRUM AIR VENT ISO. VALVE-RIGHT (HAN15AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BP07-02, ZZ99- |  | EPD | PEM
104 | 1HB | D03L2.5 | 10.4.26 | 1HB11FP01 | 415V SWGR MODULE # 1HB11FF | FINAL SH OUTLET HEADER VENT ISOL. VALVE (HAN20AA007) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, ZZ99- |  | EPD | PEM
105 | 1HB | D03L2.5 | 10.4.26 | 1HB11QP01 | 415V SWGR MODULE # 1HB11RC | BACKPASS SCW DRAIN REG. VALVE-FRONT (HAN20AA053) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 90 | 102 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, ZZ99- |  | EPD | PEM
106 | 1HB | D03L2.5 | 10.4.26 | 1HB11RP01 | 415V SWGR MODULE # 1HB11RD | RH ERV ISOLATION VALVE-RIGHT (LBB50AA003) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | POWER SUPPLY (1.02kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, ZZ99- |  | EPD | PEM
107 | 1HB | D03L2.5 | 10.4.26 | 1HB11UP01 | 415V SWGR MODULE # 1HB11RG | FD FAN - B OUTLET GATE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 134 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-02, BA21-02, BA22-02, BA23-02, ZZ99- |  | EPD | PEM
108 | 1HB | D03L2.5 | 10.4.26 | 1HB12BP01 | 415V SWGR MODULE # 1HB12FB | LDO RETURN LINE PCV ISOLATION VALVE (HJF73AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 577 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV27-L4, LV41-03, LV40-05, IR17-05, IM01-05, IM02-R6, IM94-R5, IM95-R5, IM96-R5, IM11-R6, IM12-R6, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IR21-03, ZZ99- |  | EPD | PEM
109 | 1HB | D03L2.5 | 10.4.26 | 1HB12CP01 | 415V SWGR MODULE # 1HB12FC | SH ERV ISOLATION VALVE BYPASS-LEFT (LBA25AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, BR21-04, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, ZZ99- |  | EPD | PEM
110 | 1HB | D03Q025 | 10.4.12 | 1HB12DP01 | 415V SWGR MODULE # 1HB12FD | ECO INLET ISO. VALVE (HAC10AA001) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV27-R1, LV26-R1, LV25-R1, LV75-02, LV77-02, LR10-L2, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BE05-01, BE06-01, BE07-01, BR45-01, ZZ99- |  | EPD | PEM
111 | 1HB | D03L2.5 | 10.4.26 | 1HB12EP01 | 415V SWGR MODULE # 1HB12FE | ECO INLET ISOLATION INTEGRAL BYPASS VALVE (HAC10AA003) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (0.11kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, ZZ99- |  | EPD | PEM
112 | 1HB | D03L2.5 | 10.4.26 | 1HB12PP01 | 415V SWGR MODULE # 1HB12RB | AIR HEATER - B PRIMARY AIR OUTLET DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  | EPD | PEM
113 | 1HB | D03L2.5 | 10.4.26 | 1HB12QP01 | 415V SWGR MODULE # 1HB12RC | SCAPH - A BYPASS DAMPER | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 132 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BR38-02, ZZ99- |  | EPD | PEM
114 | 1HB | D03L2.5 | 10.4.26 | 1HB12RP01 | 415V SWGR MODULE # 1HB12RD | RH SPRAY WATER ISO. VALVE BYPASS LINE -RIGHT (LAE40AA004) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
115 | 1HB | D03L2.5 | 10.4.26 | 1HB12SP01 | 415V SWGR MODULE # 1HB12RE | RAD. ROOF SH INLET HDR DRAIN ISO VALVE (HAN20AA051) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 165 | 90 | 16.02.20 | DR1006_0001 |  |  | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-04, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, ZZ99- |  | EPD | PEM
116 | 1HB | D03L2.5 | 10.4.26 | 1HB12UP01 | 415V SWGR MODULE # 1HB12RG | SH SPRAY WATER ISO. VALVE BYPASS LINE -LEFT (LAE30AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV27-L4, LV26-L4, LV25-L4, LV75-02, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99- |  | EPD | PEM
1 | 1KA | D02C1.5 | 10.5.01 | 1KA01BC01 | 415V SWGR MOTOR MODULE # 1KA01FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
2 | 1KA | D03L2.5 | 10.4.26 | 1KA01BP01 | 415V SWGR MOTOR MODULE # 1KA01FB | MOTOR FOR RE-CIRCUL. PUMP - 1 (MAJ63AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HWR
3 | 1KA | D02C1.5 | 10.5.01 | 1KA01CC01 | 415V SWGR MOTOR MODULE # 1KA01FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV05-L4, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, ZZ99- |  | EPD | EPD
4 | 1KA | D02L2.5 | 10.4.24 | 1KA01CC02 | 415V SWGR MOTOR MODULE # 1KA01FC | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | LV06-L4, LV05-L4, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, ZZ99- |  | EPD | HWR
5 | 1KA | D03Q095 | 10.4.15 | 1KA01CP01 | 415V SWGR MOTOR MODULE # 1KA01FC | AUXILARY OIL PUMP - 1 (MAV22AP001) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 61 | 80 | 02.03.20 | DR0822_0005 |  |  | POWER SUPPLY (75kW) | XLPE-AL UNARMOURED | LV06-L1, LV05-L1, LV04-L1, LV64-02, TR48-02, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, ZZ99- |  | EPD | HWR
6 | 1KA | D02C1.5 | 10.5.01 | 1KA01PC01 | 415V SWGR MOTOR MODULE # 1KA01RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG31-03, TR06-02, ZZ99- |  | EPD | EPD
7 | 1KA | D03L2.5 | 10.4.26 | 1KA01PP01 | 415V SWGR MOTOR MODULE # 1KA01RB | SEAL OIL VACUUM PUMP - 1 (MKW11AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV06-L4, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG31-03, TR06-02, ZZ99- |  | EPD | HWR
8 | 1KA | D02C1.5 | 10.5.01 | 1KA01QC01 | 415V SWGR MOTOR MODULE # 1KA01RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 55 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV05-L4, LV04-L4, LV64-05, TR25-05, TP55-02, TP56-02, TP57-02, ZZ99- |  | EPD | EPD
9 | 1KA | D03L2.5 | 10.4.26 | 1KA01QP01 | 415V SWGR MOTOR MODULE # 1KA01RC | CF REGEN UNIT PUMP (MAX05AP021) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 55 | [5 empty] | POWER SUPPLY (0.08kW) | XLPE-CU UNARMOURED | LV06-L4, LV05-L4, LV04-L4, LV64-05, TR25-05, TP55-02, TP56-02, TP57-02, ZZ99- |  | EPD | HWR
10 | 1KA | D02C1.5 | 10.5.01 | 1KA01RC01 | 415V SWGR MOTOR MODULE # 1KA01RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, ZZ99- |  | EPD | EPD
11 | 1KA | D03L2.5 | 10.4.26 | 1KA01RP01 | 415V SWGR MOTOR MODULE # 1KA01RD | COOLING FAN - 2 IN HPSU (MAX05AN012) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, ZZ99- |  | EPD | HWR
12 | 1KA | D02C1.5 | 10.5.01 | 1KA01TC01 | 415V SWGR MOTOR MODULE # 1KA01RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 123 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP44-02, ZZ99- |  | EPD | EPD
13 | 1KA | D03L2.5 | 10.4.26 | 1KA01TP01 | 415V SWGR MOTOR MODULE # 1KA01RF | GSC AIR EXHAUSTER - 1 (MAW80AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 123 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP44-02, ZZ99- |  | EPD | HWR
14 | 1KA | D02C1.5 | 10.5.01 | 1KA02BC01 | 415V SWGR MOTOR MODULE # 1KA02FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 161 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TP41-02, ZZ99- |  | EPD | EPD
15 | 1KA | D03L2.5 | 10.4.26 | 1KA02BP01 | 415V SWGR MOTOR MODULE # 1KA02FB | BRG EXHAUST FAN MOTOR - 1 (MKQ01AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 161 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TP41-02, ZZ99- |  | EPD | HWR
16 | 1KA | D02C1.5 | 10.5.01 | 1KA02EC01 | 415V SWGR MOTOR MODULE # 1KA02FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 61 | 76 | 03.03.20 | DR1150_17PA011786 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV05-L4, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, ZZ99- |  | EPD | EPD
17 | 1KA | D03L2.5 | 10.4.26 | 1KA02EP01 | 415V SWGR MOTOR MODULE # 1KA02FE | OIL VAPOUR EXTRACTOR - 1 (MAV82AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 61 | 85 | 04.03.20 | DR2450_N-466 |  |  | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV06-L4, LV05-L4, LV04-L4, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, ZZ99- |  | EPD | HWR
18 | 1KA | D03Q010 | 10.4.11 | 1KA02FP01 | 415V SWGR O/G MODULE # 1KA02FF | GAS DRIER - 1 REFREGERATION (MKG69BT001) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 154 | [5 empty] | POWER SUPPLY (3.75kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, ZZ99- |  | EPD | HWR
19 | 1KA | D02C1.5 | 10.5.01 | 1KA02GC01 | 415V SWGR MOTOR MODULE # 1KA02FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-R3, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | EPD
20 | 1KA | D03L2.5 | 10.4.26 | 1KA02GP01 | 415V SWGR MOTOR MODULE # 1KA02FG | CTRL FLUID - C CIR PUMP - 2 (MAX05AP012) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 72 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HWR
21 | 1KA | D02C1.5 | 10.5.01 | 1KA02QC01 | 415V SWGR MOTOR MODULE # 1KA02RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 148 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-R3, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, TP36-02, ZZ99- |  | EPD | EPD
22 | 1KA | D03Q025 | 10.4.12 | 1KA02QP01 | 415V SWGR MOTOR MODULE # 1KA02RC | CTRL FLUID PUMP - 1 HPSU (MAX05AP001) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 146 | [5 empty] | POWER SUPPLY (9.2kW) | XLPE-AL UNARMOURED | LV06-L1, LV05-L1, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP27-01, TP28-01, TP29-01, TP30-01, TP31-01, TP32-01, TP34-01, TP35-01, TR30-01, TP36-01, ZZ99- |  | EPD | HWR
23 | 1KA | D02C1.5 | 10.5.01 | 1KA03RC01 | 415V SWGR MOTOR MODULE # 1KA03RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
24 | 1KA | D03Q010 | 10.4.11 | 1KA03RP01 | 415V SWGR MOTOR MODULE # 1KA03RD | OIL SUPPLY UNIT - 2 OF HP BYPASS SYSTEM | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | HWR
25 | 1KA | E04V0.5 | 10.7.02 | 1KA04AC01 | 415V SWGR I/C MODULE # 1KA04FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 52 | 75 | 28.09.2019 | DR0817_4798-4G-34 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
26 | 1KA | D02C1.5 | 10.5.01 | 1KA04AC02 | 415V SWGR I/C MODULE # 1KA04FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV06-L4, LV07-L4, LV76-02, MR10-03, MA05-03, MV08-L2, MV26-L2, MV27-L2, MV44-L2, MV45-L2, MV46-L2, MV47-02, ZZ99- |  | EPD | EPD
27 | 1KA | E04V0.5 | 10.7.02 | 1KA04AC03 | 415V SWGR I/C MODULE # 1KA04FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 52 | 75 | 28.09.2019 | DR0817_4798-4G-34 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
28 | 1KA | E04V0.5 | 10.7.02 | 1KA05AC01 | 415V SWGR B/C MODULE # 1KA05FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 52 | 75 | 28.09.2019 | DR0817_4798-4G-34 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
29 | 1KA | E04V0.5 | 10.7.02 | 1KA05AC02 | 415V SWGR B/C MODULE # 1KA05FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 52 | 75 | 28.09.2019 | DR0817_4798-4G-34 |  |  | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
30 | 1KA | E04V0.5 | 10.7.02 | 1KA06AC01 | 415V SWGR I/C MODULE # 1KA06FA | DDCMIS # CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 52 | 75 | 28.09.2019 | DR0817_4798-4G-34 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
31 | 1KA | D02C1.5 | 10.5.01 | 1KA06AC02 | 415V SWGR I/C MODULE # 1KA06FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV06-L4, LV53-02, LV52-02, LV51-02, LV50-02, LV36-L4, LV72-04, LR11-L3, MR05-L3, MV76-03, MV77-03, MV49-02, ZZ99- |  | EPD | EPD
32 | 1KA | E04V0.5 | 10.7.02 | 1KA06AC03 | 415V SWGR I/C MODULE # 1KA06FA | DDCMIS # CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 52 | 75 | 28.09.2019 | DR0817_4798-4G-34 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | EPD | EDN
33 | 1KA | D02C1.5 | 10.5.01 | 1KA07BC01 | 415V SWGR MOTOR MODULE # 1KA07FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 52 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-R3, LV05-R3, LV04-R3, LV64-05, TR25-05, TP55-02, TP56-02, TP58-02, ZZ99- |  | EPD | EPD
34 | 1KA | D03Q010 | 10.4.11 | 1KA07BP01 | 415V SWGR MOTOR MODULE # 1KA07FB | CTRL FLUID PUMP - 2 HPSU (MAX05AP002) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (9.2kW) | XLPE-AL UNARMOURED | LV06-L1, LV05-L1, LV04-L1, LV64-02, TR25-01, TP55-01, TP56-01, TP58-01, ZZ99- |  | EPD | HWR
35 | 1KA | D02C1.5 | 10.5.01 | 1KA07PC01 | 415V SWGR MOTOR MODULE # 1KA07RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG31-03, TR06-02, TG32-02, TG33-02, ZZ99- |  | EPD | EPD
36 | 1KA | D03Q010 | 10.4.11 | 1KA07PP01 | 415V SWGR MOTOR MODULE # 1KA07RB | SEAL OIL PUMP - 1 (MKW11AP001) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 127 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV06-L1, LV07-L1, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG31-01, TR06-01, TG32-01, TG33-01, ZZ99- |  | EPD | HWR
37 | 1KA | D02C1.5 | 10.5.01 | 1KA07RC01 | 415V SWGR MOTOR MODULE # 1KA07RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | EPD
38 | 1KA | D03L2.5 | 10.4.26 | 1KA07RP01 | 415V SWGR MOTOR MODULE # 1KA07RD | LEAKAGE OIL RETURN PUMP (MAV85AP001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HWR
39 | 1KA | D02C1.5 | 10.5.01 | 1KA07UC01 | 415V SWGR MOTOR MODULE # 1KA07RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 145 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-R3, LV07-R3, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, TG39-02, TG41-02, TG42-02, TR08-02, ZZ99- |  | EPD | EPD
40 | 1KA | D03Q025 | 10.4.12 | 1KA07UP01 | 415V SWGR MOTOR MODULE # 1KA07RG | CO2 VAPORISER (MKG71AH001) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 142 | [5 empty] | POWER SUPPLY (18kW) | XLPE-AL UNARMOURED | LV06-L1, LV07-L1, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG36-01, TG37-01, TG38-01, TR07-01, TG39-01, TG41-01, TG42-01, TR08-01, ZZ99- |  | EPD | HWR
41 | 1KA | D02C1.5 | 10.5.01 | 1KA08QC01 | 415V SWGR MOTOR MODULE # 1KA08RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 123 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP44-02, ZZ99- |  | EPD | EPD
42 | 1KA | D03L2.5 | 10.4.26 | 1KA08QP01 | 415V SWGR MOTOR MODULE # 1KA08RC | GSC AIR EXHAUSTER - 2 (MAW80AN002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 123 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP44-02, ZZ99- |  | EPD | HWR
43 | 1KA | D02C1.5 | 10.5.01 | 1KA08RC01 | 415V SWGR MOTOR MODULE # 1KA08RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-R3, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | EPD
44 | 1KA | D03L2.5 | 10.4.26 | 1KA08RP01 | 415V SWGR MOTOR MODULE # 1KA08RD | CTRL FLUID - C CIR PUMP - 1 (MAX05AP011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 72 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR49-02, TG62-02, TR19-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HWR
45 | 1KA | D03L2.5 | 10.4.26 | 1KA08SP01 | 415V SWGR MOTOR MODULE # 1KA08RE | EXCITER SPACE HEATER (MKC71AH001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY (3kW) | XLPE-CU UNARMOURED | LV06-L4, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, ZZ99- |  | EPD | HWR
46 | 1KA | D02C1.5 | 10.5.01 | 1KA09BC01 | 415V SWGR MOTOR MODULE # 1KA09FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-R3, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TP41-02, ZZ99- |  | EPD | EPD
47 | 1KA | D03L2.5 | 10.4.26 | 1KA09BP01 | 415V SWGR MOTOR MODULE # 1KA09FB | BRG EXHAUST FAN MOTOR - 2 (MKQ02AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 161 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TP41-02, ZZ99- |  | EPD | HWR
48 | 1KA | D02C1.5 | 10.5.01 | 1KA09CC01 | 415V SWGR MOTOR MODULE # 1KA09FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-L4, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, ZZ99- |  | EPD | EPD
49 | 1KA | D03L2.5 | 10.4.26 | 1KA09CP01 | 415V SWGR MOTOR MODULE # 1KA09FC | SEAL OIL VACUUM PUMP - 2 (MKW12AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV06-L4, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, ZZ99- |  | EPD | HWR
50 | 1KA | D02C1.5 | 10.5.01 | 1KA09DC01 | 415V SWGR MOTOR MODULE # 1KA09FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
51 | 1KA | D03L2.5 | 10.4.26 | 1KA09DP01 | 415V SWGR MOTOR MODULE # 1KA09FD | MOTOR FOR RE-CIRCUL. PUMP - 2 (MAJ73AN001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HWR
52 | 1KA | D03Q010 | 10.4.11 | 1KA09EP01 | 415V SWGR O/G MODULE # 1KA09FE | GAS DRIER - 2 REFREGERATION (MKG69BT011) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 154 | [5 empty] | POWER SUPPLY (3.75kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, ZZ99- |  | EPD | HWR
53 | 1KA | D02C1.5 | 10.5.01 | 1KA09FC01 | 415V SWGR MOTOR MODULE # 1KA09FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
54 | 1KA | D03Q010 | 10.4.11 | 1KA09FP01 | 415V SWGR MOTOR MODULE # 1KA09FF | OIL SUPPLY UNIT - 1 OF HP BYPASS SYSTEM | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | HWR
55 | 1KA | D02C1.5 | 10.5.01 | 1KA09GC01 | 415V SWGR MOTOR MODULE # 1KA09FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 154 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV06-R3, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, ZZ99- |  | EPD | EPD
56 | 1KA | D03L2.5 | 10.4.26 | 1KA09GP01 | 415V SWGR MOTOR MODULE # 1KA09FG | COOLING FAN - 1 IN HPSU (MAX05AN011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, ZZ99- |  | EPD | HWR
1 | 1KB | D03L2.5 | 10.4.26 | 1KB01DP01 | 415V SWGR O/G MODULE # 1KB01FD | DC & LPH-1 BYPASS (CD-31) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV04-L4, LV05-L4, LV06-L3, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, ZZ99- |  | EPD | HYD
2 | 1KB | D03L2.5 | 10.4.26 | 1KB01PP01 | 415V SWGR O/G MODULE # 1KB01RB | EXTN. TO HPH-6 (EX-14) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TD01-02, TD02-02, TD04-02, TD05-02, ZZ99- |  | EPD | HYD
3 | 1KB | D03L2.5 | 10.4.26 | 1KB01QP01 | 415V SWGR O/G MODULE # 1KB01RC | MIN RECIRCULATION CV BYPASSS (CD-27) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-02, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP35-02, TP34-02, TP32-02, TP31-02, TP30-02, TP29-02, TP44-02, TP45-02, TP47-02, TP48-02, ZZ99- |  | EPD | HYD
4 | 1KB | D03L2.5 | 10.4.26 | 1KB01RP01 | 415V SWGR O/G MODULE # 1KB01RD | INTERCONNECTION TO EXISTING UNIT (AS-35) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 108 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD13-02, ZZ99- |  | EPD | HYD
5 | 1KB | D03L2.5 | 10.4.26 | 1KB01SP01 | 415V SWGR O/G MODULE # 1KB01RE | MAIN CONDENSATE 30% CV CD-11 U/S ISOL (CD-10) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV04-L3, LV05-L4, LV06-L3, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, ZZ99- |  | EPD | HYD
6 | 1KB | D03L2.5 | 10.4.26 | 1KB01TP01 | 415V SWGR O/G MODULE # 1KB01RF | EXTN. TO LPH-3 (EX-11) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP06-02, TP07-02, ZZ99- |  | EPD | HYD
7 | 1KB | D03Q010 | 10.4.11 | 1KB01UP01 | 415V SWGR O/G MODULE # 1KB01RG | BYP VLV FOR LEAK-OFF VLV (MAW55AA001) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | HYD
8 | 1KB | D03Q010 | 10.4.11 | 1KB01VP01 | 415V SWGR O/G MODULE # 1KB01RH | HPH-5 INLET (FD-7) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV02-L1, LV03-L1, LV64-01, TR25-01, TP55-01, TP54-01, TP52-02, TP49-02, TP03-02, TP05-01, TP06-01, TP07-01, ZZ99- |  | EPD | HYD
9 | 1KB | D03Q010 | 10.4.11 | 1KB01WP01 | 415V SWGR O/G MODULE # 1KB01RI | HPH-5 BYPASS (FD-8) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV02-L1, LV03-L1, LV64-01, TR25-01, TP55-01, TP54-01, TP52-02, TP49-02, TP03-02, TP05-01, TP10-01, TP11-01, TP12-01, ZZ99- |  | EPD | HYD
10 | 1KB | D03Q010 | 10.4.11 | 1KB02EP01 | 415V SWGR O/G MODULE # 1KB02FE | MAIN STEAM TO AUX PRDS CV BYPASS ISLN (AS-13) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 117 | [5 empty] | POWER SUPPLY (5.2kW) | XLPE-AL UNARMOURED | LV02-L1, LV03-L1, LV64-02, TR25-01, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TR28-01, TD16-01, TD12-01, TD10-01, TD09-01, ZZ99- |  | EPD | HYD
11 | 1KB | D03Q010 | 10.4.11 | 1KB02FP01 | 415V SWGR O/G MODULE # 1KB02FF | HPH-5 OUTLET (FD-9) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV02-L1, LV03-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-02, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, ZZ99- |  | EPD | HYD
12 | 1KB | D03L2.5 | 10.4.26 | 1KB02PP01 | 415V SWGR O/G MODULE # 1KB02RB | EXTN. TO DEAERATOR (EX-12) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (2.48kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TR41-02, TD35-02, TD36-02, TD37-02, TD38-02, ZZ99- |  | EPD | HYD
13 | 1KB | D03L2.5 | 10.4.26 | 1KB02RP01 | 415V SWGR O/G MODULE # 1KB02RD | MO BFV - DMCW PUMP - DISCHARGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV01-02, MR01-03, MV01-03, MV02-R1, MV98-04, MV14-02, MV13-02, MV12-02, MV86-02, MR18-03, MA04-02, TG21-02, TG18-02, ZZ99- |  | EPD | HYD
14 | 1KB | D03L2.5 | 10.4.26 | 1KB02SP01 | 415V SWGR O/G MODULE # 1KB02RE | RECIRCULATION ACROSS PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV04-L3, LV05-L4, LV06-L3, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, ZZ99- |  | EPD | HYD
15 | 1KB | D03L2.5 | 10.4.26 | 1KB02TP01 | 415V SWGR O/G MODULE # 1KB02RF | MS TO HC AUX STEAM PRDS LINE (AS-119) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, ZZ99- |  | EPD | HYD
16 | 1KB | D03L2.5 | 10.4.26 | 1KB02UP01 | 415V SWGR O/G MODULE # 1KB02RG | BYPASS VALVE FOR MS-1 (MS-3) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 188 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV63-05, LV13-L4, LV12-R3, LV11-L4, LV10-L4, LV09-L4, LV08-L4, LV76-04, LV79-03, LR10-R3, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BO02-02, BO03-02, ZZ99- |  | EPD | HYD
17 | 1KB | D03Q010 | 10.4.11 | 1KB02WP01 | 415V SWGR O/G MODULE # 1KB02RI | HPH-6 INLET (FD-10) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 88 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV02-L1, LV03-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-02, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, ZZ99- |  | EPD | HYD
18 | 1KB | D03L2.5 | 10.4.26 | 1KB03DP01 | 415V SWGR O/G MODULE # 1KB03FD | MO BFV - DMCW PUMP - DISCHARGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV01-02, MR01-03, MV01-03, MV02-R1, MV98-04, MV14-02, MV13-02, MV12-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, ZZ99- |  | EPD | HYD
19 | 1KB | D03Q010 | 10.4.11 | 1KB03GP01 | 415V SWGR O/G MODULE # 1KB03FG | CRH STEAM TO D/A PEGGING (CRH-5) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 117 | [5 empty] | POWER SUPPLY (5.2kW) | XLPE-AL UNARMOURED | LV02-R1, LV03-R1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP04-01, TR26-01, TR40-01, TD18-01, TD19-01, TD23-01, TD24-01, TR53-01, TD25-01, TD26-01, TD27-01, ZZ99- |  | EPD | HYD
20 | 1KB | D03L2.5 | 10.4.26 | 1KB03QP01 | 415V SWGR O/G MODULE # 1KB03RC | MS STRAINER DRAIN TO FLASH TANK (MS-105) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-06, TR48-05, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
21 | 1KB | D03L2.5 | 10.4.26 | 1KB03RP01 | 415V SWGR O/G MODULE # 1KB03RD | MS STRAINER DRAIN TO FLASH TANK (MS-106) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-06, TR48-05, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
22 | 1KB | D03L2.5 | 10.4.26 | 1KB03SP01 | 415V SWGR O/G MODULE # 1KB03RE | BYP VLV FOR SUPPLY VLV (MAW15AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
23 | 1KB | D03L2.5 | 10.4.26 | 1KB03TP01 | 415V SWGR O/G MODULE # 1KB03RF | WATER INJECTION BYP VLV-1 (MAN90AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
24 | 1KB | D03L2.5 | 10.4.26 | 1KB03UP01 | 415V SWGR O/G MODULE # 1KB03RG | WATER INJECTION BYP VLV-2 (MAN90AA002) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-06, TR25-05, TP55-02, TP56-02, TP57-02, ZZ99- |  | EPD | HYD
25 | 1KB | D03L2.5 | 10.4.26 | 1KB04CP01 | 415V SWGR O/G MODULE # 1KB04FC | DRN VLV BEF HP CV-2 (MAL12AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
26 | 1KB | D03L2.5 | 10.4.26 | 1KB04DP01 | 415V SWGR O/G MODULE # 1KB04FD | DRN VLV HP CASING (MAL22AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-06, TR25-05, TP55-02, TP56-02, TP58-02, ZZ99- |  | EPD | HYD
27 | 1KB | D03L2.5 | 10.4.26 | 1KB04EP01 | 415V SWGR O/G MODULE # 1KB04FE | DRN VLV BEF IP CV-1 (MAL26AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
28 | 1KB | D03L2.5 | 10.4.26 | 1KB04FP01 | 415V SWGR O/G MODULE # 1KB04FF | DRN VLV BEF IP CV-2 (MAL27AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
29 | 1KB | D03Q010 | 10.4.11 | 1KB04GP01 | 415V SWGR O/G MODULE # 1KB04FG | LPH-3 BYPASS (CD-37) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 96 | [5 empty] | POWER SUPPLY (5.2kW) | XLPE-AL UNARMOURED | LV02-R1, LV03-R1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-01, TP15-01, TP16-01, ZZ99- |  | EPD | HYD
30 | 1KB | D03Q025 | 10.4.12 | 1KB04IP01 | 415V SWGR O/G MODULE # 1KB04FI | MAIN STEAM LINE STOP VALVE (MS-1) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 166 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV02-R1, LV03-R1, LV63-01, LV13-L1, LV12-L1, LV11-R3, LV10-R2, LV09-R1, LV08-R1, LV76-04, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, BO05-01, BR71-01, BP08-01, ZZ99- |  | EPD | HYD
31 | 1KB | D03L2.5 | 10.4.26 | 1KB04QP01 | 415V SWGR O/G MODULE # 1KB04RC | DRN VLV AFTER IP CV-1 (MAL31AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
32 | 1KB | D03L2.5 | 10.4.26 | 1KB04RP01 | 415V SWGR O/G MODULE # 1KB04RD | DRN VLV AFTER IP CV-2 (MAL32AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
33 | 1KB | D03L2.5 | 10.4.26 | 1KB04SP01 | 415V SWGR O/G MODULE # 1KB04RE | DRN VLV BEF NRV EXTR. 5 (MAL47AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, ZZ99- |  | EPD | HYD
34 | 1KB | D03L2.5 | 10.4.26 | 1KB04TP01 | 415V SWGR O/G MODULE # 1KB04RF | DRN VLV BEF NRV EXTR. 4 (MAL51AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV02-L4, LV03-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, ZZ99- |  | EPD | HYD
35 | 1KB | D03Q010 | 10.4.11 | 1KB04VP01 | 415V SWGR O/G MODULE # 1KB04RH | LPH-2 BYPASS (CD-34) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 96 | [5 empty] | POWER SUPPLY (5.2kW) | XLPE-AL UNARMOURED | LV02-R1, LV03-R1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-01, TP16-01, ZZ99- |  | EPD | HYD
36 | 1KB | D03Q025 | 10.4.12 | 1KB04WP01 | 415V SWGR O/G MODULE # 1KB04RI | MAIN STEAM LINE STOP VALVE (MS-2) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 171 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV02-R1, LV03-R1, LV63-01, LV13-L1, LV12-L1, LV11-R3, LV10-R2, LV09-R1, LV08-R1, LV76-04, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, BO05-01, BO06-01, BO07-01, ZZ99- |  | EPD | HYD
37 | 1KB | D03L2.5 | 10.4.26 | 1KB05DP01 | 415V SWGR O/G MODULE # 1KB05FD | AUX STEAM TO D/A INI. HEATING (AS-7) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, TD33-02, TD34-01, ZZ99- |  | EPD | HYD
38 | 1KB | D03L2.5 | 10.4.26 | 1KB05EP01 | 415V SWGR O/G MODULE # 1KB05FE | EXTN.TO HPH-5 DRN TO HP F/T (EX-104) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR48-05, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
39 | 1KB | D03L2.5 | 10.4.26 | 1KB05FP01 | 415V SWGR O/G MODULE # 1KB05FF | HRH STRAINER DRN TO HP DRN MANIFOLD (HRH-101) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR48-05, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG56-02, TG57-02, TG59-02, ZZ99- |  | EPD | HYD
40 | 1KB | D03L2.5 | 10.4.26 | 1KB05QP01 | 415V SWGR O/G MODULE # 1KB05RC | HRH STRAINER DRN TO HP DRN MANIFOLD (HRH-102) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG56-02, TG57-02, TG59-02, ZZ99- |  | EPD | HYD
41 | 1KB | D03L2.5 | 10.4.26 | 1KB05RP01 | 415V SWGR O/G MODULE # 1KB05RD | BYPASS VALVE FOR MS-1 (MS-5) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 182 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV03-L4, LV63-05, LV13-L4, LV12-R3, LV11-L4, LV10-L4, LV09-L4, LV08-L4, LV76-04, LV79-03, LR10-R3, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP02-02, ZZ99- |  | EPD | HYD
42 | 1KB | D03L2.5 | 10.4.26 | 1KB05SP01 | 415V SWGR O/G MODULE # 1KB05RE | BYPASS VALVE FOR MS-2 (MS-6) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV03-L4, LV63-05, LV13-L4, LV12-R3, LV11-L4, LV10-L4, LV09-L4, LV08-L4, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-01, BR03-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BO02-02, BO03-02, ZZ99- |  | EPD | HYD
43 | 1KB | D03L2.5 | 10.4.26 | 1KB05TP01 | 415V SWGR O/G MODULE # 1KB05RF | DM MAKE UP CONTROL STN BYPASS (DM-4) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (0.62kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TR19-02, TG62-02, ZZ99- |  | EPD | HYD
44 | 1KB | D03L2.5 | 10.4.26 | 1KB05UP01 | 415V SWGR O/G MODULE # 1KB05RG | DRN VLV BEF HP CV-1 (MAL11AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
45 | 1KB | D03L2.5 | 10.4.26 | 1KB06BP01 | 415V SWGR O/G MODULE # 1KB06FB | DRN VLV BEF NRV EXTR. 3 (MAL54AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, ZZ99- |  | EPD | HYD
46 | 1KB | D03L2.5 | 10.4.26 | 1KB06CP01 | 415V SWGR O/G MODULE # 1KB06FC | DRN VLV BEF NRV EXTR. 2 (MAL55AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, ZZ99- |  | EPD | HYD
47 | 1KB | D03L2.5 | 10.4.26 | 1KB06DP01 | 415V SWGR O/G MODULE # 1KB06FD | DRN VLV BEF NRV CRH (MAL66AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TR41-02, TD35-02, TD36-02, TD37-02, TD38-02, TD39-02, ZZ99- |  | EPD | HYD
48 | 1KB | D03L2.5 | 10.4.26 | 1KB06EP01 | 415V SWGR O/G MODULE # 1KB06FE | DRN VLV GLAND STEAM (MAL81AA011) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 127 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV03-L4, LV04-L3, LV05-L4, LV06-L3, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, ZZ99- |  | EPD | HYD
49 | 1KB | D03L2.5 | 10.4.26 | 1KB06FP01 | 415V SWGR O/G MODULE # 1KB06FF | GLAND STM COND SAFETY VLV (MAW80AA016) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 127 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | LV03-L4, LV04-L3, LV05-L4, LV06-L3, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, ZZ99- |  | EPD | HYD
50 | 1KB | D03L2.5 | 10.4.26 | 1KB06GP01 | 415V SWGR O/G MODULE # 1KB06FG | MO BFV - CONDENSER INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 81 | [5 empty] | POWER SUPPLY (5kW) | XLPE-CU UNARMOURED | LV03-L1, LV64-06, TR48-01, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, TG76-01, TR15-01, TG78-01, TG79-01, TR13-01, ZZ99- |  | EPD | HYD
51 | 1KB | D03Q025 | 10.4.12 | 1KB06HP01 | 415V SWGR O/G MODULE # 1KB06FH | HPH-6 BYPASS (FD-11) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV03-L1, LV64-04, TR25-01, TP55-01, TP54-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TR28-01, TD16-01, TD13-01, ZZ99- |  | EPD | HYD
52 | 1KB | D03Q025 | 10.4.12 | 1KB06IP01 | 415V SWGR O/G MODULE # 1KB06FI | HPH-6 OUTLET (FD-12) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV03-L1, LV64-04, TR25-01, TP55-01, TP54-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TR28-01, TD16-01, TD13-01, TD14-01, TD15-01, ZZ99- |  | EPD | HYD
53 | 1KB | D03L2.5 | 10.4.26 | 1KB06VP01 | 415V SWGR O/G MODULE # 1KB06RH | MO BFV - CONDENSER INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (5kW) | XLPE-CU UNARMOURED | LV03-L1, LV64-06, TR48-01, TG71-02, TG72-02, TR16-02, TG73-02, TG74-01, TG75-01, TG76-01, TR15-01, TG78-01, TG79-01, TR13-01, ZZ99- |  | EPD | HYD
54 | 1KB | D03Q025 | 10.4.12 | 1KB06WP01 | 415V SWGR O/G MODULE # 1KB06RI | CONDENSATE TO DC INLET (CD-29) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 118 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV03-L1, LV04-L1, LV05-L1, LV06-L2, LV07-L1, LV45-01, TR52-02, TG67-02, TG68-02, TR03-02, TG22-02, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, ZZ99- |  | EPD | HYD
55 | 1KB | D03L2.5 | 10.4.26 | 1KB07DP01 | 415V SWGR O/G MODULE # 1KB07FD | CRH STEAM TO AUX PRV AS-16 BYPASS (AS-18) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.52kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD12-02, TD11-02, ZZ99- |  | EPD | HYD
56 | 1KB | D03L2.5 | 10.4.26 | 1KB07EP01 | 415V SWGR O/G MODULE # 1KB07FE | MO BFV - DMCW PUMP - DISCHARGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV03-L4, LV02-L4, LV01-02, MR01-03, MV01-03, MV02-R1, MV03-L2, MV04-L2, MV05-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, ZZ99- |  | EPD | HYD
57 | 1KB | D03L2.5 | 10.4.26 | 1KB07FP01 | 415V SWGR O/G MODULE # 1KB07FF | MO BFV - DMCW PUMP - DISCHARGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV03-L4, LV02-L4, LV01-02, MR01-03, MV01-03, MV02-R1, MV03-L2, MV04-L2, MV05-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, ZZ99- |  | EPD | HYD
58 | 1KB | D03L2.5 | 10.4.26 | 1KB07GP01 | 415V SWGR O/G MODULE # 1KB07FG | MO BFV - CONDENSER INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (5kW) | XLPE-CU UNARMOURED | LV03-L1, LV64-06, TR48-01, TG71-02, TG72-02, TR16-02, TG73-02, TG74-01, TG75-01, TG76-01, TR15-01, TG78-01, TG79-01, TR13-01, ZZ99- |  | EPD | HYD
59 | 1KB | D03Q025 | 10.4.12 | 1KB07IP01 | 415V SWGR O/G MODULE # 1KB07FI | CEP - A DISCHARGE ISOLATION (CD-3) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV03-L1, LV02-L2, LV01-01, MR01-02, MV01-02, MV02-L2, MV03-L2, MV04-L2, MV05-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-01, TG88-01, TG16-L1, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, TG08-R1, TG07-02, ZZ99- |  | EPD | HYD
60 | 1KB | D03L2.5 | 10.4.26 | 1KB07QP01 | 415V SWGR O/G MODULE # 1KB07RC | MO BFV - MDBFP COOLERS | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV03-L4, LV02-L4, LV01-02, MR01-03, MV01-03, MV02-R1, MV03-L2, MV04-L2, MV05-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99- |  | EPD | HYD
61 | 1KB | D03L2.5 | 10.4.26 | 1KB07RP01 | 415V SWGR O/G MODULE # 1KB07RD | MO BFV - MDBFP COOLERS | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 108 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV03-L4, LV02-L4, LV01-02, MR01-03, MV01-03, MV02-R1, MV03-L2, MV04-L2, MV05-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, ZZ99- |  | EPD | HYD
62 | 1KB | D03L2.5 | 10.4.26 | 1KB07SP01 | 415V SWGR O/G MODULE # 1KB07RE | MO BFV - MDBFP COOLERS | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV03-L4, LV02-L4, LV01-02, MR01-03, MV01-03, MV02-R1, MV98-04, MV14-02, MV13-02, MV12-02, MV11-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99- |  | EPD | HYD
63 | 1KB | D03L2.5 | 10.4.26 | 1KB07TP01 | 415V SWGR O/G MODULE # 1KB07RF | MO BFV - ACW PUMP - DISCHARGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TR19-02, TG62-02, ZZ99- |  | EPD | HYD
64 | 1KB | D03L2.5 | 10.4.26 | 1KB07UP01 | 415V SWGR O/G MODULE # 1KB07RG | MO BFV - ACW PUMP - DISCHARGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV03-L4, LV64-06, TR48-04, ZZ99- |  | EPD | HYD
65 | 1KB | D03L2.5 | 10.4.26 | 1KB07VP01 | 415V SWGR O/G MODULE # 1KB07RH | MO BFV - CONDENSER INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (5kW) | XLPE-CU UNARMOURED | LV03-L1, LV64-06, TR48-01, TG71-02, TG72-02, TR16-02, TG73-02, TG74-01, TG75-01, TG76-01, TR15-01, TG78-01, TG79-01, TR13-01, ZZ99- |  | EPD | HYD
66 | 1KB | D03Q025 | 10.4.12 | 1KB07WP01 | 415V SWGR O/G MODULE # 1KB07RI | AUX STEAM TO D/A PEGG. (AS-5) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV03-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-01, TP49-01, TP03-01, TP04-01, TR26-01, TR40-01, TD18-02, TD19-01, TD23-01, TD24-01, TR53-01, TD25-01, TD26-01, TD27-01, ZZ99- |  | EPD | HYD
67 | 1KB | D03L2.5 | 10.4.26 | 1KB08CP01 | 415V SWGR O/G MODULE # 1KB08FC | MO BFV - SCS INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, ZZ99- |  | EPD | HYD
68 | 1KB | D03L2.5 | 10.4.26 | 1KB08DP01 | 415V SWGR O/G MODULE # 1KB08FD | MO BFV - SCS INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, ZZ99- |  | EPD | HYD
69 | 1KB | D03L2.5 | 10.4.26 | 1KB08EP01 | 415V SWGR O/G MODULE # 1KB08FE | MO BFV - SCS INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, ZZ99- |  | EPD | HYD
70 | 1KB | D03L2.5 | 10.4.26 | 1KB08FP01 | 415V SWGR O/G MODULE # 1KB08FF | MO BFV - SCS INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, ZZ99- |  | EPD | HYD
71 | 1KB | D03Q010 | 10.4.11 | 1KB08GP01 | 415V SWGR O/G MODULE # 1KB08FG | BFP 'A' DISCHARGE (FD-4) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (4.8kW) | XLPE-AL UNARMOURED | LV04-R1, LV03-R1, LV02-R1, LV01-01, MR01-02, MV01-02, MV02-L2, MV03-L2, MV04-L2, MV05-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-01, TG88-01, TG16-L1, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, TG08-R1, ZZ99- |  | EPD | HYD
72 | 1KB | D03Q025 | 10.4.12 | 1KB08HP01 | 415V SWGR O/G MODULE # 1KB08FH | FEED CONTROL VALVE (FD-14) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 137 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-04, TR25-01, TP55-01, TP54-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TR28-01, TR41-01, TD35-01, TD36-01, TD37-01, TD38-01, TD39-01, ZZ99- |  | EPD | HYD
73 | 1KB | D03Q025 | 10.4.12 | 1KB08IP01 | 415V SWGR O/G MODULE # 1KB08FI | FEED CONTROL VALVE FD-17 (HIGH CAP.) U/S ISLN (FD-16) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 132 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-02, TR25-01, TP55-01, TP54-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TR28-01, TR41-01, TD35-01, TD36-01, TD37-01, TD38-01, TD39-01, ZZ99- |  | EPD | HYD
74 | 1KB | D03L2.5 | 10.4.26 | 1KB08QP01 | 415V SWGR O/G MODULE # 1KB08RC | MO BFV - PHE INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
75 | 1KB | D03L2.5 | 10.4.26 | 1KB08RP01 | 415V SWGR O/G MODULE # 1KB08RD | MO BFV - PHE INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
76 | 1KB | D03L2.5 | 10.4.26 | 1KB08SP01 | 415V SWGR O/G MODULE # 1KB08RE | MO BFV - PHE INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
77 | 1KB | D03L2.5 | 10.4.26 | 1KB08TP01 | 415V SWGR O/G MODULE # 1KB08RF | MO BFV - PHE INLET/OUTLET | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
78 | 1KB | D03Q010 | 10.4.11 | 1KB08WP01 | 415V SWGR O/G MODULE # 1KB08RI | LPH-2 OUTLET ISOL (CD-33) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 92 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-02, TP05-02, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, ZZ99- |  | EPD | HYD
79 | 1KB | D03L2.5 | 10.4.26 | 1KB09BP01 | 415V SWGR O/G MODULE # 1KB09FB | MO BFV - TAP OFF FROM CW LINE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, TG76-02, TR15-02, TG78-02, TG79-02, TR13-02, ZZ99- |  | EPD | HYD
80 | 1KB | D03L2.5 | 10.4.26 | 1KB09CP01 | 415V SWGR O/G MODULE # 1KB09FC | MO BFV - TAP OFF FROM CW LINE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, TG76-02, TR15-02, TG78-02, TG79-02, TR13-02, ZZ99- |  | EPD | HYD
81 | 1KB | D03L2.5 | 10.4.26 | 1KB09DP01 | 415V SWGR O/G MODULE # 1KB09FD | MO BFV - ACW PUMP SUCTION | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TR19-02, TG62-02, ZZ99- |  | EPD | HYD
82 | 1KB | D03L2.5 | 10.4.26 | 1KB09EP01 | 415V SWGR O/G MODULE # 1KB09FE | MO BFV - ACW PUMP SUCTION | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, ZZ99- |  | EPD | HYD
83 | 1KB | D03Q010 | 10.4.11 | 1KB09GP01 | 415V SWGR O/G MODULE # 1KB09FG | BFP 'B' DISCHARGE (FD-5) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (4.8kW) | XLPE-AL UNARMOURED | LV04-R1, LV03-R1, LV02-R1, LV01-01, MR01-02, MV01-02, MV02-L2, MV03-L2, MV04-L2, MV05-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-01, TG88-01, TG16-L1, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, ZZ99- |  | EPD | HYD
84 | 1KB | D03Q010 | 10.4.11 | 1KB09IP01 | 415V SWGR O/G MODULE # 1KB09FI | LPH-3 INLET ISOL (CD-35) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-02, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, ZZ99- |  | EPD | HYD
85 | 1KB | D03L2.5 | 10.4.26 | 1KB09RP01 | 415V SWGR O/G MODULE # 1KB09RD | COLD GAS TEMP CONTROL VALVE (PGB33AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.35kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
86 | 1KB | D03L2.5 | 10.4.26 | 1KB09SP01 | 415V SWGR O/G MODULE # 1KB09RE | MO BFV - NORMAL M/U LINE TO DMCW O/H TANK | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | HYD
87 | 1KB | D03L2.5 | 10.4.26 | 1KB09TP01 | 415V SWGR O/G MODULE # 1KB09RF | MO BFV - EMERGENCY M/U LINE TO DMCW O/H TANK | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | HYD
88 | 1KB | D03L2.5 | 10.4.26 | 1KB09UP01 | 415V SWGR O/G MODULE # 1KB09RG | CRH STEAM TO AUX PRV AS-16 BYPASS (AS-34) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD12-02, TD11-02, ZZ99- |  | EPD | HYD
89 | 1KB | D03L2.5 | 10.4.26 | 1KB09VP01 | 415V SWGR O/G MODULE # 1KB09RH | BFP 'C' DISCHARGE (FD-6) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (4.8kW) | XLPE-CU UNARMOURED | LV04-R1, LV64-06, TR48-01, MR16-01, MV99-02, MV03-L2, MV04-L2, MV05-L2, MV06-L2, MV75-02, TR51-02, TG69-02, TG70-02, ZZ99- |  | EPD | HYD
90 | 1KB | D03Q025 | 10.4.12 | 1KB09WP01 | 415V SWGR O/G MODULE # 1KB09RI | CEP - B DISCHARGE ISOLATION (CD-4) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 124 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-R1, LV03-R1, LV02-R1, LV01-01, MR01-02, MV01-02, MV02-L2, MV03-L2, MV04-L2, MV05-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-01, TG88-01, TG16-L1, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, TG08-R1, TG07-02, ZZ99- |  | EPD | HYD
91 | 1KB | D03L2.5 | 10.4.26 | 1KB10CP01 | 415V SWGR O/G MODULE # 1KB10FC | CRH STEAM TO AUX PRV AS-16 U/S ISLN (AS-14) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD12-02, TD11-02, ZZ99- |  | EPD | HYD
92 | 1KB | D03L2.5 | 10.4.26 | 1KB10DP01 | 415V SWGR O/G MODULE # 1KB10FD | DM MU PUMP DISCH HDR TO DMCW O/H TANK (DM-24) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (0.18kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | HYD
93 | 1KB | D03L2.5 | 10.4.26 | 1KB10EP01 | 415V SWGR O/G MODULE # 1KB10FE | CRH TO AUX STEAM PRDS LINE (AS-128) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 84 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TD01-02, TD02-02, TD04-02, TD05-02, ZZ99- |  | EPD | HYD
94 | 1KB | D03L2.5 | 10.4.26 | 1KB10FP01 | 415V SWGR O/G MODULE # 1KB10FF | MS STOP VALVE U/S LINE DRAIN TO IBD (MS-101) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
95 | 1KB | D03Q010 | 10.4.11 | 1KB10IP01 | 415V SWGR O/G MODULE # 1KB10FI | LPH-3 OUTLET ISOL (CD-36) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-02, TP10-02, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, ZZ99- |  | EPD | HYD
96 | 1KB | D03L2.5 | 10.4.26 | 1KB10PP01 | 415V SWGR O/G MODULE # 1KB10RB | MS STOP VALVE U/S LINE DRAIN TO IBD (MS-102) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV63-05, LV13-L4, LV12-R3, LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-01, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BO06-02, ZZ99- |  | EPD | HYD
97 | 1KB | D03L2.5 | 10.4.26 | 1KB10QP01 | 415V SWGR O/G MODULE # 1KB10RC | LUB. OIL TEMP. CONTROL VLV. (MAV41AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
98 | 1KB | D03L2.5 | 10.4.26 | 1KB10UP01 | 415V SWGR O/G MODULE # 1KB10RG | SPARE (EX-106) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | HYD
99 | 1KB | D03L2.5 | 10.4.26 | 1KB10VP01 | 415V SWGR O/G MODULE # 1KB10RH | FEED CONTROL VALVE FD-20 (LOW CAP.) U/S ISLN (FD-19) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (4kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TR41-02, TD35-02, TD36-02, TD37-02, TD38-02, ZZ99- |  | EPD | HYD
100 | 1KB | D03Q025 | 10.4.12 | 1KB10WP01 | 415V SWGR O/G MODULE # 1KB10RI | EXTN. TO HPH-5 (EX-13) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-03, TR25-01, TP55-01, TP54-01, TP52-02, TP49-02, TP03-02, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-02, TP23-01, TP24-01, TR29-01, TD06-01, TD07-01, ZZ99- |  | EPD | HYD
101 | 1KB | D03L2.5 | 10.4.26 | 1KB11EP01 | 415V SWGR O/G MODULE # 1KB11FE | COND. SPRAY TO AUX PRDS (DESH-1) (CD-64) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (0.09kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TD06-02, ZZ99- |  | EPD | HYD
102 | 1KB | D03L2.5 | 10.4.26 | 1KB11FP01 | 415V SWGR O/G MODULE # 1KB11FF | LP WATER INJECTION (MAC01AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (0.09kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-06, TR25-05, TP55-02, TP56-02, TP58-02, ZZ99- |  | EPD | HYD
103 | 1KB | D03L2.5 | 10.4.26 | 1KB11GP01 | 415V SWGR O/G MODULE # 1KB11FG | GLAND STM COND SEAL VLV (MAW80AA001) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 118 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV04-R3, LV05-R3, LV06-R3, LV07-R3, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, ZZ99- |  | EPD | HYD
104 | 1KB | D03Q025 | 10.4.12 | 1KB11HP01 | 415V SWGR O/G MODULE # 1KB11FH | MAIN CONDENSATE 100% CV CD-14 U/S ISOL (CD-13) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 122 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV05-L1, LV06-L2, LV07-L1, LV45-01, TR52-02, TG67-02, TG68-02, TR03-02, TG22-02, TR04-02, TG23-02, TG24-02, TG25-02, TG26-02, TG27-02, TG28-02, TR05-01, TG29-01, ZZ99- |  | EPD | HYD
105 | 1KB | D03Q025 | 10.4.12 | 1KB11IP01 | 415V SWGR O/G MODULE # 1KB11FI | MAIN CONDENSATE STATION LINE (CD-19) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-R1, LV05-R1, LV06-R1, LV07-R1, LV45-01, TR52-02, TG67-02, TG68-02, TR03-02, TG22-02, TR04-02, TG23-02, TG24-02, TG25-02, TG26-02, TG27-02, TG28-02, TR05-02, TG29-02, ZZ99- |  | EPD | HYD
106 | 1KB | D03L2.5 | 10.4.26 | 1KB11QP01 | 415V SWGR O/G MODULE # 1KB11RC | AS TO GLAND SEAL LINE DRAIN TO HP FLASH TANK (AS-19) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 67 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
107 | 1KB | D03L2.5 | 10.4.26 | 1KB11RP01 | 415V SWGR O/G MODULE # 1KB11RD | COND. SPRAY TO AUX PRDS(DESH-1) BYPASS CV CD-61 (CD-63) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TD06-02, ZZ99- |  | EPD | HYD
108 | 1KB | D03L2.5 | 10.4.26 | 1KB11SP01 | 415V SWGR O/G MODULE # 1KB11RE | COND. SPRAY TO AUX PRDS(DESH-1) (CD-60) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TD06-02, ZZ99- |  | EPD | HYD
109 | 1KB | D03L2.5 | 10.4.26 | 1KB11TP01 | 415V SWGR O/G MODULE # 1KB11RF | CEP DISCHARGE TO OVERHEAD TANK (DM-53) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-R3, LV03-R3, LV02-R3, LV01-02, MR01-03, MV01-03, MV02-R1, MV03-L2, MV04-L2, MV05-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, TG08-R2, TG07-03, ZZ99- |  | EPD | HYD
110 | 1KB | D03L2.5 | 10.4.26 | 1KB11UP01 | 415V SWGR O/G MODULE # 1KB11RG | FROM DM PLANT TO DM TANK INLET (DM-8) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 414 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-R3, LV05-R3, LV06-R3, LV49-04, LV48-04, LV47-04, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, CC05-04, IR19-02, IM06-02, IM07-05, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM22-03, IM23-03, IM24-03, IM25-03, IM26-03, IM27-03, IM28-03, IM29-03, IM30-03, IM31-03, ZZ99- |  | EPD | HYD
111 | 1KB | D03L2.5 | 10.4.26 | 1KB11VP01 | 415V SWGR O/G MODULE # 1KB11RH | MAIN STEAM TO AUX PRDS CV BYPASS ISLN (AS-33) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD12-02, TD10-02, TD09-02, ZZ99- |  | EPD | HYD
112 | 1KB | D03Q010 | 10.4.11 | 1KB11WP01 | 415V SWGR O/G MODULE # 1KB11RI | EXTN. TO LPH-2 (EX-10) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 93 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-02, TP10-02, TP11-02, TP12-02, TP13-01, TP14-01, TP21-01, TP20-01, ZZ99- |  | EPD | HYD
113 | 1KB | D03L2.5 | 10.4.26 | 1KB12CP01 | 415V SWGR O/G MODULE # 1KB12FC | IBV for FD-19 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 127 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TR41-02, TD35-02, TD36-02, TD37-02, TD38-02, ZZ99- |  | EPD | HYD
114 | 1KB | D03L2.5 | 10.4.26 | 1KB12DP01 | 415V SWGR O/G MODULE # 1KB12FD | CRH NRV & LINE DRN TO HP DRN F/T (CRH-101) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-R3, LV64-06, TR48-04, TG65-02, TR17-02, TG64-02, TG63-02, TG61-02, TG60-02, TG59-02, TG57-02, TG56-02, TR21-02, TG54-02, TG53-02, ZZ99- |  | EPD | HYD
115 | 1KB | D03L2.5 | 10.4.26 | 1KB12EP01 | 415V SWGR O/G MODULE # 1KB12FE | EXTN.TO HPH-6 LINE DRN U/S OF EX-14 (EX-133) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 131 | [5 empty] | POWER SUPPLY (0.06kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TR41-02, TD35-02, TD36-02, TD37-02, TD38-02, TD39-02, ZZ99- |  | EPD | HYD
116 | 1KB | D03L2.5 | 10.4.26 | 1KB12GP01 | 415V SWGR O/G MODULE # 1KB12FG | MAIN STEAM TO AUX PRDS CV AS-10 U/S ISLN (AS-9) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (3.3kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD12-02, TD10-02, TD09-02, ZZ99- |  | EPD | HYD
117 | 1KB | D03Q010 | 10.4.11 | 1KB12HP01 | 415V SWGR O/G MODULE # 1KB12FH | LPH-1 OUTLET ISOL (CD-30) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 88 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-01, TP21-01, ZZ99- |  | EPD | HYD
118 | 1KB | D03Q010 | 10.4.11 | 1KB12IP01 | 415V SWGR O/G MODULE # 1KB12FI | LPH-2 INLET ISOL (CD-32) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 91 | [5 empty] | POWER SUPPLY (11.72kW) | XLPE-AL UNARMOURED | LV04-L1, LV64-01, TR25-02, TP55-01, TP54-01, TP52-02, TP49-02, TP03-01, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-01, TP16-01, ZZ99- |  | EPD | HYD
119 | 1KB | D03L2.5 | 10.4.26 | 1KB12RP01 | 415V SWGR O/G MODULE # 1KB12RD | BYPASS VALVE FOR MS-2 (MS-4) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV63-05, LV13-L4, LV12-R3, LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-01, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BP08-02, ZZ99- |  | EPD | HYD
120 | 1KB | D03L2.5 | 10.4.26 | 1KB13EP01 | 415V SWGR O/G MODULE # 1KB13FE | IBV for FD-16 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 131 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TR41-02, TD35-02, TD36-02, TD37-02, TD38-02, TD39-02, ZZ99- |  | EPD | HYD
121 | 1KB | D03L2.5 | 10.4.26 | 1KB13FP01 | 415V SWGR O/G MODULE # 1KB13FF | IBV for FD-12 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD13-02, TD14-02, TD15-02, ZZ99- |  | EPD | HYD
122 | 1KB | D03L2.5 | 10.4.26 | 1KB13GP01 | 415V SWGR O/G MODULE # 1KB13FG | IBV for FD-10 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, ZZ99- |  | EPD | HYD
123 | 1KB | D03L2.5 | 10.4.26 | 1KB13HP01 | 415V SWGR O/G MODULE # 1KB13FH | IBV for FD-8 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-06, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, ZZ99- |  | EPD | HYD
124 | 1KB | D03L2.5 | 10.4.26 | 1KB13PP01 | 415V SWGR O/G MODULE # 1KB13RB | IBV for FD-7 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-06, TR25-04, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP06-02, TP07-02, ZZ99- |  | EPD | HYD
125 | 1KB | D03L2.5 | 10.4.26 | 1KB13QP01 | 415V SWGR O/G MODULE # 1KB13RC | IBV for FD-6 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 57 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-R3, LV59-02, TR50-02, TG66-02, TR18-02, TG63-02, TG61-02, TG60-02, TG59-02, TG58-02, TR20-02, ZZ99- |  | EPD | HYD
126 | 1KB | D03L2.5 | 10.4.26 | 1KB13RP01 | 415V SWGR O/G MODULE # 1KB13RD | IBV for FD-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-R3, LV59-02, TR50-02, TG66-02, TR18-02, TG63-02, TG61-02, TG60-02, TG59-02, TG58-02, TR20-02, ZZ99- |  | EPD | HYD
127 | 1KB | D03L2.5 | 10.4.26 | 1KB13SP01 | 415V SWGR O/G MODULE # 1KB13RE | IBV for FD-4 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 72 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-R3, LV59-02, TR50-02, TG66-02, TR18-02, TG63-02, TG61-02, TG60-02, TG59-02, TG58-02, TR20-02, ZZ99- |  | EPD | HYD
128 | 1KB | D03L2.5 | 10.4.26 | 1KB13TP01 | 415V SWGR O/G MODULE # 1KB13RF | IBV for AS-33 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD12-02, TD11-02, ZZ99- |  | EPD | HYD
129 | 1KB | D03L2.5 | 10.4.26 | 1KB13UP01 | 415V SWGR O/G MODULE # 1KB13RG | IBV for AS-9 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | LV04-L4, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TR28-02, TD16-02, TD12-02, TD10-02, TD09-02, ZZ99- |  | EPD | HYD
1 | 1QA | D3HQ050 | 10.4.19 | 1QA01CP01 | 415V SWGR O/G MODULE # 1QA01FC | FEEDER FOR BOILER PASSENGER CUM GOODS ELEVATOR | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 167 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV24-L1, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, CR01-L1, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, BR15-01, ZZ99- |  | EPD | PEM
2 | 1QA | D02L2.5 | 10.4.24 | 1QA01DP01 | 415V SWGR O/G MODULE # 1QA01FD | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (1kVA) | XLPE-CU UNARMOURED | LV20-L4, LV21-L4, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV39-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | TRY
3 | 1QA | D3HQ025 | 10.4.18 | 1QA01GP01 | 415V SWGR O/G MODULE # 1QA01FG | HOIST FOR SOOT LOWER MCC ROOM (3T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, QR03-L1, BQ20-L1, BQ19-L1, BQ06-01, BQ05-01, BQ04-01, BQ03-L1, BQ02-L1, QR01-01, ZZ99- |  | EPD | PEM
4 | 1QA | D02Q025 | 10.4.07 | 1QA01QP01 | 415V SWGR O/G MODULE # 1QA01RC | AIR DRIER EXCITER UNIT | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 156 | [5 empty] | POWER SUPPLY (3.5kW) | XLPE-AL UNARMOURED | LV20-L2, LV62-02, LV63-02, LV04-L1, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TP18-01, TP19-01, TP22-01, TP27-01, TP28-01, TP44-01, TP45-01, TP46-01, ZZ99- |  | EPD | PEM
5 | 1QA | D02L2.5 | 10.4.24 | 1QA01RP01 | 415V SWGR O/G MODULE # 1QA01RD | AIR PREHEATER - A LIGHT ASSEMBLY | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 217 | [5 empty] | POWER SUPPLY (0.5kW) | XLPE-CU UNARMOURED | LV20-L4, LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, ZZ99- |  | EPD | RPT
6 | 1QA | D02L2.5 | 10.4.24 | 1QA01SP01 | 415V SWGR O/G MODULE # 1QA01RE | STARTER CAB FOR DC SOP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY (16A) | XLPE-CU UNARMOURED | LV20-L4, LV21-L4, LV22-L4, LV48-04, LV49-04, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG31-03, TR06-02, TG32-02, TG33-02, ZZ99- |  | EPD | HWR
7 | 1QA | D04Q010 | 10.4.22 | 1QA01TP01 | 415V SWGR O/G MODULE # 1QA01RF | MILL CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 213 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV20-R1, LV21-R1, LV22-R1, LV23-R1, LV43-01, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-02, IC46-02, IC47-02, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-03, BA15-03, BR39-02, BB12-01, ZZ99- |  | EPD | RPT
8 | 1QA | D04Q010 | 10.4.22 | 1QA01UP01 | 415V SWGR O/G MODULE # 1QA01RG | MILL CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV43-01, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-02, IC46-02, IC47-02, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-03, BA15-03, BR39-02, BB12-01, ZZ99- |  | EPD | RPT
9 | 1QA | D3HQ095 | 10.4.20 | 1QA01VP01 | 415V SWGR O/G MODULE # 1QA01RH | ID FAN HANDLING (HOIST) | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 398 | [5 empty] | POWER SUPPLY (25kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV47-02, LV46-02, LV38-L3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R4, IM32-R4, IM33-R4, IR31-R3, IM34-R4, IM35-R4, IM36-R4, IM37-R4, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, ZZ99- |  | EPD | PEM
10 | 1QA | D04Q010 | 10.4.22 | 1QA02BP01 | 415V SWGR O/G MODULE # 1QA02FB | SCS MCC | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (1kW) | XLPE-AL UNARMOURED | LV20-L2, LV62-02, LV63-03, LV64-03, TR48-03, TG65-01, TR17-01, TG64-01, ZZ99- |  | EPD | PEM
11 | 1QA | D02L2.5 | 10.4.24 | 1QA02CP01 | 415V SWGR O/G MODULE # 1QA02FC | BREAKER PANEL FOR CEP-1A | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (16A) | XLPE-CU UNARMOURED | LV20-L4, LV21-L4, LV51-02, LV29-L4, ZZ99- |  | EPD | BPL
12 | 1QA | D04Q010 | 10.4.22 | 1QA02DP01 | 415V SWGR O/G MODULE # 1QA02FD | FURNACE TEMP. PROBE STARTER BOX | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 185 | [5 empty] | POWER SUPPLY (1.5kVA) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, CR01-L1, IC01-L2, IC02-L2, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR17-01, BR18-01, BR19-01, BR20-01, BR21-01, BR22-01, BR23-01, BR24-01, BJ05-01, BJ06-01, ZZ99- |  | EPD | TRY
13 | 1QA | D04Q010 | 10.4.22 | 1QA02FP01 | 415V SWGR O/G MODULE # 1QA02FF | SOOT BLOWER MCC | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 92 | [5 empty] | POWER SUPPLY (5kVA) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, QR03-L1, BQ20-L1, BQ19-L1, BQ06-01, BQ23-01, BQ09-01, ZZ99- |  | EPD | PEM
14 | 1QA | D3HQ025 | 10.4.18 | 1QA02PP01 | 415V SWGR O/G MODULE # 1QA02RB | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
15 | 1QA | D02L2.5 | 10.4.24 | 1QA02RP01 | 415V SWGR O/G MODULE # 1QA02RD | POWER SUPPLY TO HYDRAULIC COUPLING ELECTRIC ACTUATOR | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV20-L4, LV62-05, LV63-05, LV04-L4, LV59-02, TR50-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, ZZ99- |  | EPD | PEM
16 | 1QA | D02L2.5 | 10.4.24 | 1QA02SP01 | 415V SWGR O/G MODULE # 1QA02RE | POWER SUPPLY TO HYDRAULIC COUPLING ELECTRIC ACTUATOR | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 88 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV20-L4, LV62-05, LV63-05, LV04-L4, LV59-02, TR50-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, ZZ99- |  | EPD | PEM
17 | 1QA | D04Q010 | 10.4.22 | 1QA02TP01 | 415V SWGR O/G MODULE # 1QA02RF | MILL CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV43-01, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-02, IC46-02, IC47-02, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-03, BA15-03, BR39-02, BB12-01, ZZ99- |  | EPD | RPT
18 | 1QA | D04Q010 | 10.4.22 | 1QA02UP01 | 415V SWGR O/G MODULE # 1QA02RG | MILL CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV43-01, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-02, IC46-02, IC47-02, BR01-02, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-03, BA15-03, BR39-02, BB12-01, ZZ99- |  | EPD | RPT
19 | 1QA | D04Q010 | 10.4.22 | 1QA02VP01 | 415V SWGR O/G MODULE # 1QA02RH | PHOSPHATE DOSING LCP | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (10kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV52-02, LV12-R1, LV58-02, LV59-01, TR50-01, MR15-01, TR02-01, TG85-01, TG86-02, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, TG08-R1, TG06-01, TG05-01, ZZ99- |  | EPD | PEM
20 | 1QA | D3HQ025 | 10.4.18 | 1QA03BP01 | 415V SWGR O/G MODULE # 1QA03FB | PRESSURE PARTS (ECO) HANDLING | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (10kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV43-01, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-02, IC46-02, IC47-02, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, ZZ99- |  | EPD | PEM
21 | 1QA | D04Q010 | 10.4.22 | 1QA03FP01 | 415V SWGR O/G MODULE # 1QA03FF | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (10.8kVA) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV47-02, LV46-02, LV38-L3, LV39-L1, LV73-01, LR08-01, CC01-01, CC72-01, CC02-01, CC04-01, ZZ99- |  | EPD | TRY
22 | 1QA | D02L2.5 | 10.4.24 | 1QA03PP01 | 415V SWGR O/G MODULE # 1QA03RB | STARTER CAB FOR DC EOP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (16A) | XLPE-CU UNARMOURED | LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, ZZ99- |  | EPD | HWR
23 | 1QA | D02L2.5 | 10.4.24 | 1QA03QP01 | 415V SWGR O/G MODULE # 1QA03RC | LIGHTING EXCITER HOUSING | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | POWER SUPPLY (0.16kW) | XLPE-CU UNARMOURED | LV20-L4, LV62-05, LV63-05, LV04-L4, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TR36-02, ZZ99- |  | EPD | PEM
24 | 1QA | D02L2.5 | 10.4.24 | 1QA03RP01 | 415V SWGR O/G MODULE # 1QA03RD | AIR PREHEATER - A SOLENOID VALVE | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 212 | [5 empty] | POWER SUPPLY (0.02kW) | XLPE-CU UNARMOURED | LV20-L4, LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-03, CC71-05, CR01-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, ZZ99- |  | EPD | RPT
25 | 1QA | D04Q010 | 10.4.22 | 1QA03TP01 | 415V SWGR O/G MODULE # 1QA03RF | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (10.8kVA) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV47-02, LV46-02, LV38-L3, LV39-L1, LV73-01, LR08-01, CC01-01, CC72-01, CC02-01, CC04-01, ZZ99- |  | EPD | TRY
26 | 1QA | D04Q010 | 10.4.22 | 1QA03UP01 | 415V SWGR O/G MODULE # 1QA03RG | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (10.8kVA) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV47-02, LV46-02, LV38-L3, LV39-L2, LV73-01, LR08-01, CC01-01, CC72-01, CC02-01, CC04-01, ZZ99- |  | EPD | TRY
27 | 1QA | D3HQ025 | 10.4.18 | 1QA03VP01 | 415V SWGR O/G MODULE # 1QA03RH | SECONDARY AIR DUCT SCAPH HANDLING | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 203 | [5 empty] | POWER SUPPLY (10kW) | XLPE-AL UNARMOURED | LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV43-01, LV44-02, LV76-02, LV79-02, LR10-L2, IC01-L3, IC02-L3, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-01, BA18-01, BA17-01, BA16-01, BA14-03, BA15-03, BR39-02, BB12-02, ZZ99- |  | EPD | PEM
28 | 1QA | D02L2.5 | 10.4.24 | 1QA04BP01 | 415V SWGR O/G MODULE # 1QA04FB | REVERSE ROTATION MONITOR POWER SUPPLY ON HYDRAULIC COUPLING | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV19-L4, LV62-05, LV63-05, LV64-05, TR48-05, MR16-05, MV99-04, MV98-04, MV14-02, MV13-02, MV12-02, MV11-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99- |  | EPD | RPT
29 | 1QA | D3HQ025 | 10.4.18 | 1QA04CP01 | 415V SWGR O/G MODULE # 1QA04FC | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
30 | 1QA | D3HQ025 | 10.4.18 | 1QA04DP01 | 415V SWGR O/G MODULE # 1QA04FD | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
31 | 1QA | D3HQ025 | 10.4.18 | 1QA04EP01 | 415V SWGR O/G MODULE # 1QA04FE | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
32 | 1QA | D3HQ025 | 10.4.18 | 1QA04FP01 | 415V SWGR O/G MODULE # 1QA04FF | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
33 | 1QA | D3HQ025 | 10.4.18 | 1QA04GP01 | 415V SWGR O/G MODULE # 1QA04FG | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
34 | 1QA | D3HQ025 | 10.4.18 | 1QA04QP01 | 415V SWGR O/G MODULE # 1QA04RC | AC FUSE DB (FOR OTHERS) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
35 | 1QA | D3HQ025 | 10.4.18 | 1QA04RP01 | 415V SWGR O/G MODULE # 1QA04RD | AC FUSE DB (FOR OTHERS) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
36 | 1QA | D04Q010 | 10.4.22 | 1QA04SP01 | 415V SWGR O/G MODULE # 1QA04RE | SUMP PUMP (FIXED DUTY) - CW PIT | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 85 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV19-L2, LV62-02, LV63-03, LV64-03, TR48-03, TG71-01, TG72-01, TR16-01, TG73-01, TG74-01, TG75-01, TG76-01, TR15-01, TG78-01, TG79-01, TR13-01, ZZ99- |  | EPD | PEM
37 | 1QA | D3HQ025 | 10.4.18 | 1QA04TP01 | 415V SWGR O/G MODULE # 1QA04RF | FD FAN MOTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, CR01-L1, IC01-L3, IC02-L3, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR16-01, BA01-01, BA02-01, BA03-01, BA04-01, BA05-01, BA07-01, BA08-01, BA09-01, ZZ99- |  | EPD | PEM
38 | 1QA | D3HQ025 | 10.4.18 | 1QA04UP01 | 415V SWGR O/G MODULE # 1QA04RG | FD FAN ROTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, CR01-L1, IC01-L3, IC02-L3, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR16-01, BA01-01, BA02-01, BA03-01, BA04-01, BA05-01, BA07-01, BA08-01, BA09-01, ZZ99- |  | EPD | TRY
39 | 1QA | D3HQ025 | 10.4.18 | 1QA05EP01 | 415V SWGR O/G MODULE # 1QA05FE | FUEL OIL PUMP HANDLING | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 594 | [5 empty] | POWER SUPPLY (10kVA) | XLPE-AL UNARMOURED | LV19-L2, LV61-02, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV40-02, IR17-03, IM01-03, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R4, IM32-R4, IM33-R4, IR31-R3, IM34-R4, IM35-R4, IM36-R4, IM37-R4, IR21-02, ZZ99- |  | EPD | TRY
40 | 1QA | D3HQ025 | 10.4.18 | 1QA05GP01 | 415V SWGR O/G MODULE # 1QA05FG | PA FAN MOTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 202 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L2, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, CR01-L1, IC01-L3, IC02-L3, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR16-01, BA01-01, BA02-01, BA03-01, BA04-01, BA05-01, BA06-01, ZZ99- |  | EPD | PEM
41 | 1QA | D3HQ025 | 10.4.18 | 1QA05QP01 | 415V SWGR O/G MODULE # 1QA05RC | HOIST FOR VACUUM PUMPS (3T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV19-R1, LV20-R2, LV21-R1, LV22-R1, LV23-R1, LV43-01, LV44-02, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG36-01, TG37-01, TG38-01, TR07-01, TG39-01, TG41-01, TG42-01, TR08-01, ZZ99- |  | EPD | PEM
42 | 1QA | D02L2.5 | 10.4.24 | 1QA05RP01 | 415V SWGR O/G MODULE # 1QA05RD | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (1kVA) | XLPE-CU UNARMOURED | LV19-L4, LV20-L4, LV21-L4, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV39-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | TRY
43 | 1QA | D02L2.5 | 10.4.24 | 1QA05SP01 | 415V SWGR O/G MODULE # 1QA05RE | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (1kVA) | XLPE-CU UNARMOURED | LV19-L4, LV20-L4, LV21-L4, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV39-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | TRY
44 | 1QA | D3HQ025 | 10.4.18 | 1QA05TP01 | 415V SWGR O/G MODULE # 1QA05RF | HOIST FOR DMCW TG PUMPS & ACW PUMPS (5T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV19-R1, LV62-01, LV63-02, LV64-03, TR48-03, TG65-01, TR17-01, TG64-01, TG63-01, TR19-01, TG62-01, ZZ99- |  | EPD | PEM
45 | 1QA | D3HQ025 | 10.4.18 | 1QA05VP01 | 415V SWGR O/G MODULE # 1QA05RH | PA FAN ROTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 202 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L2, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, CR01-L1, IC01-L3, IC02-L3, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR16-01, BA01-01, BA02-01, BA03-01, BA04-01, BA05-01, BA06-01, ZZ99- |  | EPD | PEM
46 | 1QA | D3HQ025 | 10.4.18 | 1QA06BP01 | 415V SWGR O/G MODULE # 1QA06FB | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
47 | 1QA | D3HQ025 | 10.4.18 | 1QA06CP01 | 415V SWGR O/G MODULE # 1QA06FC | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
48 | 1QA | D02Q025 | 10.4.07 | 1QA06DP01 | 415V SWGR O/G MODULE # 1QA06FD | FEEDER FOR BOILER PASSENGER CUM GOODS ELEVATOR | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 154 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L1, LV43-01, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-02, IC46-02, IC47-02, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, BR15-01, ZZ99- |  | EPD | PEM
49 | 1QA | D3HQ025 | 10.4.18 | 1QA06EP01 | 415V SWGR O/G MODULE # 1QA06FE | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
50 | 1QA | D04Q010 | 10.4.22 | 1QA06FP01 | 415V SWGR O/G MODULE # 1QA06FF | SCS MCC | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (1kW) | XLPE-AL UNARMOURED | LV19-L2, LV62-02, LV63-03, LV64-03, TR48-03, TG65-01, TR17-01, TG64-01, ZZ99- |  | EPD | PEM
51 | 1QA | D02L2.5 | 10.4.24 | 1QA06GP01 | 415V SWGR O/G MODULE # 1QA06FG | AIR PREHEATER - B LIGHT ASSEMBLY | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 174 | [5 empty] | POWER SUPPLY (0.5kW) | XLPE-CU UNARMOURED | LV19-L4, LV20-L4, LV21-L4, LV22-L4, LV23-L4, LV43-03, LV44-03, LV76-02, LV79-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, ZZ99- |  | EPD | RPT
52 | 1QA | D04Q010 | 10.4.22 | 1QA06PP01 | 415V SWGR O/G MODULE # 1QA06RB | MILL CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 217 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L2, LV43-01, LV44-02, LV76-02, LV79-02, LR10-L2, IC01-L3, IC02-L3, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-03, BA15-03, BR39-02, BB13-01, ZZ99- |  | EPD | RPT
53 | 1QA | D04Q010 | 10.4.22 | 1QA06QP01 | 415V SWGR O/G MODULE # 1QA06RC | MILL CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 217 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L2, LV43-01, LV44-02, LV76-02, LV79-02, LR10-L2, IC01-L3, IC02-L3, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-03, BA15-03, BR39-02, BB13-01, ZZ99- |  | EPD | RPT
54 | 1QA | D02L2.5 | 10.4.24 | 1QA06SP01 | 415V SWGR O/G MODULE # 1QA06RE | POWER SUPPLY TO HYDRAULIC COUPLING ELECTRIC ACTUATOR | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV19-L4, LV62-05, LV63-05, LV64-05, TR48-05, MR16-05, MV99-04, MV98-04, MV14-02, MV13-02, MV12-02, MV11-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99- |  | EPD | PEM
55 | 1QA | D3HQ025 | 10.4.18 | 1QA06UP01 | 415V SWGR O/G MODULE # 1QA06RG | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
56 | 1QA | D3HQ025 | 10.4.18 | 1QA06VP01 | 415V SWGR O/G MODULE # 1QA06RH | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
57 | 1QA | D3HQ025 | 10.4.18 | 1QA06WP01 | 415V SWGR O/G MODULE # 1QA06RI | AC FUSE DB (FOR LIE/LIR) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
58 | 1QA | D02L2.5 | 10.4.24 | 1QA07BP01 | 415V SWGR O/G MODULE # 1QA07FB | BREAKER PANEL FOR CEP-1B | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (16A) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV20-L4, LV21-L4, LV51-02, LV29-L4, ZZ99- |  | EPD | BPL
59 | 1QA | D04Q010 | 10.4.22 | 1QA07CP01 | 415V SWGR O/G MODULE # 1QA07FC | FURNACE TEMP. PROBE STARTER BOX | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 148 | [5 empty] | POWER SUPPLY (1.5kVA) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-02, LR10-L2, IC01-L3, IC02-L3, IR06-02, IC46-02, IC47-02, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BJ01-01, BJ02-01, ZZ99- |  | EPD | TRY
60 | 1QA | D04Q010 | 10.4.22 | 1QA07DP01 | 415V SWGR O/G MODULE # 1QA07FD | MILL CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 219 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-01, BA15-01, BR39-03, BB13-01, ZZ99- |  | EPD | RPT
61 | 1QA | D3HQ025 | 10.4.18 | 1QA07EP01 | 415V SWGR O/G MODULE # 1QA07FE | PA FAN MOTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 158 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-01, BA24-01, ZZ99- |  | EPD | PEM
62 | 1QA | D3HQ025 | 10.4.18 | 1QA07FP01 | 415V SWGR O/G MODULE # 1QA07FF | PA FAN ROTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 160 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-03, LV76-02, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-01, BA24-01, ZZ99- |  | EPD | PEM
63 | 1QA | D3HQ025 | 10.4.18 | 1QA07HP01 | 415V SWGR O/G MODULE # 1QA07FH | HOIST FOR DMCW SG PUMPS (3T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV18-R1, LV19-R1, LV20-R2, LV21-R1, LV22-R1, LV23-R1, LV43-01, LV44-02, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, ZZ99- |  | EPD | PEM
64 | 1QA | D02L2.5 | 10.4.24 | 1QA07PP01 | 415V SWGR O/G MODULE # 1QA07RB | GEN. INST. CABINET | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (16A) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV62-05, LV63-05, LV04-L4, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TR36-02, ZZ99- |  | EPD | PEM
65 | 1QA | D02L2.5 | 10.4.24 | 1QA07QP01 | 415V SWGR O/G MODULE # 1QA07RC | AIR PREHEATER - B SOLENOID VALVE | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 177 | [5 empty] | POWER SUPPLY (0.02kW) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV62-05, LV13-L4, LV12-L4, LV11-L4, LV10-L4, LV44-03, LV76-02, LV79-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, ZZ99- |  | EPD | RPT
66 | 1QA | D02L2.5 | 10.4.24 | 1QA07RP01 | 415V SWGR O/G MODULE # 1QA07RD | STROBOSCOPE FUSE MONITORING | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 182 | [5 empty] | POWER SUPPLY (0.015kW) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV62-05, LV63-05, LV04-L4, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | EPD | HWR
67 | 1QA | D3HQ025 | 10.4.18 | 1QA07TP01 | 415V SWGR O/G MODULE # 1QA07RF | HOIST FOR VACUUM PUMPS (3T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV18-R1, LV19-R1, LV62-01, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG36-01, TG37-01, TG38-01, ZZ99- |  | EPD | PEM
68 | 1QA | D3HQ025 | 10.4.18 | 1QA07VP01 | 415V SWGR O/G MODULE # 1QA07RH | SECONDARY AIR DUCT SCAPH HANDLING | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 205 | [5 empty] | POWER SUPPLY (10kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-03, LV76-02, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BA16-02, BA14-01, BA15-01, BR39-03, BB13-01, ZZ99- |  | EPD | PEM
69 | 1QA | D02L2.5 | 10.4.24 | 1QA08DP01 | 415V SWGR O/G MODULE # 1QA08FD | STARTER CAB FOR DC JOP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (16A) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, ZZ99- |  | EPD | HWR
70 | 1QA | D3HQ025 | 10.4.18 | 1QA08FP01 | 415V SWGR O/G MODULE # 1QA08FF | HOIST FOR TG BUILDING ELEVATOR M/C ROOM (3T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 156 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV18-R1, LV19-R1, LV62-02, LV63-02, LV04-L1, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP04-01, TR26-01, TR40-01, TD18-01, TR47-01, TD51-01, TD50-01, TD47-01, TD45-01, TD43-01, TR46-01, TD41-01, TD59-01, TD60-01, TD61-01, TD62-01, TD63-01, TD64-01, TD65-01, TD66-01, TD67-01, ZZ99- |  | EPD | PEM
71 | 1QA | D3HQ050 | 10.4.19 | 1QA08GP01 | 415V SWGR O/G MODULE # 1QA08FG | MILL SERVICE CRANE WITH HOIST MOTOR | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 245 | [5 empty] | POWER SUPPLY (25kW) | XLPE-AL UNARMOURED | LV18-R1, LV19-R1, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV76-02, LV79-01, LR10-L2, IC01-L2, IC02-L2, IR06-02, IC46-02, IC47-02, BR01-01, BA25-01, BA26-01, BA27-01, BA28-01, BA29-01, BA19-01, BA18-01, BA17-01, BA16-01, BA14-03, BA15-03, BR39-02, BB13-01, ZZ99- |  | EPD | PEM
72 | 1QA | D3HQ050 | 10.4.19 | 1QA08HP01 | 415V SWGR O/G MODULE # 1QA08FH | COMPRESSOR HOUSE CRANE (8T) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV18-R1, LV71-02, LR02-02, TY14-R1, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, CM07-R1, CM12-02, ZZ99- |  | EPD | PEM
73 | 1QA | D3HQ050 | 10.4.19 | 1QA08IP01 | 415V SWGR O/G MODULE # 1QA08FI | HOIST FOR CW VALVES IN CW PIT (8T) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 182 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV18-R1, LV19-R2, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV10-L2, LV44-02, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG36-01, TG37-01, TG38-01, TG43-01, TG44-01, TG45-01, TG46-01, TR11-01, TG47-01, TR12-01, ZZ99- |  | EPD | PEM
74 | 1QA | D02L2.5 | 10.4.24 | 1QA08PP01 | 415V SWGR O/G MODULE # 1QA08RB | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (1kVA) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV20-L4, LV21-L4, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV39-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | TRY
75 | 1QA | D02L2.5 | 10.4.24 | 1QA08QP01 | 415V SWGR O/G MODULE # 1QA08RC | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (1kVA) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV20-L4, LV21-L4, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV39-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | TRY
76 | 1QA | D02L2.5 | 10.4.24 | 1QA08RP01 | 415V SWGR O/G MODULE # 1QA08RD | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (1kVA) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV20-L4, LV21-L4, LV51-02, LV50-02, LV36-L4, LV37-L4, LV38-L4, LV39-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | TRY
77 | 1QA | D04Q010 | 10.4.22 | 1QA08TP01 | 415V SWGR O/G MODULE # 1QA08RF | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (10.8kVA) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV61-02, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV39-R1, LV73-02, LR08-01, CC01-01, CC72-01, CC02-01, CC04-01, ZZ99- |  | EPD | TRY
78 | 1QA | D04Q010 | 10.4.22 | 1QA08UP01 | 415V SWGR O/G MODULE # 1QA08RG | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (10.8kVA) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV61-02, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV39-R1, LV73-02, LR08-01, CC01-01, CC72-01, CC02-01, CC04-01, ZZ99- |  | EPD | TRY
79 | 1QA | D3HQ025 | 10.4.18 | 1QA08VP01 | 415V SWGR O/G MODULE # 1QA08RH | AC FUSE DB (FOR OTHERS) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
80 | 1QA | D3HQ025 | 10.4.18 | 1QA08WP01 | 415V SWGR O/G MODULE # 1QA08RI | AC FUSE DB (FOR OTHERS) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
81 | 1QA | D04Q010 | 10.4.22 | 1QA09DP01 | 415V SWGR O/G MODULE # 1QA09FD | APH ELEMENTS HANDLING (HOIST) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 212 | [5 empty] | POWER SUPPLY (5kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV20-L2, LV21-L2, LV22-L1, LV23-L2, LV24-L2, LV25-L1, LV74-02, LR07-01, CC90-01, CC81-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-02, CR01-L1, IC01-L3, IC02-L3, IC03-L2, IC04-L2, IC05-L2, IC06-L2, IR07-01, IC50-01, IC51-01, IC52-01, BR17-01, BC01-01, BC02-01, BC03-01, BC29-01, BC30-01, BC31-01, BC10-01, ZZ99- |  | EPD | RPT
82 | 1QA | D3HQ025 | 10.4.18 | 1QA09EP01 | 415V SWGR O/G MODULE # 1QA09FE | SUMP PUMP (FIXED DUTY) - CW PIT | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV13-L2, LV12-L3, LV11-L3, LV49-02, LV07-L1, LV45-01, TR52-01, TG67-01, TG68-01, TR03-01, TG22-01, TR04-01, TG23-01, TG24-01, TG25-01, TG26-01, TG27-01, TG28-01, TR05-01, TG29-01, TG30-01, TG36-01, TG37-01, TG38-01, TG43-01, TG44-01, TG45-01, TG46-01, TR11-01, TG47-01, TR12-01, ZZ99- |  | EPD | PEM
83 | 1QA | D3HQ025 | 10.4.18 | 1QA09FP01 | 415V SWGR O/G MODULE # 1QA09FF | FD FAN MOTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 143 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV13-R2, LV12-R1, LV11-R3, LV10-R1, LV44-03, LV76-02, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR02-01, BC25-01, BC24-01, BC23-01, ZZ99- |  | EPD | PEM
84 | 1QA | D3HQ025 | 10.4.18 | 1QA09GP01 | 415V SWGR O/G MODULE # 1QA09FG | FD FAN ROTOR HANDLING (HOIST) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 118 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV75-01, LR06-01, CC91-01, CC83-01, CC84-01, CC86-02, CC87-01, CC52-01, CC71-02, CR01-L1, IC01-L2, IC02-L2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, ZZ99- |  | EPD | TRY
85 | 1QA | D02L2.5 | 10.4.24 | 1QA09RP01 | 415V SWGR O/G MODULE # 1QA09RD | REVERSE ROTATION MONITOR POWER SUPPLY ON HYDRAULIC COUPLING | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV62-05, LV63-05, LV04-L4, LV59-02, TR50-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, ZZ99- |  | EPD | RPT
86 | 1QA | D02L2.5 | 10.4.24 | 1QA09SP01 | 415V SWGR O/G MODULE # 1QA09RE | REVERSE ROTATION MONITOR POWER SUPPLY ON HYDRAULIC COUPLING | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 88 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV18-L4, LV19-L4, LV62-05, LV63-05, LV04-L4, LV59-02, TR50-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, ZZ99- |  | EPD | RPT
87 | 1QA | D04Q010 | 10.4.22 | 1QA09TP01 | 415V SWGR O/G MODULE # 1QA09RF | GRAVIMETRIC FEEDER REMOTE POWER CABINET (CER) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (10.8kVA) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV61-02, LV31-L1, LV30-L1, LV50-01, LV36-R1, LV37-R2, LV38-R3, LV39-R1, LV73-02, LR08-01, CC01-01, CC72-01, CC02-01, CC04-01, ZZ99- |  | EPD | TRY
88 | 1QA | D04Q010 | 10.4.22 | 1QA09VP01 | 415V SWGR O/G MODULE # 1QA09RH | PHOSPHATE DOSING LCP | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 123 | [5 empty] | POWER SUPPLY (10kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-02, LV63-03, LV64-03, TR48-03, MR16-02, MR17-03, TG91-02, TG85-01, TG86-02, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, TG08-R1, TG06-01, TG05-01, ZZ99- |  | EPD | PEM
89 | 1QA | D3HQ025 | 10.4.18 | 1QA09WP01 | 415V SWGR O/G MODULE # 1QA09RI | PRESSURE PARTS (ECO) HANDLING | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 189 | [5 empty] | POWER SUPPLY (10kW) | XLPE-AL UNARMOURED | LV18-L2, LV19-L2, LV62-03, LV13-R2, LV12-R1, LV11-R3, LV10-R1, LV44-03, LV76-01, LV79-02, LR10-R2, IC01-R1, IC02-R1, IR06-02, IC46-02, IC47-02, BR02-01, BR03-01, BR04-01, BR05-01, BR06-01, BR07-01, BR08-01, BR09-01, BR10-01, BR11-01, BR12-01, BR13-01, BR14-01, ZZ99- |  | EPD | PEM
1 | 0DA | D3HQ185 | 10.4.21 | 0DA01BP01 | 415V SWGR O/G MODULE # 0DA01FB | FEEDER TO CHIMNEY DB | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 410 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | MV58-R1, MV59-L2, MV62-05, MR06-05, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99- |  | EPD | PEM
2 | 0DA | D3HQ185 | 10.4.21 | 0DA01BP02 | 415V SWGR O/G MODULE # 0DA01FB | FEEDER TO CHIMNEY DB | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 410 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | MV58-R1, MV59-L2, MV62-05, MR06-05, IM02-R2, IM94-R3, IM95-R3, IM96-R3, IM11-R3, IM12-R3, IM13-R3, IM14-R3, IM15-R3, IM16-R3, IM17-R3, IM18-R3, IM19-R3, IM20-R3, IM21-R3, IM32-R2, IM33-R2, IR31-R2, IM34-R2, IM35-R2, IM36-R2, IM37-R2, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-02, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99- |  | EPD | PEM
3 | 0DA | D03Q095 | 10.4.15 | 0DA01CP01 | 415V SWGR O/G MODULE # 0DA01FC | FEEDER TO WDB - MV SWGR ROOM (1UK) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV58-R1, MV57-R1, MV56-R1, MV93-01 |  | EPD | PEM
4 | 0DA | D03Q095 | 10.4.15 | 0DA01DP01 | 415V SWGR O/G MODULE # 0DA01FD | FEEDER TO LDB - MV SWGR ROOM (1UA) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV58-R1, MV57-R1, MV56-R1, MV55-R1 |  | EPD | PEM
5 | 0DA | D03Q095 | 10.4.15 | 0DA01PP01 | 415V SWGR O/G MODULE # 0DA01RB | FEEDER TO LDB - MV SWGR ROOM (1UB) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV58-R1, MV57-R1, MV56-R1, MV55-R1, MA03-01, MR04-01, LV70-01, LV33-L1, LV60-01, LV31-L1, ZZ99- |  | EPD | PEM
6 | 0DA | D03Q095 | 10.4.15 | 0DA01QP01 | 415V SWGR O/G MODULE # 0DA01RC | FEEDER TO LDB - LV SWGR ROOM (1UC) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV58-R1, MV57-R1, MV56-R1, MV55-R1, MA03-01, MR04-01, LV70-01, LV33-L1, LV34-L1, LV35-L1, LV36-L1 |  | EPD | PEM
7 | 0DA | D03Q095 | 10.4.15 | 0DA02CP01 | 415V SWGR O/G MODULE # 0DA02FC | FEEDER TO LDB - LV SWGR ROOM (1UD) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV58-R1, MV57-R1, MV56-R1, MV55-R1, MA03-01, MR04-01, LV70-01, LV33-L1, LV34-L1 |  | EPD | PEM
8 | 0DA | D3HQ185 | 10.4.21 | 0DA02PP01 | 415V SWGR O/G MODULE # 0DA02RB | UPS FEEDER | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 71 | 70 | 23.12.2019 | DR2687-1 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV58-R1, MV69-02, MV70-02, MV42-01, MV65-03, MV28-L2, MA06-02, MR09-02, LV75-01, LV25-L1, LV74-02, DC07-02, ZZ99- |  | EPD | EDN
9 | 0DA | D3HQ185 | 10.4.21 | 0DA02PP02 | 415V SWGR O/G MODULE # 0DA02RB | UPS FEEDER | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 71 | 70 | 23.12.2019 | DR2687-1 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV58-R1, MV69-02, MV70-02, MV42-01, MV65-03, MV28-L2, MA06-02, MR09-02, LV75-01, LV25-L1, LV74-02, DC07-02, ZZ99- |  | EPD | EDN
10 | 0DA | E04V0.5 | 10.7.02 | 0DA03AC01 | 415V SWGR O/G MODULE # 0DA03FA | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 74 | 77 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
11 | 0DA | D01Q400 | 10.4.04 | 0DA03AP01 | 415V SWGR O/G MODULE # 0DA03FA | AC MCC # 0TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 96 | 96 | 07.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-R1, AC15-R1, AC16-R1, AC17-R1, AC18-R1, ZZ99- |  | EPD | EPD
12 | 0DA | D01Q400 | 10.4.04 | 0DA03AP02 | 415V SWGR O/G MODULE # 0DA03FA | AC MCC # 0TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 96 | 96 | 07.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-R1, AC15-R1, AC16-R1, AC17-R1, AC18-R1, ZZ99- |  | EPD | EPD
13 | 0DA | D01Q400 | 10.4.04 | 0DA03AP03 | 415V SWGR O/G MODULE # 0DA03FA | AC MCC # 0TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 96 | 96 | 07.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-R1, AC15-R1, AC16-R1, AC17-R1, AC18-R1, ZZ99- |  | EPD | EPD
14 | 0DA | D01Q400 | 10.4.04 | 0DA03AP04 | 415V SWGR O/G MODULE # 0DA03FA | AC MCC # 0TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 96 | 96 | 07.09.2019 | DR1006_0001 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, AC16-L2, AC17-L2, AC18-L2, ZZ99- |  | EPD | EPD
15 | 0DA | D01Q400 | 10.4.04 | 0DA03AP05 | 415V SWGR O/G MODULE # 0DA03FA | AC MCC # 0TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 96 | 96 | 07.09.2019 | DR0968_0011 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, AC16-L2, AC17-L2, AC18-L2, ZZ99- |  | EPD | EPD
16 | 0DA | D01Q400 | 10.4.04 | 0DA03AP06 | 415V SWGR O/G MODULE # 0DA03FA | AC MCC # 0TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 96 | 96 | 07.09.2019 | DR0968_0011 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, AC16-L2, AC17-L2, AC18-L2, ZZ99- |  | EPD | EPD
17 | 0DA | D01Q400 | 10.4.04 | 0DA03AP07 | 415V SWGR O/G MODULE # 0DA03FA | AC MCC # 0TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 97 | 96 | 07.09.2019 | DR0968_0011 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-R1, AC15-R1, AC16-R1, AC17-R1, AC18-R1, ZZ99- |  | EPD | EPD
18 | 0DA | E04V0.5 | 10.7.02 | 0DA03BC01 | 415V SWGR O/G MODULE # 0DA03FB | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 74 | 79 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
19 | 0DA | D01Q400 | 10.4.04 | 0DA03BP01 | 415V SWGR O/G MODULE # 0DA03FB | VENTILATION & AIR WASHER MCC # 1TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 93 | 90 | 01.11.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV77-02, LR10-R1, CR01-L1, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ21-01, BQ17-01, BQ18-01, ZZ99- |  | EPD | EPD
20 | 0DA | D01Q400 | 10.4.04 | 0DA03BP02 | 415V SWGR O/G MODULE # 0DA03FB | VENTILATION & AIR WASHER MCC # 1TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 93 | 90 | 01.11.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV77-02, LR10-R1, CR01-L1, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ21-01, BQ17-01, BQ18-01, ZZ99- |  | EPD | EPD
21 | 0DA | D01Q400 | 10.4.04 | 0DA03BP03 | 415V SWGR O/G MODULE # 0DA03FB | VENTILATION & AIR WASHER MCC # 1TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 93 | 90 | 01.11.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV77-02, LR10-R1, CR01-L1, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ21-01, BQ17-01, BQ18-01, ZZ99- |  | EPD | EPD
22 | 0DA | D01Q400 | 10.4.04 | 0DA03BP04 | 415V SWGR O/G MODULE # 0DA03FB | VENTILATION & AIR WASHER MCC # 1TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 87 | 90 | 01.11.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV71-03, MV29-R1, MV28-L2, MA06-03, MR09-03, LV77-02, LR10-R1, CR01-L1, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ21-01, BQ17-01, BQ18-01, ZZ99- |  | EPD | EPD
23 | 0DA | D01Q400 | 10.4.04 | 0DA03BP05 | 415V SWGR O/G MODULE # 0DA03FB | VENTILATION & AIR WASHER MCC # 1TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 87 | 90 | 04.12.2019 | DR0968_0010 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV71-03, MV29-R1, MV28-L2, MA06-03, MR09-03, LV77-02, LR10-R1, CR01-L1, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ21-01, BQ17-01, BQ18-01, ZZ99- |  | EPD | EPD
24 | 0DA | D01Q400 | 10.4.04 | 0DA03BP06 | 415V SWGR O/G MODULE # 0DA03FB | VENTILATION & AIR WASHER MCC # 1TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 87 | 90 | 04.12.2019 | DR0968_0010 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV71-03, MV29-R1, MV28-L2, MA06-03, MR09-03, LV77-02, LR10-R1, CR01-L1, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ21-01, BQ17-01, BQ18-01, ZZ99- |  | EPD | EPD
25 | 0DA | D01Q400 | 10.4.04 | 0DA03BP07 | 415V SWGR O/G MODULE # 0DA03FB | VENTILATION & AIR WASHER MCC # 1TA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 93 | 90 | 05.12.2019 | DR0968_0010 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV77-02, LR10-R1, CR01-L1, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ14-01, BQ21-01, BQ17-01, BQ18-01, ZZ99- |  | EPD | EPD
26 | 0DA | E04V0.5 | 10.7.02 | 0DA04AC01 | 415V SWGR O/G MODULE # 0DA04FA | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 74 | 79 | 19.09.2019 | DR0817_4798-4G-16 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
27 | 0DA | D01Q400 | 10.4.04 | 0DA04AP01 | 415V SWGR O/G MODULE # 0DA04FA | MISC. SERVICE MCC # 0SA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 64 | 64 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV75-02, LV24-R1, LV23-R1, ZZ99- |  | EPD | EPD
28 | 0DA | D01Q400 | 10.4.04 | 0DA04AP02 | 415V SWGR O/G MODULE # 0DA04FA | MISC. SERVICE MCC # 0SA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 64 | 64 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV75-02, LV24-R1, LV23-R1, ZZ99- |  | EPD | EPD
29 | 0DA | D01Q400 | 10.4.04 | 0DA04AP03 | 415V SWGR O/G MODULE # 0DA04FA | MISC. SERVICE MCC # 0SA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 64 | 64 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV75-02, LV24-R1, LV23-R1, ZZ99- |  | EPD | EPD
30 | 0DA | D01Q400 | 10.4.04 | 0DA04AP04 | 415V SWGR O/G MODULE # 0DA04FA | MISC. SERVICE MCC # 0SA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 66 | 64 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV42-01, MV65-03, MV28-L2, MA06-02, MR09-02, LV75-01, LV24-L1, LV23-L1, ZZ99- |  | EPD | EPD
31 | 0DA | D01Q400 | 10.4.04 | 0DA04AP05 | 415V SWGR O/G MODULE # 0DA04FA | MISC. SERVICE MCC # 0SA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 66 | 68 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV42-01, MV65-03, MV28-L2, MA06-02, MR09-02, LV75-01, LV24-L1, LV23-L1, ZZ99- |  | EPD | EPD
32 | 0DA | D01Q400 | 10.4.04 | 0DA04AP06 | 415V SWGR O/G MODULE # 0DA04FA | MISC. SERVICE MCC # 0SA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 66 | 69 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-01, MV70-02, MV42-01, MV65-03, MV28-L2, MA06-02, MR09-02, LV75-01, LV24-L1, LV23-L1, ZZ99- |  | EPD | EPD
33 | 0DA | D01Q400 | 10.4.04 | 0DA04AP07 | 415V SWGR O/G MODULE # 0DA04FA | MISC. SERVICE MCC # 0SA SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 64 | 65 | 03.09.2019 | DR1006_0002 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV49-02, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV75-02, LV24-R1, LV23-R1, ZZ99- |  | EPD | EPD
34 | 0DA | E04V0.5 | 10.7.02 | 0DA05BC01 | 415V SWGR I/C MODULE # 0DA05FB | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 74 | 83 | 16.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
35 | 0DA | D02L2.5 | 10.4.24 | 0DA05BC02 | 415V SWGR I/C MODULE # 0DA05FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | MV49-02, MV78-03, MV40-02, MV83-02 |  | EPD | JHS
36 | 0DA | D02L2.5 | 10.4.24 | 0DA05BC03 | 415V SWGR I/C MODULE # 0DA05FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | MV49-02, MV78-03, MV40-02, MV83-02 |  | EPD | JHS
37 | 0DA | D02C1.5 | 10.5.01 | 0DA05BC04 | 415V SWGR I/C MODULE # 0DA05FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 37 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | MV49-02, MV50-02, MV88-03, MV89-03, MV90-03, MV91-03, MV14-02 |  | EPD | BPL
38 | 0DA | E04V0.5 | 10.7.02 | 0DA05BC05 | 415V SWGR I/C MODULE # 0DA05FB | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 74 | 83 | 16.09.2019 | DR0817_4798-4G-87 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
39 | 0DA | E04V0.5 | 10.7.02 | 0DA07BC01 | 415V SWGR B/C MODULE # 0DA07FB | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 83 | 16.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV50-03, MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
40 | 0DA | E04V0.5 | 10.7.02 | 0DA07BC02 | 415V SWGR B/C MODULE # 0DA07FB | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 84 | 19.09.2019 | DR0817_4798-4G-34 |  |  | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | MV50-03, MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
41 | 0DA | E04V0.5 | 10.7.02 | 0DA09BC01 | 415V SWGR I/C MODULE # 0DA09FB | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 84 | 19.09.2019 | DR0817_4798-4G-34 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | MV50-03, MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
42 | 0DA | D02L2.5 | 10.4.24 | 0DA09BC02 | 415V SWGR I/C MODULE # 0DA09FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 18 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | MV50-02, MV88-03, MV89-03 |  | EPD | JHS
43 | 0DA | D02L2.5 | 10.4.24 | 0DA09BC03 | 415V SWGR I/C MODULE # 0DA09FB | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 18 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | MV50-02, MV88-03, MV89-03 |  | EPD | JHS
44 | 0DA | D02C1.5 | 10.5.01 | 0DA09BC04 | 415V SWGR I/C MODULE # 0DA09FB | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | MV50-02, MV88-03, MV89-03, MV90-03, MV20-02 |  | EPD | BPL
45 | 0DA | E04V0.5 | 10.7.02 | 0DA09BC05 | 415V SWGR I/C MODULE # 0DA09FB | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 78 | 84 | 19.09.2019 | DR0817_4798-4G-34 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | MV50-03, MV49-03, MV70-04, MV42-03, MV43-03, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
46 | 0DA | E04V0.5 | 10.7.02 | 0DA10AC01 | 415V SWGR O/G MODULE # 0DA10FA | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | 86 | 19.09.2019 | DR0817_4798-4G-34 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV51-03, MV50-03, MV49-03, MV48-03, MV47-03, MV46-R2, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
47 | 0DA | D01Q400 | 10.4.04 | 0DA10AP01 | 415V SWGR O/G MODULE # 0DA10FA | MISC. SERVICE MCC # 0SA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 70 | 101 | 09.09.2019 | DR0968_0011 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-02, MV94-02, MV95-02, MV34-L2, MA01-02, MR02-02, LV71-02, LV18-R1, LV19-R1, LV20-R1, LV21-R1, LV22-R1, ZZ99- |  | EPD | EPD
48 | 0DA | D01Q400 | 10.4.04 | 0DA10AP02 | 415V SWGR O/G MODULE # 0DA10FA | MISC. SERVICE MCC # 0SA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 70 | 101 | 09.09.2019 | DR0968_0011 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-02, MV94-02, MV95-02, MV34-L2, MA01-02, MR02-02, LV71-02, LV18-R1, LV19-R1, LV20-R1, LV21-R1, LV22-R1, ZZ99- |  | EPD | EPD
49 | 0DA | D01Q400 | 10.4.04 | 0DA10AP03 | 415V SWGR O/G MODULE # 0DA10FA | MISC. SERVICE MCC # 0SA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 70 | 101 | 09.09.2019 | DR0968_0011 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-02, MV94-02, MV95-02, MV34-L2, MA01-02, MR02-02, LV71-02, LV18-R1, LV19-R1, LV20-R1, LV21-R1, LV22-R1, ZZ99- |  | EPD | EPD
50 | 0DA | D01Q400 | 10.4.04 | 0DA10AP04 | 415V SWGR O/G MODULE # 0DA10FA | MISC. SERVICE MCC # 0SA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 70 | 101 | 09.09.2019 | DR0968_0011 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-02, MV94-02, MV95-02, MV34-L2, MA01-02, MR02-02, LV71-02, LV18-R1, LV19-R1, LV20-R1, LV21-R1, LV22-R1, ZZ99- |  | EPD | EPD
51 | 0DA | D01Q400 | 10.4.04 | 0DA10AP05 | 415V SWGR O/G MODULE # 0DA10FA | MISC. SERVICE MCC # 0SA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 70 | 101 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-02, MV94-02, MV95-02, MV34-L2, MA01-02, MR02-02, LV71-02, LV18-R1, LV19-R1, LV20-R1, LV21-R1, LV22-R1, ZZ99- |  | EPD | EPD
52 | 0DA | D01Q400 | 10.4.04 | 0DA10AP06 | 415V SWGR O/G MODULE # 0DA10FA | MISC. SERVICE MCC # 0SA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 70 | 101 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-02, MV94-02, MV95-02, MV34-L2, MA01-02, MR02-02, LV71-02, LV18-R1, LV19-R1, LV20-R1, LV21-R1, LV22-R1, ZZ99- |  | EPD | EPD
53 | 0DA | D01Q400 | 10.4.04 | 0DA10AP07 | 415V SWGR O/G MODULE # 0DA10FA | MISC. SERVICE MCC # 0SA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 70 | 101 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-02, MV94-02, MV95-02, MV34-L2, MA01-02, MR02-02, LV71-02, LV18-R1, LV19-R1, LV20-R1, LV21-R1, LV22-R1, ZZ99- |  | EPD | EPD
54 | 0DA | E04V0.5 | 10.7.02 | 0DA11BC01 | 415V SWGR O/G MODULE # 0DA11FB | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | 87 | 19.09.2019 | DR0817_4798-4G-34 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV51-03, MV50-03, MV49-03, MV48-03, MV47-03, MV46-R2, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
55 | 0DA | D01Q400 | 10.4.04 | 0DA11BP01 | 415V SWGR O/G MODULE # 0DA11FB | AC MCC # 0TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 101 | 101 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV56-R1, MV57-R1, MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, ZZ99- |  | EPD | EPD
56 | 0DA | D01Q400 | 10.4.04 | 0DA11BP02 | 415V SWGR O/G MODULE # 0DA11FB | AC MCC # 0TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 101 | 101 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV56-R1, MV57-R1, MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, ZZ99- |  | EPD | EPD
57 | 0DA | D01Q400 | 10.4.04 | 0DA11BP03 | 415V SWGR O/G MODULE # 0DA11FB | AC MCC # 0TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 101 | 101 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV56-R1, MV57-R1, MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-02, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, ZZ99- |  | EPD | EPD
58 | 0DA | D01Q400 | 10.4.04 | 0DA11BP04 | 415V SWGR O/G MODULE # 0DA11FB | AC MCC # 0TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 102 | 102 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV56-R1, MV57-R1, MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, ZZ99- |  | EPD | EPD
59 | 0DA | D01Q400 | 10.4.04 | 0DA11BP05 | 415V SWGR O/G MODULE # 0DA11FB | AC MCC # 0TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 102 | 102 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV56-R1, MV57-R1, MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, ZZ99- |  | EPD | EPD
60 | 0DA | D01Q400 | 10.4.04 | 0DA11BP06 | 415V SWGR O/G MODULE # 0DA11FB | AC MCC # 0TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 102 | 102 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV56-R1, MV57-R1, MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, ZZ99- |  | EPD | EPD
61 | 0DA | D01Q400 | 10.4.04 | 0DA11BP07 | 415V SWGR O/G MODULE # 0DA11FB | AC MCC # 0TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 102 | 102 | 10.09.2019 | DR1050_0006 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV56-R1, MV57-R1, MV58-L2, MV59-L2, MV60-L2, MV61-L2, MV46-L2, MV45-L2, MA07-02, MR08-02, DC07-02, DC08-02, DC09-02, DC10-02, DC11-02, DR03-03, AC01-02, AC04-02, AC09-02, AC13-02, DR07-02, AC14-L2, AC15-L2, ZZ99- |  | EPD | EPD
62 | 0DA | E04V0.5 | 10.7.02 | 0DA11CC01 | 415V SWGR O/G MODULE # 0DA11FC | DDCMIS # CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | 105 | 16.09.2019 | DR0817_4798-4G-87 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86) | OVERALL SCREENED | MV51-03, MV50-03, MV49-03, MV48-03, MV47-03, MV46-R2, MV45-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | EPD | EDN
63 | 0DA | D01Q400 | 10.4.04 | 0DA11CP01 | 415V SWGR O/G MODULE # 0DA11FC | VENTILATION & AIR WASHER MCC # 1TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 91 | 95 | 05.12.2019 | DR0968_0010 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-01, MV88-01, MV89-02, MV32-L2, MV31-L2, MV30-L2, MV29-R1, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ15-L1, BQ16-01, ZZ99- |  | EPD | EPD
64 | 0DA | D01Q400 | 10.4.04 | 0DA11CP02 | 415V SWGR O/G MODULE # 0DA11FC | VENTILATION & AIR WASHER MCC # 1TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 91 | 95 | 05.12.2019 | DR0968_0010 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-01, MV88-01, MV89-02, MV32-L2, MV31-L2, MV30-L2, MV29-R1, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ15-L1, BQ16-01, ZZ99- |  | EPD | EPD
65 | 0DA | D01Q400 | 10.4.04 | 0DA11CP03 | 415V SWGR O/G MODULE # 0DA11FC | VENTILATION & AIR WASHER MCC # 1TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 91 | 95 | 05.12.2019 | DR0968_0010 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-01, MV88-01, MV89-02, MV32-L2, MV31-L2, MV30-L2, MV29-R1, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ15-L1, BQ16-01, ZZ99- |  | EPD | EPD
66 | 0DA | D01Q400 | 10.4.04 | 0DA11CP04 | 415V SWGR O/G MODULE # 0DA11FC | VENTILATION & AIR WASHER MCC # 1TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 91 | 95 | 06.12.2019 | DR0968_0010 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-01, MV88-01, MV89-02, MV32-L2, MV31-L2, MV30-L2, MV29-L2, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ15-L1, BQ16-01, ZZ99- |  | EPD | EPD
67 | 0DA | D01Q400 | 10.4.04 | 0DA11CP05 | 415V SWGR O/G MODULE # 0DA11FC | VENTILATION & AIR WASHER MCC # 1TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 91 | 95 | 10.12.2019 | DR0968_0009 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-01, MV88-01, MV89-02, MV32-L2, MV31-L2, MV30-L2, MV29-L2, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ15-L1, BQ16-01, ZZ99- |  | EPD | EPD
68 | 0DA | D01Q400 | 10.4.04 | 0DA11CP06 | 415V SWGR O/G MODULE # 0DA11FC | VENTILATION & AIR WASHER MCC # 1TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 91 | 95 | 10.12.2019 | DR0968_0009 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-01, MV88-01, MV89-02, MV32-L2, MV31-L2, MV30-L2, MV29-L2, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ15-L1, BQ16-01, ZZ99- |  | EPD | EPD
69 | 0DA | D01Q400 | 10.4.04 | 0DA11CP07 | 415V SWGR O/G MODULE # 0DA11FC | VENTILATION & AIR WASHER MCC # 1TA SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 91 | 95 | 11.12.2019 | DR0968_0009 |  |  | POWER SUPPLY (800A) | XLPE-AL UNARMOURED | MV51-01, MV88-01, MV89-02, MV32-L2, MV31-L2, MV30-L2, MV29-R1, MV66-01, MV67-01, MV68-01, MA05-01, MR10-01, LR05-01, CC92-01, CC89-01, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-R1, BQ26-01, BQ15-L1, BQ16-01, ZZ99- |  | EPD | EPD
70 | 0DA | D3HQ185 | 10.4.21 | 0DA13BP01 | 415V SWGR O/G MODULE # 0DA13FB | UPS FEEDER | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 82 | 72 | 04.01.2020 | DR2687-1 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV56-L1, MV57-L1, MV58-R1, MV69-02, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV75-01, LV25-L1, LV74-02, DC07-03, ZZ99- |  | EPD | EDN
71 | 0DA | D3HQ185 | 10.4.21 | 0DA13BP02 | 415V SWGR O/G MODULE # 0DA13FB | UPS FEEDER | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 82 | 72 | 04.01.2020 | DR2687-1 |  |  | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | MV56-L1, MV57-L1, MV58-R1, MV69-02, MV70-02, MV71-02, MV29-R1, MV28-L2, MA06-02, MR09-02, LV75-01, LV25-L1, LV74-02, DC07-03, ZZ99- |  | EPD | EDN
72 | 0DA | D03Q095 | 10.4.15 | 0DA13CP01 | 415V SWGR O/G MODULE # 0DA13FC | FEEDER TO LDB - LV SWGR ROOM (1UC) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV56-L1, MV55-L1, MA03-01, MR04-01, LV70-01, LV33-L1, LV34-L1, LV35-L1, LV36-L1 |  | EPD | PEM
73 | 0DA | D03Q095 | 10.4.15 | 0DA13PP01 | 415V SWGR O/G MODULE # 0DA13RB | FEEDER TO WDB - MV SWGR ROOM (1UK) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 13 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV56-L1, MV93-01 |  | EPD | PEM
74 | 0DA | D03Q095 | 10.4.15 | 0DA13RP01 | 415V SWGR O/G MODULE # 0DA13RD | FEEDER TO LDB - MV SWGR ROOM (1UA) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV56-L1, MV55-L1 |  | EPD | PEM
75 | 0DA | D3HQ185 | 10.4.21 | 0DA14BP01 | 415V SWGR O/G MODULE # 0DA14FB | FEEDER TO CHIMNEY DB | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 418 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | MV56-L1, MV57-L1, MV58-R1, MV59-R1, MV62-05, MR06-05, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R4, IM32-R4, IM33-R4, IR31-R3, IM34-R4, IM35-R4, IM36-R4, IM37-R4, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99- |  | EPD | PEM
76 | 0DA | D3HQ185 | 10.4.21 | 0DA14BP02 | 415V SWGR O/G MODULE # 0DA14FB | FEEDER TO CHIMNEY DB | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 419 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | MV56-L1, MV57-L2, MV58-R1, MV59-R1, MV62-05, MR06-05, IM02-R3, IM94-R4, IM95-R4, IM96-R4, IM11-R4, IM12-R4, IM13-R4, IM14-R4, IM15-R4, IM16-R4, IM17-R4, IM18-R4, IM19-R4, IM20-R4, IM21-R4, IM32-R4, IM33-R4, IR31-R3, IM34-R4, IM35-R4, IM36-R4, IM37-R4, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99- |  | EPD | PEM
77 | 0DA | D03Q095 | 10.4.15 | 0DA14CP01 | 415V SWGR O/G MODULE # 0DA14FC | FEEDER TO LDB - MV SWGR ROOM (1UB) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV56-L1, MV55-L1, MA03-01, MR04-01, LV70-01, LV33-L1, LV60-01, LV31-L1, ZZ99- |  | EPD | PEM
78 | 0DA | D03Q095 | 10.4.15 | 0DA14DP01 | 415V SWGR O/G MODULE # 0DA14FD | FEEDER TO LDB - LV SWGR ROOM (1UD) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 41 | [5 empty] | POWER SUPPLY (100kVA) | XLPE-AL UNARMOURED | MV56-L1, MV55-L1, MA03-01, MR04-01, LV70-01, LV33-L1, LV34-L1 |  | EPD | PEM
1 | 0DB | E04V0.5 | 10.7.02 | 0DB02AC01 | 415V SWGR I/C MODULE # 0DB02FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 24 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | RV19-R2, RV20-R2, RV21-R2, RV22-R2, RV23-R2, ZZ99- |  | EPD | EDN
2 | 0DB | D02L2.5 | 10.4.24 | 0DB02AC02 | 415V SWGR I/C MODULE # 0DB02FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 14 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | RV19-L2, RV20-L2, ZZ99- |  | EPD | JHS
3 | 0DB | D02L2.5 | 10.4.24 | 0DB02AC03 | 415V SWGR I/C MODULE # 0DB02FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 14 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | RV19-L2, RV20-L2, ZZ99- |  | EPD | JHS
4 | 0DB | D02C1.5 | 10.5.01 | 0DB02AC04 | 415V SWGR I/C MODULE # 0DB02FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | RV19-L2, RV15-L2, RV09-L2, RV08-L2, RV07-L2, ZZ99- |  | EPD | BPL
5 | 0DB | E04V0.5 | 10.7.02 | 0DB02AC05 | 415V SWGR I/C MODULE # 0DB02FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 24 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | RV19-R2, RV20-R2, RV21-R2, RV22-R2, RV23-R2, ZZ99- |  | EPD | EDN
6 | 0DB | D04Q010 | 10.4.22 | 0DB03BP01 | 415V SWGR O/G MODULE # 0DB03FB | MOTORIZED BUTTERFLY VALVE WITH INTEGRAL STARTER-A | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
7 | 0DB | D3HQ050 | 10.4.19 | 0DB03CP01 | 415V SWGR O/G MODULE # 0DB03FC | TWS WITH SPRAY WASH SYSTEM | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
8 | 0DB | D04Q010 | 10.4.22 | 0DB03DP01 | 415V SWGR O/G MODULE # 0DB03FD | MOTORIZED BUTTERFLY VALVE WITH INTEGRAL STARTER-C | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
9 | 0DB | D02L2.5 | 10.4.24 | 0DB03EP01 | 415V SWGR O/G MODULE # 0DB03FE | PROPELLOR FAN-B (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | RV19-L2, RV45-R1, RV27-02, RV26-02, RV25-02, ZZ99- |  | EPD | PEM
10 | 0DB | D3HQ025 | 10.4.18 | 0DB03GP01 | 415V SWGR O/G MODULE # 0DB03FG | UNDER SLUNG SINGLE GIRDER 5 TON EOT CRANE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
11 | 0DB | D02C1.5 | 10.5.01 | 0DB03IC01 | 415V SWGR MOTOR MODULE # 0DB03FI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
12 | 0DB | D03L2.5 | 10.4.26 | 0DB03IP01 | 415V SWGR MOTOR MODULE # 0DB03FI | ALUM DOSING PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
13 | 0DB | D04Q010 | 10.4.22 | 0DB03QP01 | 415V SWGR O/G MODULE # 0DB03RC | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
14 | 0DB | D02Q010 | 10.4.06 | 0DB03RP01 | 415V SWGR O/G MODULE # 0DB03RD | SPLIT AC FOR CONTROL ROOM-A | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | RV19-R1, RV20-R1, RV21-R1, RV22-R1, ZZ99- |  | EPD | PEM
15 | 0DB | D04Q010 | 10.4.22 | 0DB03SP01 | 415V SWGR O/G MODULE # 0DB03RE | RW AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | RV19-R1, RV20-R1, RV21-R1, RV22-R1, RV23-R1, ZZ99- |  | EPD | EDN
16 | 0DB | D03L2.5 | 10.4.26 | 0DB03WP01 | 415V SWGR O/G MODULE # 0DB03RI | AXIAL FAN FOR PH-A1 (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
17 | 0DB | D3HQ025 | 10.4.18 | 0DB03XP01 | 415V SWGR O/G MODULE # 0DB03RJ | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
18 | 0DB | D02Q010 | 10.4.06 | 0DB04BP01 | 415V SWGR O/G MODULE # 0DB04FB | SPLIT AC FOR CONTROL ROOM-C | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | RV19-R1, RV45-L2, RV28-01, RV29-01, RV30-01, RV31-01, ZZ99- |  | EPD | PEM
19 | 0DB | D03L2.5 | 10.4.26 | 0DB04CP01 | 415V SWGR O/G MODULE # 0DB04FC | AXIAL FAN FOR PH-C1 (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
20 | 0DB | D03L2.5 | 10.4.26 | 0DB04DP01 | 415V SWGR O/G MODULE # 0DB04FD | AXIAL FAN FOR SWITCHGEAR ROOM-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | RV19-L2, RV45-R1, RV27-02, RV26-02, ZZ99- |  | EPD | PEM
21 | 0DB | D02C1.5 | 10.5.01 | 0DB04QC01 | 415V SWGR MOTOR MODULE # 0DB04RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
22 | 0DB | D03L2.5 | 10.4.26 | 0DB04QP01 | 415V SWGR MOTOR MODULE # 0DB04RC | FILTER FEED PUMP-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
23 | 0DB | D02Q010 | 10.4.06 | 0DB04RP01 | 415V SWGR O/G MODULE # 0DB04RD | SPLIT AC FOR CONTROL ROOM-E | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | RV19-R1, RV20-R1, RV21-R1, RV22-R1, RV23-R1, ZZ99- |  | EPD | PEM
24 | 0DB | D3HQ095 | 10.4.20 | 0DB04TP01 | 415V SWGR O/G MODULE # 0DB04RF | LP-1 | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
25 | 0DB | D03L2.5 | 10.4.26 | 0DB04UP01 | 415V SWGR O/G MODULE # 0DB04RG | AXIAL FAN FOR SWITCHGEAR ROOM-D | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | RV19-L2, RV45-R1, RV28-01, RV29-01, ZZ99- |  | EPD | PEM
26 | 0DB | D03L2.5 | 10.4.26 | 0DB05DP01 | 415V SWGR O/G MODULE # 0DB05FD | AXIAL FAN FOR PH-B2 (0.75kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
27 | 0DB | D03L2.5 | 10.4.26 | 0DB05EP01 | 415V SWGR O/G MODULE # 0DB05FE | AXIAL FAN FOR PH-D2 (0.75kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
28 | 0DB | D03L2.5 | 10.4.26 | 0DB05FP01 | 415V SWGR O/G MODULE # 0DB05FF | AXIAL FAN FOR BATTERY ROOM-B (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | RV19-L2, RV15-L2, RV10-L2, RV11-L2, ZZ99- |  | EPD | PEM
29 | 0DB | D3HQ025 | 10.4.18 | 0DB05HP01 | 415V SWGR O/G MODULE # 0DB05FH | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
30 | 0DB | D3HQ050 | 10.4.19 | 0DB05IP01 | 415V SWGR O/G MODULE # 0DB05FI | RW FLOAT-CUM-BOOST CHARGER- A | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | RV19-R1, RV15-L2, RV10-R1, RV11-R1, RV12-R1, RV13-R1, ZZ99- |  | EPD | PEM
31 | 0DB | D3HQ025 | 10.4.18 | 0DB05QP01 | 415V SWGR O/G MODULE # 0DB05RC | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | RV19-R1, RV45-L2, RV28-01, RV29-01, RV30-01, RV31-01, ZZ99- |  | EPD | EDN
32 | 0DB | D04Q010 | 10.4.22 | 0DB05RP01 | 415V SWGR O/G MODULE # 0DB05RD | RW AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | RV19-R1, RV20-R1, RV21-R1, RV22-R1, RV23-R1, ZZ99- |  | EPD | EDN
33 | 0DB | D03L2.5 | 10.4.26 | 0DB05UP01 | 415V SWGR O/G MODULE # 0DB05RG | AXIAL FAN FOR BATTERY ROOM-D (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | RV19-L2, RV15-L2, RV10-L2, RV11-L2, RV12-L2, ZZ99- |  | EPD | PEM
34 | 0DB | E04V0.5 | 10.7.02 | 0DB06AC01 | 415V SWGR B/C MODULE # 0DB06FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 24 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | RV19-R2, RV20-R2, RV21-R2, RV22-R2, RV23-R2, ZZ99- |  | EPD | EDN
35 | 0DB | E04V0.5 | 10.7.02 | 0DB06AC02 | 415V SWGR B/C MODULE # 0DB06FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 24 | [5 empty] | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | RV19-R2, RV20-R2, RV21-R2, RV22-R2, RV23-R2, ZZ99- |  | EPD | EDN
36 | 0DB | D04Q010 | 10.4.22 | 0DB07CP01 | 415V SWGR O/G MODULE # 0DB07FC | RW AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | RV16-L2, RV19-R1, RV20-R1, RV21-R1, RV22-R1, RV23-R1, ZZ99- |  | EPD | EDN
37 | 0DB | D03L2.5 | 10.4.26 | 0DB07FP01 | 415V SWGR O/G MODULE # 0DB07FF | AXIAL FAN FOR BATTERY ROOM-C (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | RV16-L2, RV15-L2, RV10-L2, RV11-L2, ZZ99- |  | EPD | PEM
38 | 0DB | D03L2.5 | 10.4.26 | 0DB07HP01 | 415V SWGR O/G MODULE # 0DB07FH | AXIAL FAN FOR PH-B1 (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
39 | 0DB | D02C1.5 | 10.5.01 | 0DB07JC01 | 415V SWGR MOTOR MODULE # 0DB07FJ | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
40 | 0DB | D03L2.5 | 10.4.26 | 0DB07JP01 | 415V SWGR MOTOR MODULE # 0DB07FJ | SUBMERSIBLE PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
41 | 0DB | D03L2.5 | 10.4.26 | 0DB07PP01 | 415V SWGR O/G MODULE # 0DB07RB | AXIAL FAN FOR BATTERY ROOM-A (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | RV16-L2, RV15-L2, RV10-L2, RV11-L2, RV12-L2, ZZ99- |  | EPD | PEM
42 | 0DB | D02C1.5 | 10.5.01 | 0DB07QC01 | 415V SWGR MOTOR MODULE # 0DB07RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
43 | 0DB | D03L2.5 | 10.4.26 | 0DB07QP01 | 415V SWGR MOTOR MODULE # 0DB07RC | FILTER FEED PUMP-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
44 | 0DB | D03L2.5 | 10.4.26 | 0DB07TP01 | 415V SWGR O/G MODULE # 0DB07RF | AXIAL FAN FOR PH-C2 (0.75kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
45 | 0DB | D03L2.5 | 10.4.26 | 0DB07UP01 | 415V SWGR O/G MODULE # 0DB07RG | AXIAL FAN FOR PH-A2 (0.75kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
46 | 0DB | D3HQ025 | 10.4.18 | 0DB08CP01 | 415V SWGR O/G MODULE # 0DB08FC | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
47 | 0DB | D02Q010 | 10.4.06 | 0DB08EP01 | 415V SWGR O/G MODULE # 0DB08FE | PORTABLE RO PLANT FOR PORTABLE WATER | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (6A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
48 | 0DB | D03L2.5 | 10.4.26 | 0DB08PP01 | 415V SWGR O/G MODULE # 0DB08RB | AXIAL FAN FOR SWITCHGEAR ROOM-C | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | RV16-L2, RV15-L2, RV10-L2, RV11-L2, ZZ99- |  | EPD | PEM
49 | 0DB | D3HQ050 | 10.4.19 | 0DB08QP01 | 415V SWGR O/G MODULE # 0DB08RC | RW FLOAT-CUM-BOOST CHARGER- B | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | RV16-L2, RV15-L2, RV10-R1, RV11-R1, RV12-R1, RV13-R1, RV14-R1, ZZ99- |  | EPD | PEM
50 | 0DB | D03L2.5 | 10.4.26 | 0DB08UP01 | 415V SWGR O/G MODULE # 0DB08RG | AXIAL FAN FOR SWITCHGEAR ROOM-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 34 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | RV16-L2, RV15-L2, RV09-L2, RV08-L2, RV07-L2, ZZ99- |  | EPD | PEM
51 | 0DB | D02Q010 | 10.4.06 | 0DB09CP01 | 415V SWGR O/G MODULE # 0DB09FC | SPLIT AC FOR CONTROL ROOM-F | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | RV16-L2, RV45-R1, RV28-01, RV29-01, RV30-01, RV31-01, RV32-01, ZZ99- |  | EPD | PEM
52 | 0DB | D02Q010 | 10.4.06 | 0DB09DP01 | 415V SWGR O/G MODULE # 0DB09FD | SPLIT AC FOR CONTROL ROOM-D | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | RV16-L2, RV19-R1, RV20-R1, RV21-R1, RV22-R1, ZZ99- |  | EPD | PEM
53 | 0DB | D02Q010 | 10.4.06 | 0DB09EP01 | 415V SWGR O/G MODULE # 0DB09FE | SPLIT AC FOR CONTROL ROOM-B | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | RV16-L2, RV45-R1, RV28-01, RV29-01, RV30-01, RV31-01, RV32-01, ZZ99- |  | EPD | PEM
54 | 0DB | D3HQ025 | 10.4.18 | 0DB09FP01 | 415V SWGR O/G MODULE # 0DB09FF | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | RV16-L2, RV45-R1, RV28-01, RV29-01, RV30-01, RV31-01, ZZ99- |  | EPD | EDN
55 | 0DB | D3HQ025 | 10.4.18 | 0DB09HP01 | 415V SWGR O/G MODULE # 0DB09FH | MOTORIZED GATE VALVE WITH INTEGRAL STARTER | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
56 | 0DB | D04Q010 | 10.4.22 | 0DB09IP01 | 415V SWGR O/G MODULE # 0DB09FI | RW AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | RV16-L2, RV19-R1, RV20-R1, RV21-R1, RV22-R1, RV23-R1, ZZ99- |  | EPD | EDN
57 | 0DB | D3HQ025 | 10.4.18 | 0DB09JP01 | 415V SWGR O/G MODULE # 0DB09FJ | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
58 | 0DB | D3HQ095 | 10.4.20 | 0DB09PP01 | 415V SWGR O/G MODULE # 0DB09RB | LP-2 | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (50 KVA) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
59 | 0DB | D04Q010 | 10.4.22 | 0DB09RP01 | 415V SWGR O/G MODULE # 0DB09RD | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
60 | 0DB | D02L2.5 | 10.4.24 | 0DB09SP01 | 415V SWGR O/G MODULE # 0DB09RE | PROPELLOR FAN-A (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | RV16-L2, RV17-L2, RV18-L2, RV24-02, RV25-02, ZZ99- |  | EPD | PEM
61 | 0DB | D04Q010 | 10.4.22 | 0DB09TP01 | 415V SWGR O/G MODULE # 0DB09RF | PORTABLE WATER PUMP FOR BD6 | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
62 | 0DB | D04Q010 | 10.4.22 | 0DB09VP01 | 415V SWGR O/G MODULE # 0DB09RH | MOTORIZED BUTTERFLY VALVE WITH INTEGRAL STARTER-B | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
63 | 0DB | D3HQ050 | 10.4.19 | 0DB09WP01 | 415V SWGR O/G MODULE # 0DB09RI | 10 TON ELECTRIC HOIST | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
64 | 0DB | E04V0.5 | 10.7.02 | 0DB10AC01 | 415V SWGR I/C MODULE # 0DB10FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | RV16-R2, RV19-R2, RV20-R2, RV21-R2, RV22-R2, RV23-R2, ZZ99- |  | EPD | EDN
65 | 0DB | D02L2.5 | 10.4.24 | 0DB10AC02 | 415V SWGR I/C MODULE # 0DB10FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 14 | [5 empty] | REF PROTECTION | XLPE-CU UNARMOURED | RV16-L2, RV17-L2, ZZ99- |  | EPD | JHS
66 | 0DB | D02L2.5 | 10.4.24 | 0DB10AC03 | 415V SWGR I/C MODULE # 0DB10FA | NEUTRAL CT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 14 | [5 empty] | SEF PROTECTION | XLPE-CU UNARMOURED | RV16-L2, RV17-L2, ZZ99- |  | EPD | JHS
67 | 0DB | D02C1.5 | 10.5.01 | 0DB10AC04 | 415V SWGR I/C MODULE # 0DB10FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 18 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | RV16-L2, RV15-L2, RV09-L2, ZZ99- |  | EPD | BPL
68 | 0DB | E04V0.5 | 10.7.02 | 0DB10AC05 | 415V SWGR I/C MODULE # 0DB10FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | RV16-R2, RV19-R2, RV20-R2, RV21-R2, RV22-R2, RV23-R2, ZZ99- |  | EPD | EDN
1 | 0SA | D04Q010 | 10.4.22 | 0SA01BP01 | 415V SWGR O/G MODULE # 0SA01FB | ELEVATOR MOTOR (TG HALL ELEVATOR M/C ROOM) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 72 | [5 empty] | POWER SUPPLY (16.5kW) | XLPE-AL UNARMOURED | LV23-R1, LV48-01, LV49-02, LV06-R1, LV54-02, TR23-01, TP01-01, TP02-01, ZZ99- |  | EPD | PEM
2 | 0SA | D02Q010 | 10.4.06 | 0SA01CP01 | 415V SWGR O/G MODULE # 0SA01FC | SG PANEL | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV23-R1, LV24-R2, LV25-R1, LV74-02, LR07-01, CC90-01, CC81-01, CC31-01, CC67-01, CC68-01, CC40-01, ZZ99- |  | EPD | EDN
3 | 0SA | D02L2.5 | 10.4.24 | 0SA01DP01 | 415V SWGR O/G MODULE # 0SA01FD | NEUTRAL GROUNDING CUBICLE | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | POWER SUPPLY (1.32kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-02, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP35-02, ZZ99- |  | EPD | PEM
4 | 0SA | D02L2.5 | 10.4.24 | 0SA01EP01 | 415V SWGR O/G MODULE # 0SA01FE | LAVT CUBICLE | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (1.32kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-02, TP39-02, TP38-02, ZZ99- |  | EPD | RUD
5 | 0SA | D3HQ095 | 10.4.20 | 0SA01FP01 | 415V SWGR O/G MODULE # 0SA01FF | TG HALL EOT CRANE | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 72 | [5 empty] | POWER SUPPLY (76kW) | XLPE-AL UNARMOURED | LV23-R1, LV48-01, LV49-02, LV06-R1, LV54-02, TR23-01, TP01-01, TP02-01, ZZ99- |  | EPD | PEM
6 | 0SA | D3HQ025 | 10.4.18 | 0SA01GP01 | 415V SWGR O/G MODULE # 0SA01FG | HOT AIR BLOWER (ISOLATED PHASE BUSDUCT) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (32kW) | XLPE-AL UNARMOURED | LV23-R1, LV22-R1, LV21-R1, LV20-R2, LV19-R2, LV18-R2, LV71-02, LR02-02, TY14-R1, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, TR38-01, TP39-01, TP38-01, ZZ99- |  | EPD | RUD
7 | 0SA | D04Q010 | 10.4.22 | 0SA01QP01 | 415V SWGR O/G MODULE # 0SA01RC | INSTRUMENT AIR COMPRESSOR AUX. SUPPLY | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 204 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV23-L2, LV22-L1, LV21-L2, LV20-L3, LV19-L2, LV18-L2, LV71-03, LR02-02, TY14-R1, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, CM07-R1, CM08-R1, CM09-R1, CM13-02, CM22-02, CM24-02, CM26-02, ZZ99- |  | EPD | PEM
8 | 0SA | D02L2.5 | 10.4.24 | 0SA01RP01 | 415V SWGR O/G MODULE # 0SA01RD | COMMON SEQUENCING PANEL - AUX. | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 220 | [5 empty] | POWER SUPPLY (0.6kW) | XLPE-CU UNARMOURED | LV23-L4, LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV18-L4, LV71-03, LR02-03, TY14-L4, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM06-L3, CM07-L3, CM08-L3, CM09-L3, CM13-02, CM22-04, CM24-04, CM26-04, CM28-04, ZZ99- |  | EPD | PEM
9 | 0SA | D04Q010 | 10.4.22 | 0SA01SP01 | 415V SWGR O/G MODULE # 0SA01RE | SERVICE AIR COMPRESSOR AUX. SUPPLY | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 208 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV23-L2, LV22-L1, LV21-L2, LV20-L3, LV19-L2, LV18-L2, LV71-03, LR02-02, TY14-R1, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, CM07-R1, CM08-R1, CM09-R1, CM13-02, CM22-02, CM24-02, CM26-02, CM28-02, ZZ99- |  | EPD | PEM
10 | 0SA | D04Q010 | 10.4.22 | 0SA01TP01 | 415V SWGR O/G MODULE # 0SA01RF | SUMP PUMP (MRS) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 243 | [5 empty] | POWER SUPPLY (2.5kW) | XLPE-AL UNARMOURED | LV23-L2, LV43-02, LV44-03, LV76-01, LV79-02, LR10-R2, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IC07-R1, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IR13-02, IC30-02, IC31-01, ZZ99- |  | EPD | PEM
11 | 0SA | D03L2.5 | 10.4.26 | 0SA01WP01 | 415V SWGR O/G MODULE # 0SA01RI | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 163 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-02, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP40-02, TP41-02, ZZ99- |  | EPD | PEM
12 | 0SA | D04Q010 | 10.4.22 | 0SA02CP01 | 415V SWGR O/G MODULE # 0SA02FC | SPACE HEATER FOR SPBD | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV23-L2, LV48-01, LV11-R3, LV12-R2, LV13-R2, LV63-04, LV03-L1, LV02-L1, LV01-01, MR01-02, ZZ99- |  | EPD | RUD
13 | 0SA | D03L2.5 | 10.4.26 | 0SA02DP01 | 415V SWGR O/G MODULE # 0SA02FD | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 152 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV43-03, LV09-L4, LV08-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TG43-02, TG48-02, ZZ99- |  | EPD | PEM
14 | 0SA | D3HQ025 | 10.4.18 | 0SA02EP01 | 415V SWGR O/G MODULE # 0SA02FE | AUX. POWER SUPPLY FOR ST # 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV23-R1, LV22-R1, LV21-R1, LV20-R2, LV19-R2, LV67-01, LV66-01, LV70-01, LR04-01, TY17-L2, TY18-R2, YR02-02, TY25-02, TY26-02, TY28-02, ZZ99- |  | EPD | JHS
15 | 0SA | D3HQ185 | 10.4.21 | 0SA02FP01 | 415V SWGR O/G MODULE # 0SA02FF | TRANSFORMER OIL FILTRATION M/C | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 161 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | LV23-R1, LV48-02, LV11-R3, LV12-R2, LV13-R2, LV14-R1, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-01, TY04-01, TY05-01, TY06-01, ZZ99- |  | EPD | PEM
16 | 0SA | D3HQ185 | 10.4.21 | 0SA02FP02 | 415V SWGR O/G MODULE # 0SA02FF | TRANSFORMER OIL FILTRATION M/C | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 161 | [5 empty] | POWER SUPPLY (250A) | XLPE-AL UNARMOURED | LV23-R1, LV48-03, LV11-R3, LV12-R2, LV13-R2, LV14-R1, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-01, TY04-01, TY05-01, TY06-01, ZZ99- |  | EPD | PEM
17 | 0SA | D3HQ025 | 10.4.18 | 0SA02GP01 | 415V SWGR O/G MODULE # 0SA02FG | AUX. POWER SUPPLY FOR UT # 1A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV23-R1, LV48-01, LV11-R3, LV12-R2, LV13-R2, LV63-03, LV03-L1, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-02, TY04-02, TY05-02, ZZ99- |  | EPD | JHS
18 | 0SA | D03L2.5 | 10.4.26 | 0SA02HP01 | 415V SWGR O/G MODULE # 0SA02FH | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR25-05, TP55-02, TP56-02, TP58-02, ZZ99- |  | EPD | PEM
19 | 0SA | D02C1.5 | 10.5.01 | 0SA02PC01 | 415V SWGR MOTOR MODULE # 0SA02RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | EPD
20 | 0SA | D03L2.5 | 10.4.26 | 0SA02PP01 | 415V SWGR MOTOR MODULE # 0SA02RB | TANK AGITATOR MOTOR (AGM 1) (HYDRAZINE DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | PEM
21 | 0SA | D03L2.5 | 10.4.26 | 0SA02QP01 | 415V SWGR O/G MODULE # 0SA02RC | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 163 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-02, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP40-02, TP41-02, ZZ99- |  | EPD | PEM
22 | 0SA | D02L2.5 | 10.4.24 | 0SA02RP01 | 415V SWGR O/G MODULE # 0SA02RD | AIR DRYER-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 195 | [5 empty] | POWER SUPPLY (0.5kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM11-02, CM18-02, CM19-02, CM20-02, ZZ99- |  | EPD | PEM
23 | 0SA | D02L2.5 | 10.4.24 | 0SA02SP01 | 415V SWGR O/G MODULE # 0SA02RE | INSTRUMENT AIR RECEIVER-1 ADT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 193 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM10-02, CM14-02, CM15-02, CM16-02, ZZ99- |  | EPD | PEM
24 | 0SA | D03L2.5 | 10.4.26 | 0SA02TP01 | 415V SWGR O/G MODULE # 0SA02RF | SUPPLY FAN FOR MCC ROOM FOR COMPRESSOR HOUSE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 192 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM11-02, ZZ99- |  | EPD | PEM
25 | 0SA | D02C1.5 | 10.5.01 | 0SA02VC01 | 415V SWGR MOTOR MODULE # 0SA02RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | EPD
26 | 0SA | D03L2.5 | 10.4.26 | 0SA02VP01 | 415V SWGR MOTOR MODULE # 0SA02RH | TANK AGITATOR MOTOR (AGM 1) (AMMONIA DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | PEM
27 | 0SA | D3HQ025 | 10.4.18 | 0SA02WP01 | 415V SWGR O/G MODULE # 0SA02RI | AUX. POWER SUPPLY FOR UT # 1B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 134 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV23-R1, LV48-02, LV11-R3, LV12-R2, LV13-R2, LV63-03, LV03-L1, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-02, TY04-02, ZZ99- |  | EPD | JHS
28 | 0SA | D03L2.5 | 10.4.26 | 0SA03BP01 | 415V SWGR O/G MODULE # 0SA03FB | SUPPLY FAN FOR MCC ROOM FOR COMPRESSOR HOUSE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 197 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM06-L3, CM07-L3, CM12-02, ZZ99- |  | EPD | PEM
29 | 0SA | D02L2.5 | 10.4.24 | 0SA03CP01 | 415V SWGR O/G MODULE # 0SA03FC | SERVICE AIR RECEIVER-1 ADT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM10-02, CM14-02, ZZ99- |  | EPD | PEM
30 | 0SA | D02L2.5 | 10.4.24 | 0SA03DP01 | 415V SWGR O/G MODULE # 0SA03FD | UNIT AIR RECEIVER-1 ADT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 195 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM11-02, CM18-02, CM19-02, CM20-02, ZZ99- |  | EPD | PEM
31 | 0SA | D02L2.5 | 10.4.24 | 0SA03EP01 | 415V SWGR O/G MODULE # 0SA03FE | GRP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC42-03, CC43-03, CC52-02, CC51-02, ZZ99- |  | EPD | BPL
32 | 0SA | D04Q010 | 10.4.22 | 0SA03FP01 | 415V SWGR O/G MODULE # 0SA03FF | LCP (NaOH DOSING) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 140 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV23-L2, LV48-03, LV11-R3, LV12-R2, LV13-R2, LV63-04, LV64-04, TR25-01, TP55-01, TP54-01, TP52-01, TP49-01, TP03-01, TP04-01, TR26-01, TR40-01, TD18-01, TD28-01, TR45-01, TD29-01, TD30-01, TD31-01, TD32-01, ZZ99- |  | EPD | PEM
33 | 0SA | D02L2.5 | 10.4.24 | 0SA03GP01 | 415V SWGR O/G MODULE # 0SA03FG | DATA CONCENTRATOR (HT & LT) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 69 | 55 | 13.2.20 | DR1095_0006 |  |  | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC82-02, CC83-03, CC84-03, CC86-03, CC88-03, CC92-03, ZZ99- |  | EPD | EPD
34 | 0SA | D3HQ025 | 10.4.18 | 0SA03HP01 | 415V SWGR O/G MODULE # 0SA03FH | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
35 | 0SA | D02L2.5 | 10.4.24 | 0SA03IP01 | 415V SWGR O/G MODULE # 0SA03FI | AUX. POWER SUPLY FOR UST # 1DAT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 23 | 110 | 16.01.20 | DR1095_0006 |  |  | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV23-L4, ZZ99- |  | EPD | JHS
36 | 0SA | D02C1.5 | 10.5.01 | 0SA03PC01 | 415V SWGR MOTOR MODULE # 0SA03RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, ZZ99- |  | EPD | EPD
37 | 0SA | D03L2.5 | 10.4.26 | 0SA03PP01 | 415V SWGR MOTOR MODULE # 0SA03RB | OIL SKIMMER FOR WASH WATER COLLECTION SUMP-1 FOR TG HALL ARE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV23-L4, ZZ99- |  | EPD | PEM
38 | 0SA | D02L2.5 | 10.4.24 | 0SA03QP01 | 415V SWGR O/G MODULE # 0SA03RC | AUX. POWER SUPLY FOR SST # 0DAT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | 97 | 16.01.20 | DR1095_0006 |  |  | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV23-L4, LV22-L4, ZZ99- |  | EPD | JHS
39 | 0SA | D02L2.5 | 10.4.24 | 0SA03RP01 | 415V SWGR O/G MODULE # 0SA03RD | S.H. SUPLY FOR NSPBD FOR 1DAT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV23-L4, LV22-L4, ZZ99- |  | EPD | JHS
40 | 0SA | D02L2.5 | 10.4.24 | 0SA03SP01 | 415V SWGR O/G MODULE # 0SA03RE | S.H. SUPLY FOR NSPBD FOR 0DAT01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV23-L4, LV22-L4, ZZ99- |  | EPD | JHS
41 | 0SA | D04Q010 | 10.4.22 | 0SA03TP01 | 415V SWGR O/G MODULE # 0SA03RF | LCP (HYDRAZINE DOSING) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 23 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV23-L2, LV22-L1, ZZ99- |  | EPD | PEM
42 | 0SA | D02C1.5 | 10.5.01 | 0SA03VC01 | 415V SWGR MOTOR MODULE # 0SA03RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | EPD
43 | 0SA | D03L2.5 | 10.4.26 | 0SA03VP01 | 415V SWGR MOTOR MODULE # 0SA03RH | BULK AMMONIA CUM TRANSFER - CENTRIFUGAL PUMP MOTOR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | PEM
44 | 0SA | D3HQ025 | 10.4.18 | 0SA03WP01 | 415V SWGR O/G MODULE # 0SA03RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
45 | 0SA | D02C1.5 | 10.5.01 | 0SA04PC01 | 415V SWGR MOTOR MODULE # 0SA04RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV63-05, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | EPD
46 | 0SA | D03L2.5 | 10.4.26 | 0SA04PP01 | 415V SWGR MOTOR MODULE # 0SA04RB | MOTOR FOR DOSING PUMP (NAOH DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV63-05, LV64-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | PEM
47 | 0SA | D02C1.5 | 10.5.01 | 0SA04QC01 | 415V SWGR MOTOR MODULE # 0SA04RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 139 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | EPD
48 | 0SA | D03L2.5 | 10.4.26 | 0SA04QP01 | 415V SWGR MOTOR MODULE # 0SA04RC | MOTOR FOR DOSING PUMP (HYDRAZINE DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | PEM
49 | 0SA | D02C1.5 | 10.5.01 | 0SA04RC01 | 415V SWGR MOTOR MODULE # 0SA04RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV67-02, LV66-02, LV70-03, LR04-03, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, ZZ99- |  | EPD | EPD
50 | 0SA | D03Q010 | 10.4.11 | 0SA04RP01 | 415V SWGR MOTOR MODULE # 0SA04RD | TRANSFORMER YARD AREA WASTE WATER TRANSFER PUMP (P5A) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 169 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV23-L2, LV22-L1, LV21-L2, LV20-L3, LV19-L2, LV67-01, LV66-01, LV70-01, LR04-01, TY17-L2, TY18-R2, YR02-02, TY25-02, TY26-02, TY28-02, TY29-02, TY30-02, TY31-02, ZZ99- |  | EPD | PEM
51 | 0SA | D3HQ025 | 10.4.18 | 0SA04VP01 | 415V SWGR O/G MODULE # 0SA04RH | S.H. SUPPLY FOR 6.6kV UNIT SWBD # 1CA | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 59 | 67 | 29.12.19 | DR0822_0003 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV23-R1, LV48-02, LV11-R3, LV12-R2, LV13-R2, LV63-03, LV64-04, TR48-04, MR16-03, MV99-02, MV02-L2, ZZ99- |  | EPD | BPL
52 | 0SA | D3HQ025 | 10.4.18 | 0SA04WP01 | 415V SWGR O/G MODULE # 0SA04RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
53 | 0SA | D02L2.5 | 10.4.24 | 0SA05BP01 | 415V SWGR O/G MODULE # 0SA05FB | MASTER SLAVE CLOCK SYSTEM | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC23-03, CC22-03, CC14-02, CC15-02, ZZ99- |  | EPD | EDN
54 | 0SA | D02L2.5 | 10.4.24 | 0SA05CP01 | 415V SWGR O/G MODULE # 0SA05FC | HMI NETWORK PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC34-02, ZZ99- |  | EPD | EDN
55 | 0SA | D02L2.5 | 10.4.24 | 0SA05DP01 | 415V SWGR O/G MODULE # 0SA05FD | HMI NETWORK PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC34-02, ZZ99- |  | EPD | EDN
56 | 0SA | D3HQ050 | 10.4.19 | 0SA06BP01 | 415V SWGR O/G MODULE # 0SA06FB | GCB # 1 | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (100A) | XLPE-AL UNARMOURED | LV23-R1, LV48-01, LV11-R3, LV12-R2, LV13-R2, LV14-R1, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, TR38-01, TP39-01, TP38-01, TP37-01, TP36-01, TR30-01, TP35-01, TP34-01, TP33-01, ZZ99- |  | EPD | PEM
57 | 0SA | D02L2.5 | 10.4.24 | 0SA06CP01 | 415V SWGR O/G MODULE # 0SA06FC | BOP PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 61 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC23-03, CC22-03, CC14-02, CC15-02, ZZ99- |  | EPD | EDN
58 | 0SA | D02L2.5 | 10.4.24 | 0SA06DP01 | 415V SWGR O/G MODULE # 0SA06FD | BOP PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV42-03, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | EDN
59 | 0SA | D02L2.5 | 10.4.24 | 0SA06EP01 | 415V SWGR O/G MODULE # 0SA06FE | S.H. SUPPLY FOR 415V UNIT EMER. MCC # 1DG | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV47-04, LV46-04, LV38-R3, ZZ99- |  | EPD | EPD
60 | 0SA | D3HQ025 | 10.4.18 | 0SA06HP01 | 415V SWGR O/G MODULE # 0SA06FH | S.H. SUPPLY FOR 6.6kV UNIT SWBD # 1CB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 69 | 67 | 29.12.19 | DR0822_0003 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV23-R1, LV48-03, LV11-R3, LV12-R2, LV13-R2, LV63-03, LV64-04, TR48-04, MR16-03, MV99-02, MV98-02, MV97-02, MV96-02, MV34-L2, MV18-L2, ZZ99- |  | EPD | BPL
61 | 0SA | D02L2.5 | 10.4.24 | 0SA06IP01 | 415V SWGR O/G MODULE # 0SA06FI | BOP PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 59 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC23-03, CC21-02, CC20-02, ZZ99- |  | EPD | EDN
62 | 0SA | D3HQ025 | 10.4.18 | 0SA06PP01 | 415V SWGR O/G MODULE # 0SA06RB | S.H. SUPPLY FOR 6.6kV STATION SWBD # 0CA | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 77 | 80 | 29.12.19 | DR0822_0003 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV23-R1, LV42-01, LV27-R1, LV81-R1, LV73-02, MR07-01, MA08-01, MV61-L2, MV47-01, MV48-01, MV49-01, MV50-01, MV88-01, MV38-01, ZZ99- |  | EPD | BPL
63 | 0SA | D02C1.5 | 10.5.01 | 0SA06QC01 | 415V SWGR MOTOR MODULE # 0SA06RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV63-05, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | EPD
64 | 0SA | D03L2.5 | 10.4.26 | 0SA06QP01 | 415V SWGR MOTOR MODULE # 0SA06RC | AGITATOR MOTOR (AGM 1) (NaOH DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV63-05, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | PEM
65 | 0SA | D02C1.5 | 10.5.01 | 0SA06RC01 | 415V SWGR MOTOR MODULE # 0SA06RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG07-03, ZZ99- |  | EPD | EPD
66 | 0SA | D03Q010 | 10.4.11 | 0SA06RP01 | 415V SWGR MOTOR MODULE # 0SA06RD | WASH WATER TRANSFER PUMP FOR TG HALL AREA (P1A) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG07-03, ZZ99- |  | EPD | PEM
67 | 0SA | D02L2.5 | 10.4.24 | 0SA06SP01 | 415V SWGR O/G MODULE # 0SA06RE | S.H. SUPPLY FOR 220V DCDB # 1FA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 26 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, ZZ99- |  | EPD | EPD
68 | 0SA | D02L2.5 | 10.4.24 | 0SA06TP01 | 415V SWGR O/G MODULE # 0SA06RF | S.H. SUPPLY FOR NGR ST # 1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV67-02, LV66-02, LV70-03, LR04-03, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, ZZ99- |  | EPD | JHS
69 | 0SA | D02L2.5 | 10.4.24 | 0SA06UP01 | 415V SWGR O/G MODULE # 0SA06RG | S.H. SUPPLY FOR NGR UT # 1A | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 148 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, ZZ99- |  | EPD | JHS
70 | 0SA | D3HQ025 | 10.4.18 | 0SA06VP01 | 415V SWGR O/G MODULE # 0SA06RH | S.H. SUPPLY FOR 6.6kV COMP. SWBD # 1CC | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV23-R1, LV48-03, LV11-R3, LV12-R2, LV13-R2, LV63-03, LV03-L1, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, CM07-R1, CM08-R1, ZZ99- |  | EPD | BPL
71 | 0SA | D3HQ025 | 10.4.18 | 0SA06WP01 | 415V SWGR O/G MODULE # 0SA06RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
72 | 0SA | D02C1.5 | 10.5.01 | 0SA07RC01 | 415V SWGR MOTOR MODULE # 0SA07RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-R3, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IC07-R3, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, ZZ99- |  | EPD | EPD
73 | 0SA | D03Q010 | 10.4.11 | 0SA07RP01 | 415V SWGR MOTOR MODULE # 0SA07RD | CLEAR WATER TRANSFER PUMP (P4A) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-R3, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IC07-R3, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, ZZ99- |  | EPD | PEM
74 | 0SA | D3HQ050 | 10.4.19 | 0SA08BP01 | 415V SWGR O/G MODULE # 0SA08FB | AUX. POWER SUPLY FOR GT # 1 | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY (100A) | XLPE-AL UNARMOURED | LV22-L1, LV21-L2, LV20-L2, LV19-L2, LV68-01, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-01, TY04-01, TY05-01, TY06-01, ZZ99- |  | EPD | BPL
75 | 0SA | D02C1.5 | 10.5.01 | 0SA08CC01 | 415V SWGR MOTOR MODULE # 0SA08FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 229 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC82-02, CC83-03, CC84-03, CC86-03, CC88-03, CC92-03, LR05-03, LV79-03, LR10-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA05-02, BA07-02, BA08-02, BA09-02, BR35-02, ZZ99- |  | EPD | EPD
76 | 0SA | D03Q010 | 10.4.11 | 0SA08CP01 | 415V SWGR MOTOR MODULE # 0SA08FC | WASH WATER TRANSFER PUMP FOR BOILER AREA (P2A) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 229 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC82-02, CC83-03, CC84-03, CC86-03, CC88-03, CC92-03, LR05-03, LV79-03, LR10-L4, IC01-L5, IC02-L5, IC03-L4, IC04-L4, IC05-L4, IC06-L4, IR07-03, IC50-03, IC51-03, IC52-03, BR16-02, BA01-02, BA02-02, BA03-02, BA04-02, BA05-02, BA07-02, BA08-02, BA09-02, BR35-02, ZZ99- |  | EPD | PEM
77 | 0SA | D02L2.5 | 10.4.24 | 0SA08DP01 | 415V SWGR O/G MODULE # 0SA08FD | SLAVE CLOCK | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (0.3A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC23-03, CC22-03, CC14-02, CC15-02, ZZ99- |  | EPD | EDN
78 | 0SA | D02L2.5 | 10.4.24 | 0SA08EP01 | 415V SWGR O/G MODULE # 0SA08FE | SLAVE CLOCK | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | POWER SUPPLY (0.3A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC69-03, CC45-02, ZZ99- |  | EPD | EDN
79 | 0SA | D02C1.5 | 10.5.01 | 0SA08GC01 | 415V SWGR MOTOR MODULE # 0SA08FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 249 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, ZZ99- |  | EPD | EPD
80 | 0SA | D03Q010 | 10.4.11 | 0SA08GP01 | 415V SWGR MOTOR MODULE # 0SA08FG | WASTER WATER TRANSFER PUMP (P1A) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 249 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, ZZ99- |  | EPD | PEM
81 | 0SA | D02C1.5 | 10.5.01 | 0SA08HC01 | 415V SWGR MOTOR MODULE # 0SA08FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR25-05, TP55-02, TP59-02, ZZ99- |  | EPD | EPD
82 | 0SA | D03L2.5 | 10.4.26 | 0SA08HP01 | 415V SWGR MOTOR MODULE # 0SA08FH | LUBE OIL PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR25-05, TP55-02, TP59-02, ZZ99- |  | EPD | PEM
83 | 0SA | D02L2.5 | 10.4.24 | 0SA08IP01 | 415V SWGR O/G MODULE # 0SA08FI | 24V DC CHARGER (UNIT) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (2A) | XLPE-CU UNARMOURED | LV22-L4, LV48-04, LV49-04, LV07-L4, ZZ99- |  | EPD | EDN
84 | 0SA | D02C1.5 | 10.5.01 | 0SA08QC01 | 415V SWGR MOTOR MODULE # 0SA08RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 139 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | EPD
85 | 0SA | D03L2.5 | 10.4.26 | 0SA08QP01 | 415V SWGR MOTOR MODULE # 0SA08RC | MOTOR FOR DOSING PUMP (AMMONIA DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | PEM
86 | 0SA | D02L2.5 | 10.4.24 | 0SA08SP01 | 415V SWGR O/G MODULE # 0SA08RE | HMI NETWORK PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC33-03, CC34-02, ZZ99- |  | EPD | EDN
87 | 0SA | D02L2.5 | 10.4.24 | 0SA08TP01 | 415V SWGR O/G MODULE # 0SA08RF | BOP PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC24-02, CC25-02, ZZ99- |  | EPD | EDN
88 | 0SA | E04V0.5 | 10.7.02 | 0SA09AC01 | 415V SWGR I/C MODULE # 0SA09FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 64 | 29.11.2019 | DR0720_4798-4G-83 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
89 | 0SA | D02C1.5 | 10.5.01 | 0SA09AC02 | 415V SWGR I/C MODULE # 0SA09FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV22-L4, LV51-02, LV50-02, LV36-L4, LV72-04, LR11-L3, MR05-L3, MV76-03, MV77-03, MV50-02, ZZ99- |  | EPD | BPL
90 | 0SA | E04V0.5 | 10.7.02 | 0SA09AC03 | 415V SWGR I/C MODULE # 0SA09FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 64 | 29.11.2019 | DR0720_4798-4G-83 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
91 | 0SA | E04V0.5 | 10.7.02 | 0SA10AC01 | 415V SWGR B/C MODULE # 0SA10FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 64 | 29.11.2019 | DR0720_4798-4G-83 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
92 | 0SA | E04V0.5 | 10.7.02 | 0SA10AC02 | 415V SWGR B/C MODULE # 0SA10FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 65 | 29.11.2019 | DR0720_4798-4G-83 |  |  | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
93 | 0SA | E04V0.5 | 10.7.02 | 0SA11AC01 | 415V SWGR I/C MODULE # 0SA11FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 64 | 29.11.2019 | DR0720_4798-4G-83 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
94 | 0SA | D02C1.5 | 10.5.01 | 0SA11AC02 | 415V SWGR I/C MODULE # 0SA11FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | LV22-L4, LV51-02, LV50-02, LV36-L4, LV72-04, LR11-L3, MR05-L3, MV76-03, MV77-03, MV50-02, ZZ99- |  | EPD | BPL
95 | 0SA | E04V0.5 | 10.7.02 | 0SA11AC03 | 415V SWGR I/C MODULE # 0SA11FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 64 | 29.11.2019 | DR0720_4798-4G-83 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
96 | 0SA | D02C1.5 | 10.5.01 | 0SA12PC01 | 415V SWGR MOTOR MODULE # 0SA12RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 139 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | EPD
97 | 0SA | D03L2.5 | 10.4.26 | 0SA12PP01 | 415V SWGR MOTOR MODULE # 0SA12RB | TANK AGITATOR MOTOR (AGM 2) (AMMONIA DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | PEM
98 | 0SA | D02C1.5 | 10.5.01 | 0SA12QC01 | 415V SWGR MOTOR MODULE # 0SA12RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-R3, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IC07-R3, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, ZZ99- |  | EPD | EPD
99 | 0SA | D03Q010 | 10.4.11 | 0SA12QP01 | 415V SWGR MOTOR MODULE # 0SA12RC | CLEAR WATER TRANSFER PUMP (P4B) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-R3, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IC07-R3, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, ZZ99- |  | EPD | PEM
100 | 0SA | D3HQ025 | 10.4.18 | 0SA12UP01 | 415V SWGR O/G MODULE # 0SA12RG | S.H. SUPPLY FOR 6.6kV STATION SWBD # 0CA | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 60 | 74 | 29.12.19 | DR0822_0003 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV22-L1, LV21-L2, LV20-L2, LV19-L2, LV67-01, LV66-01, LV70-01, MR04-01, MA03-01, MV54-L1, MV53-L1, MV37-01, ZZ99- |  | EPD | BPL
101 | 0SA | D3HQ025 | 10.4.18 | 0SA12WP01 | 415V SWGR O/G MODULE # 0SA12RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
102 | 0SA | D3HQ025 | 10.4.18 | 0SA13CP01 | 415V SWGR O/G MODULE # 0SA13FC | S.H. SUPPLY FOR 6.6kV COMP. SWBD # 1CC | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 171 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV22-L1, LV21-L2, LV20-L3, LV62-03, LV63-03, LV03-L1, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, ZZ99- |  | EPD | BPL
103 | 0SA | D02C1.5 | 10.5.01 | 0SA13VC01 | 415V SWGR MOTOR MODULE # 0SA13RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-03, IC46-03, IC47-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-02, BA21-02, BA22-02, BA23-02, BR33-02, ZZ99- |  | EPD | EPD
104 | 0SA | D03L2.5 | 10.4.26 | 0SA13VP01 | 415V SWGR MOTOR MODULE # 0SA13RH | OIL SKIMMER FOR WASH WATER COLLECTION SUMP-2 FOR BOILER AREA | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-02, BA21-02, BA22-02, BA23-02, BR33-02, ZZ99- |  | EPD | PEM
131 | 0SA | D02L2.5 | 10.4.24 | 0SA14BP01 | 415V SWGR O/G MODULE # 0SA14FB | BTS-1 1CA - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC69-03, CC70-03, CC50-03, ZZ99- |  | EPD | BPL
105 | 0SA | D3HQ025 | 10.4.18 | 0SA14GP01 | 415V SWGR O/G MODULE # 0SA14FG | S.H. SUPPLY FOR 6.6kV UNIT SWBD # 1CB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 59 | 62 | 29.12.19 | DR0822_0003 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV22-L1, LV21-L2, LV20-L3, LV62-03, LV63-04, LV64-04, TR48-04, MR16-03, MV99-02, MV98-02, MV97-02, MV20-01, ZZ99- |  | EPD | BPL
106 | 0SA | D02C1.5 | 10.5.01 | 0SA14HC01 | 415V SWGR MOTOR MODULE # 0SA14FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV13-R3, LV63-05, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | EPD
107 | 0SA | D03L2.5 | 10.4.26 | 0SA14HP01 | 415V SWGR MOTOR MODULE # 0SA14FH | AGITATOR MOTOR (AGM 2) (NaOH DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV13-R3, LV63-05, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | PEM
108 | 0SA | D3HQ025 | 10.4.18 | 0SA14IP01 | 415V SWGR O/G MODULE # 0SA14FI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
109 | 0SA | D02C1.5 | 10.5.01 | 0SA14PC01 | 415V SWGR MOTOR MODULE # 0SA14RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 139 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | EPD
110 | 0SA | D03L2.5 | 10.4.26 | 0SA14PP01 | 415V SWGR MOTOR MODULE # 0SA14RB | MOTOR FOR DOSING PUMP (AMMONIA DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | PEM
111 | 0SA | D02C1.5 | 10.5.01 | 0SA14QC01 | 415V SWGR MOTOR MODULE # 0SA14RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 249 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, ZZ99- |  | EPD | EPD
112 | 0SA | D03Q010 | 10.4.11 | 0SA14QP01 | 415V SWGR MOTOR MODULE # 0SA14RC | WASTER WATER TRANSFER PUMP (P1B) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 249 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, ZZ99- |  | EPD | PEM
113 | 0SA | D3HQ025 | 10.4.18 | 0SA14UP01 | 415V SWGR O/G MODULE # 0SA14RG | S.H. SUPPLY FOR 6.6kV UNIT SWBD # 1CA | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 51 | 58 | 29.12.19 | DR0822_0003 |  |  | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | LV22-L1, LV21-L2, LV20-L2, LV62-03, LV63-03, LV64-04, TR48-03, MR16-03, MV99-02, MV98-02, MV15-02, ZZ99- |  | EPD | BPL
114 | 0SA | D02C1.5 | 10.5.01 | 0SA14VC01 | 415V SWGR MOTOR MODULE # 0SA14RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 131 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | EPD
115 | 0SA | D03L2.5 | 10.4.26 | 0SA14VP01 | 415V SWGR MOTOR MODULE # 0SA14RH | MOTOR FOR DOSING PUMP (HYDRAZINE DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 144 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | PEM
116 | 0SA | D3HQ025 | 10.4.18 | 0SA14WP01 | 415V SWGR O/G MODULE # 0SA14RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
117 | 0SA | D02L2.5 | 10.4.24 | 0SA15BP01 | 415V SWGR O/G MODULE # 0SA15FB | SLAVE CLOCK | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (0.3A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC40-02, ZZ99- |  | EPD | EDN
118 | 0SA | D02L2.5 | 10.4.24 | 0SA15CP01 | 415V SWGR O/G MODULE # 0SA15FC | SLAVE CLOCK | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | POWER SUPPLY (0.3A) | XLPE-CU UNARMOURED | LV22-L4, LV47-04, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, ZZ99- |  | EPD | EDN
119 | 0SA | D02L2.5 | 10.4.24 | 0SA15DP01 | 415V SWGR O/G MODULE # 0SA15FD | 24V DC CHARGER (UNIT) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (2A) | XLPE-CU UNARMOURED | LV22-L4, LV48-04, LV10-L4, ZZ99- |  | EPD | EDN
120 | 0SA | D02C1.5 | 10.5.01 | 0SA15PC01 | 415V SWGR MOTOR MODULE # 0SA15RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 139 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | EPD
121 | 0SA | D03L2.5 | 10.4.26 | 0SA15PP01 | 415V SWGR MOTOR MODULE # 0SA15RB | BULK AMMONIA CUM TRANSFER - CENTRIFUGAL PUMP MOTOR | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 153 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG02-02, TG01-02, ZZ99- |  | EPD | PEM
122 | 0SA | D02C1.5 | 10.5.01 | 0SA15QC01 | 415V SWGR MOTOR MODULE # 0SA15RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-R3, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-02, BA21-02, BA22-02, BA23-02, BR33-02, ZZ99- |  | EPD | EPD
123 | 0SA | D03Q010 | 10.4.11 | 0SA15QP01 | 415V SWGR MOTOR MODULE # 0SA15RC | WASH WATER TRANSFER PUMP FOR BOILER AREA (P2B) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 168 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV75-03, LV77-03, LR10-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA20-02, BA21-02, BA22-02, BA23-02, BR33-02, ZZ99- |  | EPD | PEM
124 | 0SA | D02L2.5 | 10.4.24 | 0SA15RP01 | 415V SWGR O/G MODULE # 0SA15RD | S.H. SUPPLY FOR NGR UT # 1B | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, ZZ99- |  | EPD | JHS
125 | 0SA | D02L2.5 | 10.4.24 | 0SA15SP01 | 415V SWGR O/G MODULE # 0SA15RE | S.H. SUPPLY FOR 220V DCDB # 1FA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 26 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV48-04, LV11-L4, ZZ99- |  | EPD | EPD
126 | 0SA | D02L2.5 | 10.4.24 | 0SA15TP01 | 415V SWGR O/G MODULE # 0SA15RF | S.H. SUPPLY FOR 415V UNIT EMER. MCC # 1DG | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 29 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV47-04, LV46-04, LV38-R3, ZZ99- |  | EPD | EPD
127 | 0SA | D02L2.5 | 10.4.24 | 0SA16CP01 | 415V SWGR O/G MODULE # 0SA16FC | BOP PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC69-03, CC45-02, ZZ99- |  | EPD | EDN
128 | 0SA | D02L2.5 | 10.4.24 | 0SA16DP01 | 415V SWGR O/G MODULE # 0SA16FD | BOP PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC40-02, ZZ99- |  | EPD | EDN
129 | 0SA | D02L2.5 | 10.4.24 | 0SA16EP01 | 415V SWGR O/G MODULE # 0SA16FE | BOP PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC69-03, CC70-03, CC50-03, ZZ99- |  | EPD | EDN
130 | 0SA | D02L2.5 | 10.4.24 | 0SA16GP01 | 415V SWGR O/G MODULE # 0SA16FG | HMI NETWORK PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC40-02, CC39-02, ZZ99- |  | EPD | EDN
131 | 0SA | D02L2.5 | 10.4.24 | 0SA16IP01 | 415V SWGR O/G MODULE # 0SA16FI | BTS-1 1CA - 0CA | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC69-03, CC70-03, CC50-03, ZZ99- |  | EPD | BPL
132 | 0SA | D02C1.5 | 10.5.01 | 0SA16PC01 | 415V SWGR MOTOR MODULE # 0SA16RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV13-R3, LV63-05, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | EPD
133 | 0SA | D03L2.5 | 10.4.26 | 0SA16PP01 | 415V SWGR MOTOR MODULE # 0SA16RB | MOTOR FOR DOSING PUMP (NAOH DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV13-R3, LV63-05, LV64-04, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP04-02, TR26-02, TR40-02, TD18-02, TD28-02, TR45-02, TD29-02, TD30-02, TD31-02, TD32-02, ZZ99- |  | EPD | PEM
134 | 0SA | D02C1.5 | 10.5.01 | 0SA16QC01 | 415V SWGR MOTOR MODULE # 0SA16RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV22-L4, LV52-02, LV12-R3, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG82-03, TG81-03, ZZ99- |  | EPD | EPD
135 | 0SA | D03L2.5 | 10.4.26 | 0SA16QP01 | 415V SWGR MOTOR MODULE # 0SA16RC | WASH WATER TRANSFER PUMP FOR TG HALL AREA (P1A) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | LV22-L4, LV52-02, LV12-L4, LV58-02, LV04-L4, LV64-05, TR48-05, MR16-05, MR17-05, TG82-03, TG81-03, ZZ99- |  | EPD | PEM
136 | 0SA | D02L2.5 | 10.4.24 | 0SA16RP01 | 415V SWGR O/G MODULE # 0SA16RD | HMI NETWORK PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC40-02, CC39-02, ZZ99- |  | EPD | EDN
137 | 0SA | D02L2.5 | 10.4.24 | 0SA16SP01 | 415V SWGR O/G MODULE # 0SA16RE | HMI NETWORK PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC40-02, CC39-02, ZZ99- |  | EPD | EDN
138 | 0SA | D02L2.5 | 10.4.24 | 0SA16TP01 | 415V SWGR O/G MODULE # 0SA16RF | ECP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC82-02, CC83-03, CC84-03, CC86-03, CC88-03, CC92-03, ZZ99- |  | EPD | EDN
139 | 0SA | D3HQ025 | 10.4.18 | 0SA16VP01 | 415V SWGR O/G MODULE # 0SA16RH | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
140 | 0SA | D3HQ050 | 10.4.19 | 0SA17BP01 | 415V SWGR O/G MODULE # 0SA17FB | AUX. POWER SUPLY FOR GT # 1 | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 136 | [5 empty] | POWER SUPPLY (100A) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV19-R2, LV68-01, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-02, TY04-02, TY05-02, TY06-02, ZZ99- |  | EPD | BPL
141 | 0SA | D02L2.5 | 10.4.24 | 0SA17CP01 | 415V SWGR O/G MODULE # 0SA17FC | HART MANAGEMENT SYSTEM | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (5A) | XLPE-CU UNARMOURED | LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC82-02, CC83-03, CC84-03, CC86-03, CC88-03, CC92-03, ZZ99- |  | EPD | EDN
142 | 0SA | D04Q010 | 10.4.22 | 0SA17EP01 | 415V SWGR O/G MODULE # 0SA17FE | LCP (AMMONIA DOSING) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV62-03, LV63-04, LV64-04, TR48-04, MR16-03, MR17-03, TG91-02, TG85-01, TG86-02, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, TG08-R1, TG06-01, TG05-01, TG04-01, TG02-01, TG01-01, ZZ99- |  | EPD | PEM
143 | 0SA | D03L2.5 | 10.4.26 | 0SA17FP01 | 415V SWGR O/G MODULE # 0SA17FF | SUPPLY FAN FOR MCC ROOM FOR COMPRESSOR HOUSE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 186 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM06-L3, CM07-L3, CM08-L3, CM09-L3, CM13-02, ZZ99- |  | EPD | PEM
144 | 0SA | D03L2.5 | 10.4.26 | 0SA17GP01 | 415V SWGR O/G MODULE # 0SA17FG | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 148 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-02, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP40-02, TP41-02, ZZ99- |  | EPD | PEM
145 | 0SA | D04Q010 | 10.4.22 | 0SA17IP01 | 415V SWGR O/G MODULE # 0SA17FI | BULK AMMONIA DOSING PANEL | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV62-03, LV63-04, LV64-04, TR48-04, MR16-03, MR17-03, TG91-02, TG85-01, TG86-02, TG15-R1, TG14-R1, TG13-R1, TG12-R1, TG11-R1, TG10-R1, TG09-R1, TG08-R1, TG06-01, TG05-01, TG04-01, TG02-01, TG01-01, ZZ99- |  | EPD | PEM
146 | 0SA | D03L2.5 | 10.4.26 | 0SA17TP01 | 415V SWGR O/G MODULE # 0SA17RF | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 85 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG71-02, TG72-02, TR16-02, TG73-02, TG74-02, TG75-02, TG76-02, ZZ99- |  | EPD | PEM
147 | 0SA | D3HQ025 | 10.4.18 | 0SA17VP01 | 415V SWGR O/G MODULE # 0SA17RH | AUX. POWER SUPPLY FOR UT # 1B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 117 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV62-03, LV63-03, LV03-L1, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-01, TY02-01, TY03-01, TY04-01, ZZ99- |  | EPD | JHS
148 | 0SA | D3HQ050 | 10.4.19 | 0SA18BP01 | 415V SWGR O/G MODULE # 0SA18FB | GCB # 1 | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 133 | [5 empty] | POWER SUPPLY (100A) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV19-R2, LV68-01, LV69-01, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, TR38-01, TP39-01, TP38-01, TP37-01, TP36-01, TR30-01, TP35-01, TP34-01, TP33-01, ZZ99- |  | EPD | PEM
149 | 0SA | D03L2.5 | 10.4.26 | 0SA18CP01 | 415V SWGR O/G MODULE # 0SA18FC | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV21-L4, LV22-L4, LV48-04, LV49-04, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TG43-02, TG48-02, ZZ99- |  | EPD | PEM
150 | 0SA | D02L2.5 | 10.4.24 | 0SA18DP01 | 415V SWGR O/G MODULE # 0SA18FD | S.H. SUPLY FOR NSPBD FOR 0DAT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, MR16-05, MV99-04, MV98-04, MV97-04, MV96-04, MV95-04, MV38-02, MV39-02, ZZ99- |  | EPD | JHS
151 | 0SA | D02L2.5 | 10.4.24 | 0SA18EP01 | 415V SWGR O/G MODULE # 0SA18FE | S.H. SUPLY FOR NSPBD FOR 1DAT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV21-L4, LV51-02, LV50-02, LV36-L4, LV72-04, LR11-L3, MR05-L3, MV76-03, MV77-03, MV49-02, MV70-03, ZZ99- |  | EPD | JHS
152 | 0SA | D03L2.5 | 10.4.26 | 0SA18FP01 | 415V SWGR O/G MODULE # 0SA18FF | EXHAUST FAN FOR AREA BETWEEN A-B-1-5 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV21-L4, LV22-L4, LV48-04, LV49-04, LV07-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TG43-02, TG48-02, ZZ99- |  | EPD | PEM
153 | 0SA | D02C1.5 | 10.5.01 | 0SA18GC01 | 415V SWGR MOTOR MODULE # 0SA18FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 121 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, MR16-05, MR17-05, TG91-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | EPD
154 | 0SA | D03L2.5 | 10.4.26 | 0SA18GP01 | 415V SWGR MOTOR MODULE # 0SA18FG | TANK AGITATOR MOTOR (AGM 2) (HYDRAZINE DOSING) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 138 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, TG65-02, TR17-02, TG64-02, TR18-02, TG66-02, MR15-02, TR02-02, TG85-02, TG86-03, TG15-L3, TG14-L3, TG13-L3, TG12-L3, TG11-L3, TG10-L3, TG09-L3, TG08-L3, TG06-02, TG05-02, TG04-02, TG03-02, ZZ99- |  | EPD | PEM
155 | 0SA | D04Q010 | 10.4.22 | 0SA18HP01 | 415V SWGR O/G MODULE # 0SA18FH | 2T A/C FOR TG HALL ELEVATOR M/C ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY (7kW) | XLPE-AL UNARMOURED | LV21-R2, LV20-R2, LV62-03, LV63-04, LV64-04, TR48-04, TG65-01, TR17-01, TG64-01, TG63-01, ZZ99- |  | EPD | PEM
156 | 0SA | D02L2.5 | 10.4.24 | 0SA18PP01 | 415V SWGR O/G MODULE # 0SA18RB | AUX. POWER SUPLY FOR SST # 0DAT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 68 | 92 | 16.01.20 | DR1095_0012 |  |  | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR48-05, MR16-05, MV99-04, MV98-04, MV97-04, MV96-04, MV95-04, MV38-02, MV39-02, ZZ99- |  | EPD | JHS
157 | 0SA | D02L2.5 | 10.4.24 | 0SA18RP01 | 415V SWGR O/G MODULE # 0SA18RD | AUX. POWER SUPLY FOR UST # 1DAT02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 60 | 92 | 16.01.20 | DR1095_0006 |  |  | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV21-L4, LV51-02, LV50-02, LV36-L4, LV72-04, LR11-L3, MR05-L3, MV76-03, MV77-03, MV49-02, MV70-03, ZZ99- |  | EPD | JHS
158 | 0SA | D02L2.5 | 10.4.24 | 0SA18SP01 | 415V SWGR O/G MODULE # 0SA18RE | DATA CONCENTRATOR (HT & LT) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | 71 | 13.2.20 | DR1095_0006 |  |  | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC82-02, CC83-03, CC84-03, CC86-03, CC88-03, CC92-03, ZZ99- |  | EPD | EPD
159 | 0SA | D02L2.5 | 10.4.24 | 0SA18TP01 | 415V SWGR O/G MODULE # 0SA18RF | STRP | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC81-03, CC31-02, CC67-03, CC68-03, CC69-03, CC70-03, CC50-03, ZZ99- |  | EPD | TBG
160 | 0SA | D04Q010 | 10.4.22 | 0SA18UP01 | 415V SWGR O/G MODULE # 0SA18RG | SUMP PUMP (MRS) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 258 | [5 empty] | POWER SUPPLY (2.5kW) | XLPE-AL UNARMOURED | LV21-R2, LV22-R1, LV23-R2, LV43-02, LV44-03, LV76-01, LV79-02, LR10-R2, IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IC07-R1, IR08-02, IC08-02, IC09-02, IC10-02, IC11-02, IC12-02, IC13-02, IR09-02, IC24-02, IC25-02, IC26-02, IR11-02, IC27-02, IC28-02, IR12-02, IC29-02, IR13-02, IC30-02, IC31-01, ZZ99- |  | EPD | PEM
161 | 0SA | D3HQ025 | 10.4.18 | 0SA18VP01 | 415V SWGR O/G MODULE # 0SA18RH | AUX. POWER SUPPLY FOR UT # 1A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 136 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV62-03, LV63-03, LV03-L1, LV02-L1, LV01-01, LR01-02, TY13-R1, TY12-R1, TY11-R1, YR01-01, TY01-02, TY02-02, TY03-01, TY04-01, TY05-02, ZZ99- |  | EPD | JHS
162 | 0SA | D02C1.5 | 10.5.01 | 0SA19CC01 | 415V SWGR MOTOR MODULE # 0SA19FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV67-02, LV66-02, LV70-03, LR04-03, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY33-02, ZZ99- |  | EPD | EPD
163 | 0SA | D03Q010 | 10.4.11 | 0SA19CP01 | 415V SWGR MOTOR MODULE # 0SA19FC | TRANSFORMER YARD AREA WASTE WATER TRANSFER PUMP (P5B) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 157 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV19-R2, LV67-01, LV66-01, LV70-01, LR04-01, TY17-L2, TY18-R2, YR02-02, TY25-02, TY26-02, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY33-02, ZZ99- |  | EPD | PEM
164 | 0SA | D02L2.5 | 10.4.24 | 0SA19DP01 | 415V SWGR O/G MODULE # 0SA19FD | TG PANEL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (10A) | XLPE-CU UNARMOURED | LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC23-03, CC22-03, CC14-02, CC15-02, ZZ99- |  | EPD | EDN
165 | 0SA | D02L2.5 | 10.4.24 | 0SA19EP01 | 415V SWGR O/G MODULE # 0SA19FE | UNIT AIR RECEIVER-2 ADT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 180 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM11-02, CM18-02, CM19-02, CM20-02, ZZ99- |  | EPD | PEM
166 | 0SA | D04Q010 | 10.4.22 | 0SA19FP01 | 415V SWGR O/G MODULE # 0SA19FF | SERVICE AIR COMPRESSOR AUX. SUPPLY | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 188 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV19-R2, LV18-R2, LV71-03, LR02-02, TY14-R1, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, CM07-R1, CM08-R1, CM09-R1, CM13-02, CM22-02, CM24-02, ZZ99- |  | EPD | PEM
167 | 0SA | D04Q010 | 10.4.22 | 0SA19GP01 | 415V SWGR O/G MODULE # 0SA19FG | BC BAY (BFP) DG EOT CRANE | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (12kW) | XLPE-AL UNARMOURED | LV21-R2, LV20-R2, LV62-03, LV63-04, LV64-04, TR48-04, TG65-01, TR17-01, TG64-01, TG63-01, TG61-01, TG60-01, TG59-01, TG58-01, TR20-01, ZZ99- |  | EPD | PEM
168 | 0SA | D3HQ025 | 10.4.18 | 0SA19IP01 | 415V SWGR O/G MODULE # 0SA19FI | AUX. POWER SUPPLY FOR ST # 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 115 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV19-R2, LV67-01, LV66-01, LV70-01, LR04-01, TY17-L2, TY18-R2, YR02-02, TY25-02, TY26-02, TY28-02, ZZ99- |  | EPD | JHS
169 | 0SA | D02L2.5 | 10.4.24 | 0SA19PP01 | 415V SWGR O/G MODULE # 0SA19RB | SERVICE AIR RECEIVER-2 ADT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM10-02, CM14-02, CM15-02, CM16-02, CM17-02, ZZ99- |  | EPD | PEM
170 | 0SA | D02C1.5 | 10.5.01 | 0SA19QC01 | 415V SWGR MOTOR MODULE # 0SA19RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 52 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR25-05, TP55-02, TP59-02, ZZ99- |  | EPD | EPD
171 | 0SA | D03L2.5 | 10.4.26 | 0SA19QP01 | 415V SWGR MOTOR MODULE # 0SA19RC | LUBE OIL PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV62-05, LV63-05, LV64-05, TR25-05, TP55-02, TP59-02, ZZ99- |  | EPD | PEM
172 | 0SA | D02L2.5 | 10.4.24 | 0SA19RP01 | 415V SWGR O/G MODULE # 0SA19RD | INSTRUMENT AIR RECEIVER-2 ADT | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (0.01kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM10-02, CM14-02, CM15-02, CM16-02, ZZ99- |  | EPD | PEM
173 | 0SA | D02L2.5 | 10.4.24 | 0SA19SP01 | 415V SWGR O/G MODULE # 0SA19RE | AIR DRYER-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 180 | [5 empty] | POWER SUPPLY (0.5kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM11-02, CM18-02, CM19-02, CM20-02, ZZ99- |  | EPD | PEM
174 | 0SA | D02L2.5 | 10.4.24 | 0SA19TP01 | 415V SWGR O/G MODULE # 0SA19RF | SPVT CUBICLE | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 134 | [5 empty] | POWER SUPPLY (1.32kW) | XLPE-CU UNARMOURED | LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-02, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP35-02, TP34-02, TP32-02, ZZ99- |  | EPD | RUD
175 | 0SA | D04Q010 | 10.4.22 | 0SA19UP01 | 415V SWGR O/G MODULE # 0SA19RG | INSTRUMENT AIR COMPRESSOR AUX. SUPPLY | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 192 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV19-R2, LV18-R2, LV71-03, LR02-02, TY14-R1, TY13-R1, TY12-R1, TY11-R1, TY36-02, TY37-02, TY38-02, TY39-02, YR03-02, TY40-02, TY41-02, TY42-02, TY43-02, NR01-02, CM04-L2, CM05-L2, CM06-R1, CM07-R1, CM08-R1, CM09-R1, CM13-02, CM22-02, CM24-02, CM26-02, ZZ99- |  | EPD | PEM
176 | 0SA | D04Q010 | 10.4.22 | 0SA19VP01 | 415V SWGR O/G MODULE # 0SA19RH | SPACE HEATER FOR SPBD | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | LV21-R1, LV20-R2, LV19-R2, LV18-R2, LV71-03, MR02-02, ZZ99- |  | EPD | RUD
1 | 0SB | D02C1.5 | 10.5.01 | 0SB01BC01 | 415V SWGR MOTOR MODULE # 0SB01FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, ZZ99- |  | EPD | EPD
2 | 0SB | D03L2.5 | 10.4.26 | 0SB01BP01 | 415V SWGR MOTOR MODULE # 0SB01FB | SCALE/CORRISION INHIBITOR AGITATOR PDN50AE002 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, ZZ99- |  | EPD | PEM
3 | 0SB | D3HQ025 | 10.4.18 | 0SB01CP01 | 415V SWGR O/G MODULE # 0SB01FC | SCREEN & GATE HANDLING-A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | CW06-01, CW05-01, CW04-01, CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, CW12-02, CW14-02, ZZ99- |  | EPD | PEM
4 | 0SB | D02C1.5 | 10.5.01 | 0SB01DC01 | 415V SWGR MOTOR MODULE # 0SB01FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
5 | 0SB | D03Q025 | 10.4.12 | 0SB01DP01 | 415V SWGR MOTOR MODULE # 0SB01FD | DILUTION WATER PUMP FOR CW-P3D | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI07-01, CI08-01, CI09-01, ZZ99- |  | EPD | PEM
6 | 0SB | D04Q010 | 10.4.22 | 0SB01EP01 | 415V SWGR O/G MODULE # 0SB01FE | MO BFV-CW PUMP DISCHARGE-A (4kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (4kW) | XLPE-AL UNARMOURED | CW06-02, CW05-01, CW04-01, CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, WR04-02, ZZ99- |  | EPD | PEM
7 | 0SB | D02L2.5 | 10.4.24 | 0SB01FP01 | 415V SWGR O/G MODULE # 0SB01FF | PROPELLOR FAN-A (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
8 | 0SB | D3HQ025 | 10.4.18 | 0SB01GP01 | 415V SWGR O/G MODULE # 0SB01FG | AC FOR CONTROL ROOM-H (15 kW) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (15 kW) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
9 | 0SB | D04Q010 | 10.4.22 | 0SB01HP01 | 415V SWGR O/G MODULE # 0SB01FH | MO BFV-CW PUMP DISCHARGE-C (4kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 87 | [5 empty] | POWER SUPPLY (4kW) | XLPE-AL UNARMOURED | CW06-02, CW05-02, CW04-01, CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, CW12-02, CW14-02, WR06-02, ZZ99- |  | EPD | PEM
10 | 0SB | D02C1.5 | 10.5.01 | 0SB01QC01 | 415V SWGR MOTOR MODULE # 0SB01RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 91 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW08-02, TW09-02, TW10-02, ZZ99- |  | EPD | EPD
11 | 0SB | D03L2.5 | 10.4.26 | 0SB01QP01 | 415V SWGR MOTOR MODULE # 0SB01RC | NEUTRALIZATION PIT (LIME PIT) DEWATERING PUMP PDN60AP002 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 91 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW08-02, TW09-02, TW10-02, ZZ99- |  | EPD | PEM
12 | 0SB | D02C1.5 | 10.5.01 | 0SB01RC01 | 415V SWGR MOTOR MODULE # 0SB01RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 96 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, TW12-02, TW16-02, TW17-02, TW18-02, TW21-02, ZZ99- |  | EPD | EPD
13 | 0SB | D03L2.5 | 10.4.26 | 0SB01RP01 | 415V SWGR MOTOR MODULE # 0SB01RD | SULPHURIC ACID UNLOADING PUMP PDN03AP002 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 96 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, TW12-02, TW16-02, TW17-02, TW18-02, TW21-02, ZZ99- |  | EPD | PEM
14 | 0SB | D04Q010 | 10.4.22 | 0SB01SP01 | 415V SWGR O/G MODULE # 0SB01RE | MO BFV-CW MUP LINE (0.37kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-AL UNARMOURED | CW06-02, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, KR01-01, TW22-01, TW23-01, ZZ99- |  | EPD | PEM
15 | 0SB | D04Q010 | 10.4.22 | 0SB01UP01 | 415V SWGR O/G MODULE # 0SB01RG | SCALE/ CORROSION INHIBITOR PUMP PDN50AP002 (0.37kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 69 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-AL UNARMOURED | CW06-02, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, KR01-01, TW22-01, TW23-01, ZZ99- |  | EPD | PEM
16 | 0SB | D02C1.5 | 10.5.01 | 0SB01VC01 | 415V SWGR MOTOR MODULE # 0SB01RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
17 | 0SB | D03Q025 | 10.4.12 | 0SB01VP01 | 415V SWGR MOTOR MODULE # 0SB01RH | NEUTRALIZATION PUMP-P4B (11 kW) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI07-01, CI08-01, CI09-01, ZZ99- |  | EPD | PEM
18 | 0SB | D02C1.5 | 10.5.01 | 0SB01WC01 | 415V SWGR MOTOR MODULE # 0SB01RI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | EPD
19 | 0SB | D03L2.5 | 10.4.26 | 0SB01WP01 | 415V SWGR MOTOR MODULE # 0SB01RI | HCl DOSING PUMP FOR CW-CLO2-DP1B (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | PEM
20 | 0SB | D04Q010 | 10.4.22 | 0SB02BP01 | 415V SWGR O/G MODULE # 0SB02FB | SULPHURIC ACID DOSING PUMP PDN30AP002 (0.37 kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 71 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-AL UNARMOURED | CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, KR01-01, TW22-01, TW23-01, TW24-01, TW25-01, TW26-01, KR04-01, ZZ99- |  | EPD | PEM
21 | 0SB | D02L2.5 | 10.4.24 | 0SB02EP01 | 415V SWGR O/G MODULE # 0SB02FE | PROPELLOR FAN-D (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
22 | 0SB | D02Q010 | 10.4.06 | 0SB02GP01 | 415V SWGR O/G MODULE # 0SB02FG | SPLIT AC FOR CONTROL ROOM-A (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 101 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI03-01, CI04-01, ZZ99- |  | EPD | PEM
23 | 0SB | D02Q010 | 10.4.06 | 0SB02HP01 | 415V SWGR O/G MODULE # 0SB02FH | SPLIT AC FOR CONTROL ROOM-C (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI03-01, ZZ99- |  | EPD | PEM
24 | 0SB | D02C1.5 | 10.5.01 | 0SB02QC01 | 415V SWGR MOTOR MODULE # 0SB02RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
25 | 0SB | D03L2.5 | 10.4.26 | 0SB02QP01 | 415V SWGR MOTOR MODULE # 0SB02RC | NaClO2 DOSING PUMP FOR CWT-CLO2-DP2B (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
26 | 0SB | D03L2.5 | 10.4.26 | 0SB02SP01 | 415V SWGR O/G MODULE # 0SB02RE | AXIAL EXHAUST AIR FAN-A1 (1.5 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (1.5 kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, TW12-02, TW16-02, TW17-02, TW18-02, TW21-02, ZZ99- |  | EPD | PEM
27 | 0SB | D03L2.5 | 10.4.26 | 0SB02TP01 | 415V SWGR O/G MODULE # 0SB02RF | AXIAL EXHAUST AIR FAN-A2 (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 102 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, TW12-02, TW16-02, TW17-02, TW18-02, TW19-02, TW20-02, ZZ99- |  | EPD | PEM
28 | 0SB | D03L2.5 | 10.4.26 | 0SB02UP01 | 415V SWGR O/G MODULE # 0SB02RG | AXIAL EXHAUST AIR FAN-C2 (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 91 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, ZZ99- |  | EPD | PEM
29 | 0SB | D3HQ025 | 10.4.18 | 0SB02XP01 | 415V SWGR O/G MODULE # 0SB02RJ | CWPH DG EOT CRANE (17 kW) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (17 kW) | XLPE-AL UNARMOURED | CW06-01, CW05-01, CW04-01, CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, CW12-02, CW14-02, ZZ99- |  | EPD | PEM
30 | 0SB | D02Q010 | 10.4.06 | 0SB03FP01 | 415V SWGR O/G MODULE # 0SB03FE | SPLIT AC FOR CONTROL ROOM-E (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI03-01, CI04-01, ZZ99- |  | EPD | PEM
31 | 0SB | D3HQ025 | 10.4.18 | 0SB03QP01 | 415V SWGR O/G MODULE # 0SB03RC | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 19 | [5 empty] | POWER SUPPLY (32 A) | XLPE-AL UNARMOURED | CW06-01, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | EDN
32 | 0SB | D03L2.5 | 10.4.26 | 0SB03UP01 | 415V SWGR O/G MODULE # 0SB03RG | AXIAL EXHAUST FAN-B1 (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-L3, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, ZZ99- |  | EPD | PEM
33 | 0SB | D03L2.5 | 10.4.26 | 0SB03VP01 | 415V SWGR O/G MODULE # 0SB03RH | AXIAL EXHAUST FAN-B2 (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 98 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI03-02, CI04-02, ZZ99- |  | EPD | PEM
34 | 0SB | D02C1.5 | 10.5.01 | 0SB03WC01 | 415V SWGR MOTOR MODULE # 0SB03RI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | EPD
35 | 0SB | D03L2.5 | 10.4.26 | 0SB03WP01 | 415V SWGR MOTOR MODULE # 0SB03RI | HCl DOSING PUMP FOR PT-CLO2-DP1D (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | PEM
36 | 0SB | D3HQ025 | 10.4.18 | 0SB03XP01 | 415V SWGR O/G MODULE # 0SB03RJ | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
37 | 0SB | D03L2.5 | 10.4.26 | 0SB04BP01 | 415V SWGR O/G MODULE # 0SB04FB | AXIAL SUPPLY FAN FOR MCC ROOM-A (2.2 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 23 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, ZZ99- |  | EPD | PEM
38 | 0SB | D02Q010 | 10.4.06 | 0SB04CP01 | 415V SWGR O/G MODULE # 0SB04FC | AC FOR CONTROL ROOM-B (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW05-01, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | PEM
39 | 0SB | D3HQ025 | 10.4.18 | 0SB04DP01 | 415V SWGR O/G MODULE # 0SB04FD | PORTABLE SUMP PUMP A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 77 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CW05-01, CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, ZZ99- |  | EPD | PEM
40 | 0SB | D02C1.5 | 10.5.01 | 0SB04PC01 | 415V SWGR MOTOR MODULE # 0SB04RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
41 | 0SB | D03L2.5 | 10.4.26 | 0SB04PP01 | 415V SWGR MOTOR MODULE # 0SB04RB | NaClO2 DOSING PUMP FOR PT-CLO2-DP2D (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
42 | 0SB | D02C1.5 | 10.5.01 | 0SB04QC01 | 415V SWGR MOTOR MODULE # 0SB04RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
43 | 0SB | D03L2.5 | 10.4.26 | 0SB04QP01 | 415V SWGR MOTOR MODULE # 0SB04RC | ACID UNLOADING PUMP-P1B (3.7 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
44 | 0SB | D03L2.5 | 10.4.26 | 0SB04RP01 | 415V SWGR O/G MODULE # 0SB04RD | AXIAL SUPPLY FAN FOR MCC ROOM-C (2.2 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 26 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | CW05-04, CW04-04, CW03-04, CW02-04, CW01-04, ZZ99- |  | EPD | PEM
45 | 0SB | D02Q010 | 10.4.06 | 0SB04SP01 | 415V SWGR O/G MODULE # 0SB04RE | AC FOR CONTROL ROOM-D (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW05-01, CW16-01, CW17-01, ZZ99- |  | EPD | PEM
46 | 0SB | D03L2.5 | 10.4.26 | 0SB04TP01 | 415V SWGR O/G MODULE # 0SB04RF | AXIAL EXHAUST FAN FOR BATTERY ROOM-B (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 41 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | CW05-04, CW16-02, CW17-02, CW18-02, CW19-02, WR03-02, CW20-02, ZZ99- |  | EPD | PEM
47 | 0SB | D04Q010 | 10.4.22 | 0SB04UP01 | 415V SWGR O/G MODULE # 0SB04RG | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 85 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW05-02, CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, ZZ99- |  | EPD | PEM
48 | 0SB | D02C1.5 | 10.5.01 | 0SB05BC01 | 415V SWGR MOTOR MODULE # 0SB05FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI10-03, ZZ99- |  | EPD | EPD
49 | 0SB | D03L2.5 | 10.4.26 | 0SB05BP01 | 415V SWGR MOTOR MODULE # 0SB05FB | NaClO2 UNLOADING PUMP-P2B (3.7 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI10-03, ZZ99- |  | EPD | PEM
50 | 0SB | D02C1.5 | 10.5.01 | 0SB05CC01 | 415V SWGR MOTOR MODULE # 0SB05FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
51 | 0SB | D03L2.5 | 10.4.26 | 0SB05CP01 | 415V SWGR MOTOR MODULE # 0SB05FC | DILUTION WATER PUMP FOR PT- P3B (3.7 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
52 | 0SB | D02Q010 | 10.4.06 | 0SB05DP01 | 415V SWGR O/G MODULE # 0SB05FD | AC FOR CONTROL ROOM-F (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW05-01, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | PEM
53 | 0SB | D04Q010 | 10.4.22 | 0SB05FP01 | 415V SWGR O/G MODULE # 0SB05FF | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 81 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW05-02, CW04-01, CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, CW12-02, CW14-02, ZZ99- |  | EPD | PEM
54 | 0SB | D02C1.5 | 10.5.01 | 0SB05HC01 | 415V SWGR MOTOR MODULE # 0SB05FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, TW24-02, ZZ99- |  | EPD | EPD
55 | 0SB | D03L2.5 | 10.4.26 | 0SB05HP01 | 415V SWGR MOTOR MODULE # 0SB05FH | ACID DILUTION PUMP PDN60AP002 (2.2 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, TW24-02, ZZ99- |  | EPD | PEM
56 | 0SB | D02C1.5 | 10.5.01 | 0SB05PC01 | 415V SWGR MOTOR MODULE # 0SB05RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW27-02, TW28-02, ZZ99- |  | EPD | EPD
57 | 0SB | D03L2.5 | 10.4.26 | 0SB05PP01 | 415V SWGR MOTOR MODULE # 0SB05RB | SMBS DOSING TANK-DT1B (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW27-02, TW28-02, ZZ99- |  | EPD | PEM
58 | 0SB | D04Q010 | 10.4.22 | 0SB05UP01 | 415V SWGR O/G MODULE # 0SB05RG | CWPH AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 23 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW05-02, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | PEM
59 | 0SB | D04Q010 | 10.4.22 | 0SB05VP01 | 415V SWGR O/G MODULE # 0SB05RH | CWPH AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 23 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW05-02, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | PEM
60 | 0SB | D3HQ025 | 10.4.18 | 0SB05WP01 | 415V SWGR O/G MODULE # 0SB05RI | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 18 | [5 empty] | POWER SUPPLY (32 A) | XLPE-AL UNARMOURED | CW05-01, CW16-01, CW21-01, CW22-01, ZZ99- |  | EPD | EDN
61 | 0SB | D04Q010 | 10.4.22 | 0SB07BP01 | 415V SWGR O/G MODULE # 0SB07FB | MO BFV-CW PUMP DISCHARGE-B (4kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (4kW) | XLPE-AL UNARMOURED | CW04-01, CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, CW12-02, WR05-02, ZZ99- |  | EPD | PEM
62 | 0SB | D02L2.5 | 10.4.24 | 0SB07CP01 | 415V SWGR O/G MODULE # 0SB07FC | PROPELLOR FAN-B (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI03-02, CI04-02, ZZ99- |  | EPD | PEM
63 | 0SB | D04Q010 | 10.4.22 | 0SB07PP01 | 415V SWGR O/G MODULE # 0SB07RB | CWPH AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | PEM
64 | 0SB | D02L2.5 | 10.4.24 | 0SB07SP01 | 415V SWGR O/G MODULE # 0SB07RE | PROPELLOR FAN-C (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI03-02, CI04-02, ZZ99- |  | EPD | PEM
65 | 0SB | D04Q010 | 10.4.22 | 0SB07TP01 | 415V SWGR O/G MODULE # 0SB07RF | MO BFV-RECIRCULATION LINE (0.55kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 77 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, KR01-01, TW22-01, TW23-01, TW24-01, ZZ99- |  | EPD | PEM
66 | 0SB | D04Q010 | 10.4.22 | 0SB07UP01 | 415V SWGR O/G MODULE # 0SB07RG | SCALE/ CORROSION INHIBITOR PUMP PDN50AP001 (0.37kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 77 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, KR01-01, TW22-01, TW23-01, TW24-01, ZZ99- |  | EPD | PEM
67 | 0SB | D02C1.5 | 10.5.01 | 0SB07VC01 | 415V SWGR MOTOR MODULE # 0SB07RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW08-02, TW09-02, TW10-02, ZZ99- |  | EPD | EPD
68 | 0SB | D03L2.5 | 10.4.26 | 0SB07VP01 | 415V SWGR MOTOR MODULE # 0SB07RH | NEUTRALIZATION PIT (LIME PIT) DEWATERING PUMP PDN60AP001 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW08-02, TW09-02, TW10-02, ZZ99- |  | EPD | PEM
69 | 0SB | D02Q010 | 10.4.06 | 0SB08CP01 | 415V SWGR O/G MODULE # 0SB08FC | SPLIT AC FOR CONTROL ROOM-B (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI03-01, ZZ99- |  | EPD | PEM
70 | 0SB | D04Q010 | 10.4.22 | 0SB08DP01 | 415V SWGR O/G MODULE # 0SB08FD | SULPHURIC ACID DOSING PUMP PDN30AP001 (0.37 kW) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 78 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, KR01-01, TW22-01, TW23-01, TW24-01, TW25-01, TW26-01, KR04-01, ZZ99- |  | EPD | PEM
71 | 0SB | D02C1.5 | 10.5.01 | 0SB08FC01 | 415V SWGR MOTOR MODULE # 0SB08FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 114 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
72 | 0SB | D03L2.5 | 10.4.26 | 0SB08FP01 | 415V SWGR MOTOR MODULE # 0SB08FF | DILUTION WATER PUMP FOR PT- P3A (3.7 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
73 | 0SB | D04Q010 | 10.4.22 | 0SB08PP01 | 415V SWGR O/G MODULE # 0SB08RB | CWPH AREA DDCMIS CHARGER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 27 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | PEM
74 | 0SB | D02C1.5 | 10.5.01 | 0SB08QC01 | 415V SWGR MOTOR MODULE # 0SB08RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI10-03, ZZ99- |  | EPD | EPD
75 | 0SB | D03L2.5 | 10.4.26 | 0SB08QP01 | 415V SWGR MOTOR MODULE # 0SB08RC | NaClO2 UNLOADING PUMP-P2A (3.7 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI10-03, ZZ99- |  | EPD | PEM
76 | 0SB | D02Q010 | 10.4.06 | 0SB08SP01 | 415V SWGR O/G MODULE # 0SB08RE | SPLIT AC FOR CONTROL ROOM-D (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 108 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW06-02, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI03-01, CI04-01, ZZ99- |  | EPD | PEM
77 | 0SB | D04Q010 | 10.4.22 | 0SB08TP01 | 415V SWGR O/G MODULE # 0SB08RF | VFD PANEL | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 101 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, KR01-01, TW22-01, TW27-01, TW28-01, TW29-01, TW30-01, ZZ99- |  | EPD | PEM
78 | 0SB | D03L2.5 | 10.4.26 | 0SB08UP01 | 415V SWGR O/G MODULE # 0SB08RG | AXIAL EXHAUST AIR FAN-B1 (1.5 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | POWER SUPPLY (1.5 kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, TW12-02, TW14-02, TW15-02, ZZ99- |  | EPD | PEM
79 | 0SB | D3HQ025 | 10.4.18 | 0SB08WP01 | 415V SWGR O/G MODULE # 0SB08RI | PORTABLE SUMP PUMP B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | CW04-01, CW05-01, CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, ZZ99- |  | EPD | PEM
80 | 0SB | D02Q010 | 10.4.06 | 0SB09CP01 | 415V SWGR O/G MODULE # 0SB09FC | AC FOR CONTROL ROOM-A (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW16-01, CW17-01, CW18-01, ZZ99- |  | EPD | PEM
81 | 0SB | D02Q010 | 10.4.06 | 0SB09DP01 | 415V SWGR O/G MODULE # 0SB09FD | AC FOR CONTROL ROOM-C (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW16-01, CW21-01, ZZ99- |  | EPD | PEM
82 | 0SB | D02C1.5 | 10.5.01 | 0SB09QC01 | 415V SWGR MOTOR MODULE # 0SB09RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 114 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
83 | 0SB | D03L2.5 | 10.4.26 | 0SB09QP01 | 415V SWGR MOTOR MODULE # 0SB09RC | ACID UNLOADING PUMP-P1A (3.7 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
84 | 0SB | D02Q010 | 10.4.06 | 0SB09RP01 | 415V SWGR O/G MODULE # 0SB09RD | AC FOR CONTROL ROOM-E (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW04-01, CW05-02, CW16-01, CW17-01, CW18-01, ZZ99- |  | EPD | PEM
85 | 0SB | D03L2.5 | 10.4.26 | 0SB09SP01 | 415V SWGR O/G MODULE # 0SB09RE | AXIAL EXHAUST AIR FAN-B2 (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI03-02, CI04-02, ZZ99- |  | EPD | PEM
86 | 0SB | D02Q010 | 10.4.06 | 0SB10CP01 | 415V SWGR O/G MODULE # 0SB10FC | AREA PANEL-4 (3 kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 74 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, CW12-02, CW14-02, ZZ99- |  | EPD | PEM
87 | 0SB | D03L2.5 | 10.4.26 | 0SB10DP01 | 415V SWGR O/G MODULE # 0SB10FD | AXIAL EXHAUST FAN-A1 (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI03-02, CI04-02, ZZ99- |  | EPD | PEM
88 | 0SB | D02C1.5 | 10.5.01 | 0SB10FC01 | 415V SWGR MOTOR MODULE # 0SB10FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
89 | 0SB | D03L2.5 | 10.4.26 | 0SB10FP01 | 415V SWGR MOTOR MODULE # 0SB10FF | NaClO2 DOSING PUMP FOR CWT-CLO2-DP2A (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
90 | 0SB | D3HQ025 | 10.4.18 | 0SB10GP01 | 415V SWGR O/G MODULE # 0SB10FG | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
91 | 0SB | D3HQ025 | 10.4.18 | 0SB10PP01 | 415V SWGR O/G MODULE # 0SB10RB | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY (32 A) | XLPE-AL UNARMOURED | CW03-01, CW04-01, CW05-01, CW16-01, CW21-01, CW22-01, CW23-01, ZZ99- |  | EPD | EDN
92 | 0SB | D03L2.5 | 10.4.26 | 0SB10RP01 | 415V SWGR O/G MODULE # 0SB10RD | AXIAL EXHAUST FAN-A2 (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI03-02, CI04-02, ZZ99- |  | EPD | PEM
93 | 0SB | D02L2.5 | 10.4.24 | 0SB10SP01 | 415V SWGR O/G MODULE # 0SB10RE | REPEATER PANEL-3 (1 kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
94 | 0SB | D03L2.5 | 10.4.26 | 0SB10TP01 | 415V SWGR O/G MODULE # 0SB10RF | AXIAL EXHAUST FAN-C2 (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI03-02, CI04-02, ZZ99- |  | EPD | PEM
95 | 0SB | D03L2.5 | 10.4.26 | 0SB10UP01 | 415V SWGR O/G MODULE # 0SB10RG | AXIAL SUPPLY FAN FOR MCC ROOM-B (2.2 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | CW03-04, CW02-04, CW01-04, ZZ99- |  | EPD | PEM
96 | 0SB | D02C1.5 | 10.5.01 | 0SB10VC01 | 415V SWGR MOTOR MODULE # 0SB10RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
97 | 0SB | D03L2.5 | 10.4.26 | 0SB10VP01 | 415V SWGR MOTOR MODULE # 0SB10RH | NaClO2 DOSING PUMP FOR PT-CLO2-DP2C (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | PEM
98 | 0SB | D3HQ025 | 10.4.18 | 0SB10WP01 | 415V SWGR O/G MODULE # 0SB10RI | UPS SYSTEM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (32 A) | XLPE-AL UNARMOURED | CW10-02, CW09-02, WR07-02, IP06-02, IP05-02, IP04-01, WR01-01, CW01-01, CW02-01, CW03-01, CW04-01, CW05-01, CW16-01, CW21-01, CW22-01, ZZ99- |  | EPD | EDN
99 | 0SB | D02C1.5 | 10.5.01 | 0SB11CC01 | 415V SWGR MOTOR MODULE # 0SB11FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 84 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW27-02, TW28-02, TW29-02, ZZ99- |  | EPD | EPD
100 | 0SB | D03L2.5 | 10.4.26 | 0SB11CP01 | 415V SWGR MOTOR MODULE # 0SB11FC | SMBS DOSING TANK-DT1A (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 84 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW27-02, TW28-02, TW29-02, ZZ99- |  | EPD | PEM
101 | 0SB | D03L2.5 | 10.4.26 | 0SB11FP01 | 415V SWGR O/G MODULE # 0SB11FF | AXIAL EXHAUST FAN FOR BATTERY ROOM-A (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW16-02, CW17-02, CW18-02, CW19-02, WR03-02, CW20-02, ZZ99- |  | EPD | PEM
102 | 0SB | D02C1.5 | 10.5.01 | 0SB11GC01 | 415V SWGR MOTOR MODULE # 0SB11FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 117 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
103 | 0SB | D03Q025 | 10.4.12 | 0SB11GP01 | 415V SWGR MOTOR MODULE # 0SB11FG | NEUTRALIZATION PUMP-P4A (11 kW) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 115 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | CW03-01, CW04-01, CW05-01, CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI07-01, CI08-01, CI09-01, ZZ99- |  | EPD | PEM
104 | 0SB | D02C1.5 | 10.5.01 | 0SB11PC01 | 415V SWGR MOTOR MODULE # 0SB11RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 123 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | EPD
105 | 0SB | D03L2.5 | 10.4.26 | 0SB11PP01 | 415V SWGR MOTOR MODULE # 0SB11RB | HCl DOSING PUMP FOR CW-CLO2-DP1A (1.1 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 123 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | PEM
106 | 0SB | D04Q010 | 10.4.22 | 0SB11RP01 | 415V SWGR O/G MODULE # 0SB11RD | LOCAL CONTROL PANEL | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW03-01, CW04-02, CW05-02, CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI07-01, CI08-01, CI09-01, CI11-01, CI12-01, CI13-01, CI14-01, ZZ99- |  | EPD | EDN
107 | 0SB | D04Q010 | 10.4.22 | 0SB11TP01 | 415V SWGR O/G MODULE # 0SB11RF | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 117 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | CW03-01, CW04-02, CW05-02, CW06-02, CW07-02, CW08-02, WR02-02, IP22-R1, IR38-R2, IP20-L1, IP21-L1, KR05-01, TW01-01, TW02-01, TW03-01, TW04-01, TW05-01, TW06-01, TW07-01, TW11-01, KR03-01, TW12-01, TW16-01, TW17-01, TW18-01, TW21-01, ZZ99- |  | EPD | PEM
108 | 0SB | D04Q010 | 10.4.22 | 0SB11UP01 | 415V SWGR O/G MODULE # 0SB11RG | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
109 | 0SB | D02C1.5 | 10.5.01 | 0SB11VC01 | 415V SWGR MOTOR MODULE # 0SB11RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, TW24-02, ZZ99- |  | EPD | EPD
110 | 0SB | D03L2.5 | 10.4.26 | 0SB11VP01 | 415V SWGR MOTOR MODULE # 0SB11RH | SCALE/CORRISION INHIBITOR AGITATOR PDN50AE001 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, TW24-02, ZZ99- |  | EPD | PEM
111 | 0SB | D02C1.5 | 10.5.01 | 0SB12BC01 | 415V SWGR MOTOR MODULE # 0SB12FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 82 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, TW24-02, TW25-02, ZZ99- |  | EPD | EPD
112 | 0SB | D03L2.5 | 10.4.26 | 0SB12BP01 | 415V SWGR MOTOR MODULE # 0SB12FB | ACID DILUTION PUMP PDN60AP001 (2.2 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, KR01-02, TW22-02, TW23-02, TW24-02, TW25-02, ZZ99- |  | EPD | PEM
113 | 0SB | D02C1.5 | 10.5.01 | 0SB12GC01 | 415V SWGR MOTOR MODULE # 0SB12FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 117 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, ZZ99- |  | EPD | EPD
114 | 0SB | D03Q025 | 10.4.12 | 0SB12GP01 | 415V SWGR MOTOR MODULE # 0SB12FG | DILUTION WATER PUMP FOR CW-P3C | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 115 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | CW03-01, CW04-01, CW05-01, CW06-01, CW07-01, CW08-01, WR02-01, IP22-L1, IR38-R2, IP20-L1, IP21-L1, IP62-01, IP63-01, IP64-01, GR03-01, CI01-01, CI02-01, CI07-01, CI08-01, CI09-01, ZZ99- |  | EPD | PEM
115 | 0SB | D3HQ025 | 10.4.18 | 0SB12IP01 | 415V SWGR O/G MODULE # 0SB12FI | AC FOR CONTROL ROOM-G (15 kW) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (15 kW) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
116 | 0SB | D02C1.5 | 10.5.01 | 0SB12QC01 | 415V SWGR MOTOR MODULE # 0SB12RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | EPD
117 | 0SB | D03L2.5 | 10.4.26 | 0SB12QP01 | 415V SWGR MOTOR MODULE # 0SB12RC | HCl DOSING PUMP FOR PT-CLO2-DP1C (0.55 kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, IP62-03, IP63-03, IP64-03, GR03-03, CI01-03, CI02-03, CI07-03, CI08-03, CI09-03, CI15-03, CI16-03, CI17-03, CI18-03, ZZ99- |  | EPD | PEM
118 | 0SB | D02C1.5 | 10.5.01 | 0SB12RC01 | 415V SWGR MOTOR MODULE # 0SB12RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, TW12-02, TW16-02, TW17-02, TW18-02, TW19-02, TW20-02, ZZ99- |  | EPD | EPD
119 | 0SB | D03L2.5 | 10.4.26 | 0SB12RP01 | 415V SWGR MOTOR MODULE # 0SB12RD | SULPHURIC ACID UNLOADING PUMP PDN03AP001 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | POWER SUPPLY (3.7kW) | XLPE-CU UNARMOURED | CW03-04, CW04-04, CW05-04, CW06-04, CW07-04, CW08-04, WR02-04, IP22-R3, IR38-L3, IP20-R2, IP21-R2, KR05-02, TW01-02, TW02-02, TW03-02, TW04-02, TW05-02, TW06-02, TW07-02, TW11-02, KR03-02, TW12-02, TW16-02, TW17-02, TW18-02, TW19-02, TW20-02, ZZ99- |  | EPD | PEM
120 | 0SB | D3HQ025 | 10.4.18 | 0SB12WP01 | 415V SWGR O/G MODULE # 0SB12RI | SCREEN & GATE HANDLING-B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 74 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | CW03-01, CW02-01, CW01-01, WR01-01, IP04-01, IP05-02, IP06-02, WR07-02, CW09-02, CW10-02, CW12-02, CW14-02, ZZ99- |  | EPD | PEM
1 | 0SC | D02C1.5 | 10.5.01 | 0SC01BC01 | 415V SWGR MOTOR MODULE # 0SC01FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP55-02, ZZ99- |  | EPD | EPD
2 | 0SC | D02L2.5 | 10.4.24 | 0SC01BC02 | 415V SWGR MOTOR MODULE # 0SC01FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP55-02, ZZ99- |  | EPD | PEM
3 | 0SC | D03Q050 | 10.4.14 | 0SC01BP01 | 415V SWGR MOTOR MODULE # 0SC01FB | SERVICE WATER PUMP-A | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP55-01, ZZ99- |  | EPD | PEM
4 | 0SC | D03Q010 | 10.4.11 | 0SC01CP01 | 415V SWGR O/G MODULE # 0SC01FC | AXIAL FAN FOR PH-B1-2.2 kW | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-AL UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, ZZ99- |  | EPD | PEM
5 | 0SC | D03Q010 | 10.4.11 | 0SC01EP01 | 415V SWGR O/G MODULE # 0SC01FE | AXIAL FAN FOR PH-D1-2.2 kW | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-AL UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, ZZ99- |  | EPD | PEM
6 | 0SC | D02Q025 | 10.4.07 | 0SC01FP01 | 415V SWGR O/G MODULE # 0SC01FF | DIESEL ENGINE CONTROL PANEL FOR HYDRANT PUMP-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, ZZ99- |  | EPD | PEM
7 | 0SC | D03L2.5 | 10.4.26 | 0SC01GP01 | 415V SWGR O/G MODULE # 0SC01FG | AXIAL FAN FOR PH-B2-1.1 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 199 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, ZZ99- |  | EPD | PEM
8 | 0SC | D02C1.5 | 10.5.01 | 0SC01PC01 | 415V SWGR MOTOR MODULE # 0SC01RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 179 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW19-02, FW20-02, ZZ99- |  | EPD | EPD
9 | 0SC | D02L2.5 | 10.4.24 | 0SC01PC02 | 415V SWGR MOTOR MODULE # 0SC01RB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 179 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW19-02, FW20-02, ZZ99- |  | EPD | PEM
10 | 0SC | D03Q050 | 10.4.14 | 0SC01PP01 | 415V SWGR MOTOR MODULE # 0SC01RB | SPRAY JOCKEY PUMP-A | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 178 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW19-01, FW20-01, ZZ99- |  | EPD | PEM
11 | 0SC | D02Q025 | 10.4.07 | 0SC01QP01 | 415V SWGR O/G MODULE # 0SC01RC | BATTERY CHARGER FOR DIESEL ENGINE OF HYDRANT PUMP-A-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 175 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, ZZ99- |  | EPD | PEM
12 | 0SC | D03L2.5 | 10.4.26 | 0SC01RP01 | 415V SWGR O/G MODULE # 0SC01RD | AXIAL FAN FOR PH-D2-1.1 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 199 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, ZZ99- |  | EPD | PEM
13 | 0SC | D02Q025 | 10.4.07 | 0SC01SP01 | 415V SWGR O/G MODULE # 0SC01RE | BATTERY CHARGER FOR DIESEL ENGINE OF SPRAY PUMP-A-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 180 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, ZZ99- |  | EPD | PEM
14 | 0SC | D03L2.5 | 10.4.26 | 0SC01TP01 | 415V SWGR O/G MODULE # 0SC01RF | AXIAL FAN FOR PH-F2-1.1 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 165 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW06-02, FW07-02, ZZ99- |  | EPD | PEM
15 | 0SC | D02Q010 | 10.4.06 | 0SC02GP01 | 415V SWGR O/G MODULE # 0SC02FG | REPEATER PANEL-4-1 kW | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (1kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
16 | 0SC | D03L2.5 | 10.4.26 | 0SC02QP01 | 415V SWGR O/G MODULE # 0SC02RC | AXIAL FAN FOR BATTERY ROOM-B-0.55 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | Hold |  | EPD | PEM
17 | 0SC | D02Q025 | 10.4.07 | 0SC02RP01 | 415V SWGR O/G MODULE # 0SC02RD | SPLIT AC FOR CONTROL ROOM-A1-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 166 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW06-01, FW07-01, ZZ99- |  | EPD | PEM
18 | 0SC | D02Q025 | 10.4.07 | 0SC02TP01 | 415V SWGR O/G MODULE # 0SC02RF | SPLIT AC FOR CONTROL ROOM-C1-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 166 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW06-01, FW07-01, ZZ99- |  | EPD | PEM
19 | 0SC | D02C1.5 | 10.5.01 | 0SC03PC01 | 415V SWGR MOTOR MODULE # 0SC03RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 174 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, ZZ99- |  | EPD | EPD
20 | 0SC | D02L2.5 | 10.4.24 | 0SC03PC02 | 415V SWGR MOTOR MODULE # 0SC03RB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 174 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, ZZ99- |  | EPD | PEM
21 | 0SC | D03Q050 | 10.4.14 | 0SC03PP01 | 415V SWGR MOTOR MODULE # 0SC03RB | HYDRANT JOCKEY PUMP-A | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 172 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, ZZ99- |  | EPD | PEM
22 | 0SC | D02C1.5 | 10.5.01 | 0SC03QC01 | 415V SWGR MOTOR MODULE # 0SC03RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW23-02, ZZ99- |  | EPD | EPD
23 | 0SC | D03Q025 | 10.4.12 | 0SC03QP01 | 415V SWGR MOTOR MODULE # 0SC03RC | POTABLE WATER PUMP-A | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 148 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW23-01, ZZ99- |  | EPD | PEM
24 | 0SC | D02Q025 | 10.4.07 | 0SC04EP01 | 415V SWGR O/G MODULE # 0SC04FE | SPLIT AC FOR CONTROL ROOM-E1-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, ZZ99- |  | EPD | PEM
25 | 0SC | D3HQ025 | 10.4.18 | 0SC04RP01 | 415V SWGR O/G MODULE # 0SC04RD | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
26 | 0SC | D03L2.5 | 10.4.26 | 0SC04SP01 | 415V SWGR O/G MODULE # 0SC04RE | AXIAL SUPPLY FAN FOR MCC ROOM-A-2.2 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
27 | 0SC | D02Q025 | 10.4.07 | 0SC04TP01 | 415V SWGR O/G MODULE # 0SC04RF | SPLIT AC FOR CONTROL ROOM-A2-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 164 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R2, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, ZZ99- |  | EPD | PEM
28 | 0SC | D02Q025 | 10.4.07 | 0SC04UP01 | 415V SWGR O/G MODULE # 0SC04RG | SPLIT AC FOR CONTROL ROOM-C2-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 169 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R2, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, ZZ99- |  | EPD | PEM
29 | 0SC | D03L2.5 | 10.4.26 | 0SC04VP01 | 415V SWGR O/G MODULE # 0SC04RH | AXIAL SUPPLY FAN FOR MCC ROOM-C-2.2 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
30 | 0SC | D03L2.5 | 10.4.26 | 0SC04WP01 | 415V SWGR O/G MODULE # 0SC04RI | AXIAL SUPPLY FAN FOR MCC ROOM-E-2.2 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
31 | 0SC | D02C1.5 | 10.5.01 | 0SC05CC01 | 415V SWGR MOTOR MODULE # 0SC05FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP05-L4, FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP55-02, ZZ99- |  | EPD | EPD
32 | 0SC | D03Q025 | 10.4.12 | 0SC05CP01 | 415V SWGR MOTOR MODULE # 0SC05FC | HVAC MUP PUMP-A | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | FP05-R1, FP04-R1, FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP55-01, ZZ99- |  | EPD | PEM
33 | 0SC | D02Q025 | 10.4.07 | 0SC05DP01 | 415V SWGR O/G MODULE # 0SC05FD | SPLIT AC FOR CONTROL ROOM-E2-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 167 | [5 empty] | POWER SUPPLY (3 kW) | XLPE-AL UNARMOURED | FP05-L2, FP04-L2, FP03-L2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, ZZ99- |  | EPD | PEM
34 | 0SC | D03L2.5 | 10.4.26 | 0SC05FP01 | 415V SWGR O/G MODULE # 0SC05FF | AXIAL EXHAUST FAN FOR BATTERY ROOM-B-0.55 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
35 | 0SC | D04Q010 | 10.4.22 | 0SC05HP01 | 415V SWGR O/G MODULE # 0SC05FH | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
36 | 0SC | D02L2.5 | 10.4.24 | 0SC05PP01 | 415V SWGR O/G MODULE # 0SC05RB | PROPELLOR FAN-A-0.1kW | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | FP05-L4, FP06-L4, FP22-02, FP21-02, FR03-02, ZZ99- |  | EPD | PEM
37 | 0SC | D04Q010 | 10.4.22 | 0SC05QP01 | 415V SWGR O/G MODULE # 0SC05RC | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
38 | 0SC | D02L2.5 | 10.4.24 | 0SC05TP01 | 415V SWGR O/G MODULE # 0SC05RF | PROPELLOR FAN-C-0.1kW | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | FP05-L4, FP06-L4, FP22-02, FP21-02, FR03-02, ZZ99- |  | EPD | PEM
39 | 0SC | D3HQ025 | 10.4.18 | 0SC05VP01 | 415V SWGR O/G MODULE # 0SC05RH | PORTABLE SUMP PUMP A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
40 | 0SC | D03L2.5 | 10.4.26 | 0SC07CP01 | 415V SWGR O/G MODULE # 0SC07FC | AXIAL FAN FOR PH-A1-2.2 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, ZZ99- |  | EPD | PEM
41 | 0SC | D03L2.5 | 10.4.26 | 0SC07DP01 | 415V SWGR O/G MODULE # 0SC07FD | AXIAL FAN FOR PH-C1-2.2 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 203 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, ZZ99- |  | EPD | PEM
42 | 0SC | D02Q025 | 10.4.07 | 0SC07EP01 | 415V SWGR O/G MODULE # 0SC07FE | DIESEL ENGINE CONTROL PANEL FOR SPRAY PUMP-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 162 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | FP04-R1, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, ZZ99- |  | EPD | PEM
43 | 0SC | D02Q025 | 10.4.07 | 0SC07FP01 | 415V SWGR O/G MODULE # 0SC07FF | BATTERY CHARGER FOR DIESEL ENGINE OF HYDRANT PUMP-B-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 173 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | FP04-R1, FP03-R2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, ZZ99- |  | EPD | PEM
44 | 0SC | D03L2.5 | 10.4.26 | 0SC07GP01 | 415V SWGR O/G MODULE # 0SC07FG | AXIAL FAN FOR PH-A2-1.1 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-CU UNARMOURED | FP04-L4, FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, ZZ99- |  | EPD | PEM
45 | 0SC | D02C1.5 | 10.5.01 | 0SC08BC01 | 415V SWGR MOTOR MODULE # 0SC08FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW19-02, FW20-02, ZZ99- |  | EPD | EPD
46 | 0SC | D02L2.5 | 10.4.24 | 0SC08BC02 | 415V SWGR MOTOR MODULE # 0SC08FB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW19-02, FW20-02, ZZ99- |  | EPD | PEM
47 | 0SC | D03Q050 | 10.4.14 | 0SC08BP01 | 415V SWGR MOTOR MODULE # 0SC08FB | SPRAY JOCKEY PUMP-B | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 172 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW19-01, FW20-01, ZZ99- |  | EPD | PEM
48 | 0SC | D02C1.5 | 10.5.01 | 0SC08PC01 | 415V SWGR MOTOR MODULE # 0SC08RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW25-02, ZZ99- |  | EPD | EPD
49 | 0SC | D02L2.5 | 10.4.24 | 0SC08PC02 | 415V SWGR MOTOR MODULE # 0SC08RB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW25-02, ZZ99- |  | EPD | PEM
50 | 0SC | D03Q050 | 10.4.14 | 0SC08PP01 | 415V SWGR MOTOR MODULE # 0SC08RB | HYDRANT JOCKEY PUMP-B | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 161 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW25-01, ZZ99- |  | EPD | PEM
51 | 0SC | D3HQ025 | 10.4.18 | 0SC08QP01 | 415V SWGR O/G MODULE # 0SC08RC | PORTABLE SUMP PUMP B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
52 | 0SC | D03L2.5 | 10.4.26 | 0SC08RP01 | 415V SWGR O/G MODULE # 0SC08RD | AXIAL FAN FOR BATTERY ROOM-A-0.55 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | Hold |  | EPD | PEM
53 | 0SC | D03L2.5 | 10.4.26 | 0SC08TP01 | 415V SWGR O/G MODULE # 0SC08RE | AXIAL FAN FOR BATTERY ROOM-C-0.55 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | Hold |  | EPD | PEM
54 | 0SC | D02C1.5 | 10.5.01 | 0SC10PC01 | 415V SWGR MOTOR MODULE # 0SC10RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP55-02, ZZ99- |  | EPD | EPD
55 | 0SC | D02L2.5 | 10.4.24 | 0SC10PC02 | 415V SWGR MOTOR MODULE # 0SC10RB | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP55-02, ZZ99- |  | EPD | PEM
56 | 0SC | D03Q050 | 10.4.14 | 0SC10PP01 | 415V SWGR MOTOR MODULE # 0SC10RB | SERVICE WATER PUMP-B | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 88 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP55-01, ZZ99- |  | EPD | PEM
57 | 0SC | D02C1.5 | 10.5.01 | 0SC11BC01 | 415V SWGR MOTOR MODULE # 0SC11FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP55-02, ZZ99- |  | EPD | EPD
58 | 0SC | D03Q025 | 10.4.12 | 0SC11BP01 | 415V SWGR MOTOR MODULE # 0SC11FB | HVAC MUP PUMP-B | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 88 | [5 empty] | POWER SUPPLY (11kW) | XLPE-AL UNARMOURED | FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP55-01, ZZ99- |  | EPD | PEM
59 | 0SC | D03L2.5 | 10.4.26 | 0SC11DP01 | 415V SWGR O/G MODULE # 0SC11FD | AXIAL SUPPLY FAN FOR MCC ROOM-D-2.2 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
60 | 0SC | D03L2.5 | 10.4.26 | 0SC11GP01 | 415V SWGR O/G MODULE # 0SC11FG | AXIAL EXHAUST FAN FOR BATTERY ROOM-A1-0.55 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
61 | 0SC | D02L2.5 | 10.4.24 | 0SC11HP01 | 415V SWGR O/G MODULE # 0SC11FH | PROPELLOR FAN-B-0.1kW | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | Hold |  | EPD | PEM
62 | 0SC | D03L2.5 | 10.4.26 | 0SC11PP01 | 415V SWGR O/G MODULE # 0SC11RB | AXIAL EXHAUST FAN FOR BATTERY ROOM-A2-0.55 kW | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (0.55 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
63 | 0SC | D04Q010 | 10.4.22 | 0SC11QP01 | 415V SWGR O/G MODULE # 0SC11RC | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
64 | 0SC | D04Q010 | 10.4.22 | 0SC11RP01 | 415V SWGR O/G MODULE # 0SC11RD | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
65 | 0SC | D02C1.5 | 10.5.01 | 0SC12BC01 | 415V SWGR MOTOR MODULE # 0SC12FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | SITE ROUTING |  | EPD | EPD
66 | 0SC | D03Q025 | 10.4.12 | 0SC12BP01 | 415V SWGR MOTOR MODULE # 0SC12FB | POTABLE WATER PUMP-B | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
67 | 0SC | D03L2.5 | 10.4.26 | 0SC12CP01 | 415V SWGR O/G MODULE # 0SC12FC | AXIAL SUPPLY FAN FOR MCC ROOM-B-2.2 Kw | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (2.2 kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
68 | 0SC | D3HQ025 | 10.4.18 | 0SC12DP01 | 415V SWGR O/G MODULE # 0SC12FD | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
69 | 0SC | D02L2.5 | 10.4.24 | 0SC12GP01 | 415V SWGR O/G MODULE # 0SC12FG | PROPELLOR FAN-D-0.1kW | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | Hold |  | EPD | PEM
70 | 0SC | D3HQ095 | 10.4.20 | 0SC12QP01 | 415V SWGR O/G MODULE # 0SC12RC | FIRE WATER PUMP HOUSE CRANE (5T) | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 198 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | FP03-R1, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, ZZ99- |  | EPD | PEM
71 | 0SC | D02Q025 | 10.4.07 | 0SC12RP01 | 415V SWGR O/G MODULE # 0SC12RD | BATTERY CHARGER FOR DIESEL ENGINE OF SPRAY PUMP-B-3 kW | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 172 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | FP03-L2, FP01-02, FR01-02, IP53-02, IP54-02, IP56-02, IP57-02, IP58-02, IP59-02, IP60-02, IP61-02, ZR01-02, FW01-02, FW02-02, FW03-02, FW04-02, FW05-02, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, ZZ99- |  | EPD | PEM
72 | 0SC | D03Q010 | 10.4.11 | 0SC12SP01 | 415V SWGR O/G MODULE # 0SC12RE | AXIAL FAN FOR PH-C2-1.1 kW | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-AL UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, ZZ99- |  | EPD | PEM
73 | 0SC | D03Q010 | 10.4.11 | 0SC12UP01 | 415V SWGR O/G MODULE # 0SC12RG | AXIAL FAN FOR PH-E2-1.1 kW | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY (1.1 kW) | XLPE-AL UNARMOURED | FP03-L4, FP01-03, FR01-03, IP53-03, IP54-03, IP56-03, IP57-03, IP58-03, IP59-03, IP60-03, IP61-03, ZR01-03, FW01-03, FW02-03, FW03-03, FW04-03, FW05-03, FW08-02, FW09-02, FW10-02, FW11-02, FW12-02, FW13-02, FW14-02, ZZ99- |  | EPD | PEM
1 | 0SD | D02Q010 | 10.4.06 | 0SD01BP01 | 415V SWGR O/G MODULE # 0DC01FB | MOTORISED FIRE DAMPER (AHU 3-4)-A | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
2 | 0SD | D3HQ025 | 10.4.18 | 0SD01CP01 | 415V SWGR O/G MODULE # 0SD01FC | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
3 | 0SD | D02L2.5 | 10.4.24 | 0SD01DP01 | 415V SWGR O/G MODULE # 0SD01FD | MOTORISED BUTTERFLY VALVE-A (0.2kW) (PLANT ROOM) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | PEM
4 | 0SD | D04Q010 | 10.4.22 | 0SD01EP01 | 415V SWGR O/G MODULE # 0SD01FE | AIR HANDLING UNIT (AHU 1-2)-A | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
5 | 0SD | D04Q010 | 10.4.22 | 0SD01FP01 | 415V SWGR O/G MODULE # 0SD01FF | AIR HANDLING UNIT (AHU 3-4)-A | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
6 | 0SD | D02L2.5 | 10.4.24 | 0SD01GP01 | 415V SWGR O/G MODULE # 0SD01FG | MOTORISED BUTTERFLY VALVE-C (PLANT ROOM) (0.2kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | PEM
7 | 0SD | D02C1.5 | 10.5.01 | 0SD01PC01 | 415V SWGR MOTOR MODULE # 0SD01RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | EPD
8 | 0SD | D03L2.5 | 10.4.26 | 0SD01PP01 | 415V SWGR MOTOR MODULE # 0SD01RB | COOLING TOWER-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
9 | 0SD | D02C1.5 | 10.5.01 | 0SD01QC01 | 415V SWGR MOTOR MODULE # 0SD01RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | EPD
10 | 0SD | D03L2.5 | 10.4.26 | 0SD01QP01 | 415V SWGR MOTOR MODULE # 0SD01RC | FRESH AIR FAN FOR AHU ROOM (AHU 1-2) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | PEM
11 | 0SD | D04Q010 | 10.4.22 | 0SD01RP01 | 415V SWGR O/G MODULE # 0SD01RD | STRIP HEATER FOR AHU ROOM (AHU 1-2) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (9kW) | XLPE-AL UNARMOURED | AD02-R1, AD01-R1, AR01-R1, IL29-R1, IL28-R1, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
12 | 0SD | D02L2.5 | 10.4.24 | 0SD01TP01 | 415V SWGR O/G MODULE # 0SD01RF | MOTORISED BUTTERFLY VALVE-E (TERRACE) (0.2kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
13 | 0SD | D03L2.5 | 10.4.26 | 0SD01UP01 | 415V SWGR O/G MODULE # 0SD01RG | SUPPY AIR FAN FOR MCC ROOM-A (0.75kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
14 | 0SD | D03L2.5 | 10.4.26 | 0SD01VP01 | 415V SWGR O/G MODULE # 0SD01RH | SUPPY AIR FAN FOR MCC ROOM-C (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
15 | 0SD | D02C1.5 | 10.5.01 | 0SD01WC01 | 415V SWGR MOTOR MODULE # 0SD01RI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | EPD
16 | 0SD | D03L2.5 | 10.4.26 | 0SD01WP01 | 415V SWGR MOTOR MODULE # 0SD01RI | FRESH AIR FAN FOR AHU ROOM (AHU 3-4) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | PEM
17 | 0SD | D01Q630 | 10.4.05 | 0SD02BP01 | 415V SWGR O/G MODULE # 0SD02FB | O & M ACDB # 0SE SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-R1, IL49-R1, IL50-R1, IL51-R1, IL52-R1, OR01-R1, OS01-R1, OS02-R1, ZZ99- |  | EPD | PEM
18 | 0SD | D01Q630 | 10.4.05 | 0SD02BP02 | 415V SWGR O/G MODULE # 0SD02FB | O & M ACDB # 0SE SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-R1, IL49-R1, IL50-R1, IL51-R1, IL52-R1, OR01-R1, OS01-R1, OS02-R1, ZZ99- |  | EPD | PEM
19 | 0SD | D01Q630 | 10.4.05 | 0SD02BP03 | 415V SWGR O/G MODULE # 0SD02FB | O & M ACDB # 0SE SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 75 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-R1, IL49-R1, IL50-R1, IL51-R1, IL52-R1, OR01-R1, OS01-R1, OS02-R1, ZZ99- |  | EPD | PEM
20 | 0SD | D01Q400 | 10.4.04 | 0SD02BP04 | 415V SWGR O/G MODULE # 0SD02FB | O & M ACDB # 0SE SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-L1, IL49-L1, IL50-L1, IL51-L1, IL52-L1, OR01-L1, OS01-L1, OS02-L1, ZZ99- |  | EPD | PEM
21 | 0SD | D03L2.5 | 10.4.26 | 0SD02DP01 | 415V SWGR O/G MODULE # 0SD02FD | EXHAUST AIR FAN FOR BATTERY ROOM-A (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD02-L3, AD03-L3, AD04-L3, AD08-02, AD09-02, AD11-02, AD12-02, AD13-02, AD14-02, ZZ99- |  | EPD | PEM
22 | 0SD | D03L2.5 | 10.4.26 | 0SD02EP01 | 415V SWGR O/G MODULE # 0SD02FE | EXHAUST AIR FAN FOR AC PLANT ROOM-A (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, ZZ99- |  | EPD | PEM
23 | 0SD | D3HQ095 | 10.4.20 | 0SD02HP01 | 415V SWGR O/G MODULE # 0SD02FH | SCREW CHILLER (50 TR)-A | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (65kW) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
24 | 0SD | D04Q010 | 10.4.22 | 0SD02PP01 | 415V SWGR O/G MODULE # 0SD02RB | STRIP HEATER FOR AHU ROOM (AHU 3-4)-C | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (6kW) | XLPE-AL UNARMOURED | AD02-R1, AD01-R1, AR01-R1, IL29-R1, IL28-R1, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
25 | 0SD | D03L2.5 | 10.4.26 | 0SD02QP01 | 415V SWGR O/G MODULE # 0SD02RC | EXHAUST AIR FAN FOR AC PLANT ROOM-C (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, ZZ99- |  | EPD | PEM
26 | 0SD | D02C1.5 | 10.5.01 | 0SD02RC01 | 415V SWGR MOTOR MODULE # 0SD02RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 96 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | EPD
27 | 0SD | D03Q010 | 10.4.11 | 0SD02RP01 | 415V SWGR MOTOR MODULE # 0SD02RD | CHILLED WATER PUPM-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AR03-01, ZZ99- |  | EPD | PEM
28 | 0SD | D02L2.5 | 10.4.24 | 0SD02SP01 | 415V SWGR O/G MODULE # 0SD02RE | 3 WAY MIXING VALVES (AHU 1-2)-B (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | PEM
29 | 0SD | D02L2.5 | 10.4.24 | 0SD02TP01 | 415V SWGR O/G MODULE # 0SD02RF | 3 WAY MIXING VALVES (AHU 3-4)-B (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | PEM
30 | 0SD | D02C1.5 | 10.5.01 | 0SD02UC01 | 415V SWGR MOTOR MODULE # 0SD02RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | EPD
31 | 0SD | D03L2.5 | 10.4.26 | 0SD02UP01 | 415V SWGR MOTOR MODULE # 0SD02RG | PUMPS FOR SOFTENING WATER PLANT-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
32 | 0SD | D02C1.5 | 10.5.01 | 0SD02VC01 | 415V SWGR MOTOR MODULE # 0SD02RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | EPD
33 | 0SD | D03L2.5 | 10.4.26 | 0SD02VP01 | 415V SWGR MOTOR MODULE # 0SD02RH | PUMPS FOR SOFTENING WATER PLANT-C | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
34 | 0SD | D3HQ025 | 10.4.18 | 0SD02WP01 | 415V SWGR O/G MODULE # 0SD02RI | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
35 | 0SD | D02L2.5 | 10.4.24 | 0SD03BP01 | 415V SWGR O/G MODULE # 0SD03FB | PROPELLOR FANS FOR STORE UTILITY ROOM-A (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, ZZ99- |  | EPD | PEM
36 | 0SD | D3HQ025 | 10.4.18 | 0SD03PP01 | 415V SWGR O/G MODULE # 0SD03RB | PORTABLE SUMP PUMP A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
37 | 0SD | D04Q010 | 10.4.22 | 0SD03QP01 | 415V SWGR O/G MODULE # 0SD03RC | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 84 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD02-R1, AD01-R1, AR01-R1, IL29-R1, IL28-R1, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, ZZ99- |  | EPD | PEM
38 | 0SD | D02C1.5 | 10.5.01 | 0SD03RC01 | 415V SWGR MOTOR MODULE # 0SD03RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | EPD
39 | 0SD | D03Q010 | 10.4.11 | 0SD03RP01 | 415V SWGR MOTOR MODULE # 0SD03RD | CONDENSER WATER PUPM-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 99 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AR03-01, ZZ99- |  | EPD | PEM
40 | 0SD | D02L2.5 | 10.4.24 | 0SD03SP01 | 415V SWGR O/G MODULE # 0SD03RE | REPEATER PANEL-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY (1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
41 | 0SD | D04Q010 | 10.4.22 | 0SD03TP01 | 415V SWGR O/G MODULE # 0SD03RF | STRIP HEATER FOR AHU ROOM (AHU 3-4)-A | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (6kW) | XLPE-AL UNARMOURED | AD02-R1, AD01-R1, AR01-R1, IL29-R1, IL28-R1, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
42 | 0SD | D04Q010 | 10.4.22 | 0SD04BP01 | 415V SWGR O/G MODULE # 0SD04FB | STRIP HEATER FOR AHU ROOM (AHU 3-4)-B | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (6kW) | XLPE-AL UNARMOURED | AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
43 | 0SD | D04Q010 | 10.4.22 | 0SD04GP01 | 415V SWGR O/G MODULE # 0SD04FG | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 87 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, ZZ99- |  | EPD | PEM
44 | 0SD | E04V0.5 | 10.7.02 | 0SD05AC01 | 415V SWGR I/C MODULE # 0SD05FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 17 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | AD03-R3, AD04-R3, AD08-03, AD09-03, AD11-03 |  | EPD | EDN
45 | 0SD | D02C1.5 | 10.5.01 | 0SD05AC02 | 415V SWGR I/C MODULE # 0SD05FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 210 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL27-L3, IL26-L3, IL25-L3, IL24-L3, IL23-L3, IL22-L3, IL21-L3, IL20-L3, IL19-L3, IL18-L3, IL17-L3, IL16-L3, IL15-L3, IL14-L3, IL13-L3, IL12-L3, IL11-L3, IL10-L3, PR02-R2, ET10-L4, ET08-L4, ET07-L4, ET06-L4, ZZ99- |  | EPD | EPD
46 | 0SD | E04V0.5 | 10.7.02 | 0SD05AC03 | 415V SWGR I/C MODULE # 0SD05FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 17 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | AD03-R3, AD04-R3, AD08-03, AD09-03, AD11-03 |  | EPD | EDN
47 | 0SD | E04V0.5 | 10.7.02 | 0SD06AC01 | 415V SWGR B/C MODULE # 0SD06FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 17 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | AD03-R3, AD04-R3, AD08-03, AD09-03, AD11-03 |  | EPD | EDN
48 | 0SD | E04V0.5 | 10.7.02 | 0SD06AC02 | 415V SWGR B/C MODULE # 0SD06FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 17 | [5 empty] | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | AD03-R3, AD04-R3, AD08-03, AD09-03, AD11-03 |  | EPD | EDN
49 | 0SD | E04V0.5 | 10.7.02 | 0SD08AC01 | 415V SWGR I/C MODULE # 0SD08FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 15 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | AD04-R3, AD08-03, AD09-03, AD11-03 |  | EPD | EDN
50 | 0SD | D02C1.5 | 10.5.01 | 0SD08AC02 | 415V SWGR I/C MODULE # 0SD08FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 219 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL27-L3, IL26-L3, IL25-L3, IL24-L3, IL23-L3, IL22-L3, IL21-L3, IL20-L3, IL19-L3, IL18-L3, IL17-L3, IL16-L3, IL15-L3, IL14-L3, IL13-L3, IL12-L3, IL11-L3, IL10-L3, PR02-R2, ET10-L4, ET08-L4, ET07-L4, ET06-L4, ET05-L4, ET04-L4, ZZ99- |  | EPD | EPD
51 | 0SD | E04V0.5 | 10.7.02 | 0SD08AC03 | 415V SWGR I/C MODULE # 0SD08FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 15 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | AD04-R3, AD08-03, AD09-03, AD11-03 |  | EPD | EDN
52 | 0SD | D3HQ025 | 10.4.18 | 0SD09FP01 | 415V SWGR O/G MODULE # 0SD09FF | PORTABLE SUMP PUMP B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
53 | 0SD | D3HQ095 | 10.4.20 | 0SD09HP01 | 415V SWGR O/G MODULE # 0SD09FH | SCREW CHILLER (50 TR)-B | 3.5C X 095 XLPE-Al FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (65kW) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
54 | 0SD | D02C1.5 | 10.5.01 | 0SD09WC01 | 415V SWGR MOTOR MODULE # 0SD09RI | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | EPD
55 | 0SD | D03Q010 | 10.4.11 | 0SD09WP01 | 415V SWGR MOTOR MODULE # 0SD09RI | CONDENSER WATER PUPM-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 102 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AR03-01, ZZ99- |  | EPD | PEM
56 | 0SD | D3HQ025 | 10.4.18 | 0SD10BP01 | 415V SWGR O/G MODULE # 0SD10FB | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 102 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AR03-01, ZZ99- |  | EPD | PEM
57 | 0SD | D04Q010 | 10.4.22 | 0SD10EP01 | 415V SWGR O/G MODULE # 0SD10FE | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, ZZ99- |  | EPD | PEM
58 | 0SD | D01Q630 | 10.4.05 | 0SD10PP01 | 415V SWGR O/G MODULE # 0SD10RB | O & M ACDB # 0SE SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-L1, IL49-L1, IL50-L1, IL51-L1, IL52-L1, OR01-L1, OS01-L1, OS02-L1, OS03-L1, OS04-L1, OS05-L1, ZZ99- |  | EPD | PEM
59 | 0SD | D01Q630 | 10.4.05 | 0SD10PP02 | 415V SWGR O/G MODULE # 0SD10RB | O & M ACDB # 0SE SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-L1, IL49-L1, IL50-L1, IL51-L1, IL52-L1, OR01-L1, OS01-L1, OS02-L1, OS03-L1, OS04-L1, OS05-L1, ZZ99- |  | EPD | PEM
60 | 0SD | D01Q630 | 10.4.05 | 0SD10PP03 | 415V SWGR O/G MODULE # 0SD10RB | O & M ACDB # 0SE SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-L1, IL49-L1, IL50-L1, IL51-L1, IL52-L1, OR01-L1, OS01-L1, OS02-L1, OS03-L1, OS04-L1, OS05-L1, ZZ99- |  | EPD | PEM
61 | 0SD | D01Q400 | 10.4.04 | 0SD10PP04 | 415V SWGR O/G MODULE # 0SD10RB | O & M ACDB # 0SE SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (400A) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL27-L1, IL26-L1, IL25-L1, IL48-L1, IL49-L1, IL50-L1, IL51-L1, IL52-L1, OR01-L1, OS01-L1, OS02-L1, OS03-L1, OS04-L1, OS05-L1, ZZ99- |  | EPD | PEM
62 | 0SD | D02C1.5 | 10.5.01 | 0SD10RC01 | 415V SWGR MOTOR MODULE # 0SD10RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | EPD
63 | 0SD | D03Q010 | 10.4.11 | 0SD10RP01 | 415V SWGR MOTOR MODULE # 0SD10RD | CHILLED WATER PUPM-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 102 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AR03-01, ZZ99- |  | EPD | PEM
64 | 0SD | D02L2.5 | 10.4.24 | 0SD11BP01 | 415V SWGR O/G MODULE # 0SD11FB | PROPELLOR FANS FOR STORE UTILITY ROOM-B (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, ZZ99- |  | EPD | PEM
65 | 0SD | D02Q010 | 10.4.06 | 0SD11CP01 | 415V SWGR O/G MODULE # 0SD11FC | MOTORISED FIRE DAMPER (AHU 3-4)-B | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD05-L1, AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
66 | 0SD | D04Q010 | 10.4.22 | 0SD11DP01 | 415V SWGR O/G MODULE # 0SD11FD | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 92 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD05-L1, AD04-L1, AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, ZZ99- |  | EPD | PEM
67 | 0SD | D02L2.5 | 10.4.24 | 0SD11HP01 | 415V SWGR O/G MODULE # 0SD11FH | 3 WAY MIXING VALVES (AHU 3-4)-A | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 117 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | PEM
68 | 0SD | D02Q010 | 10.4.06 | 0SD11IP01 | 415V SWGR O/G MODULE # 0SD11FI | MOTORISED FIRE DAMPER (AHU 1-2)-B | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD05-L1, AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
69 | 0SD | D02C1.5 | 10.5.01 | 0SD11QC01 | 415V SWGR MOTOR MODULE # 0SD11RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | EPD
70 | 0SD | D03L2.5 | 10.4.26 | 0SD11QP01 | 415V SWGR MOTOR MODULE # 0SD11RC | COOLING TOWER-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
71 | 0SD | D04Q010 | 10.4.22 | 0SD11RP01 | 415V SWGR O/G MODULE # 0SD11RD | PAN HUMIDIFIER FOR AHU ROOM (AHU 3-4) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 117 | [5 empty] | POWER SUPPLY (6kW) | XLPE-AL UNARMOURED | AD05-L1, AD04-L1, AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
72 | 0SD | D02Q010 | 10.4.06 | 0SD11SP01 | 415V SWGR O/G MODULE # 0SD11RE | MOTORISED FIRE DAMPER (AHU 1-2)-A | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 116 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | AD05-L1, AD04-L1, AD03-L1, AD02-L1, AD01-L1, AR01-L1, IL29-L1, IL28-L1, IL30-01, IL31-01, IL32-01, IL33-01, IL34-01, IL35-01, IL36-01, IL37-01, IL38-01, AR02-01, AD15-01, AD16-01, AD17-01, AD18-01, AD19-01, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
73 | 0SD | D02C1.5 | 10.5.01 | 0SD11TC01 | 415V SWGR MOTOR MODULE # 0SD11RF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 118 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | EPD
74 | 0SD | D03L2.5 | 10.4.26 | 0SD11TP01 | 415V SWGR MOTOR MODULE # 0SD11RF | PUMPS FOR SOFTENING WATER PLANT-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 118 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
75 | 0SD | D02C1.5 | 10.5.01 | 0SD11UC01 | 415V SWGR MOTOR MODULE # 0SD11RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | EPD
76 | 0SD | D03L2.5 | 10.4.26 | 0SD11UP01 | 415V SWGR MOTOR MODULE # 0SD11RG | PUMPS FOR SOFTENING WATER PLANT-D | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
77 | 0SD | D03L2.5 | 10.4.26 | 0SD11VP01 | 415V SWGR O/G MODULE # 0SD11RH | EXHAUST AIR FAN FOR AC PLANT ROOM-D (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 108 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, ZZ99- |  | EPD | PEM
78 | 0SD | D3HQ025 | 10.4.18 | 0SD11WP01 | 415V SWGR O/G MODULE # 0SD01RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
79 | 0SD | D03L2.5 | 10.4.26 | 0SD12BP01 | 415V SWGR O/G MODULE # 0SD12FB | EXHAUST AIR FAN FOR AC PLANT ROOM-B (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD06-L3, AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, ZZ99- |  | EPD | PEM
80 | 0SD | D03L2.5 | 10.4.26 | 0SD12CP01 | 415V SWGR O/G MODULE # 0SD12FC | EXHAUST AIR FAN FOR BATTERY ROOM-B (0.55kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AD06-L3, AD05-L3, AD08-02, AD09-02, AD11-02, AD12-02, AD13-02, AD14-02, ZZ99- |  | EPD | PEM
81 | 0SD | D02L2.5 | 10.4.24 | 0SD12DP01 | 415V SWGR O/G MODULE # 0SD12FD | 3 WAY MIXING VALVES (AHU 1-2)-A (0.1kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (0.1kW) | XLPE-CU UNARMOURED | AD06-L3, AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, ZZ99- |  | EPD | PEM
82 | 0SD | D03L2.5 | 10.4.26 | 0SD12EP01 | 415V SWGR O/G MODULE # 0SD12FE | SUPPY AIR FAN FOR MCC ROOM-D (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
83 | 0SD | D02L2.5 | 10.4.24 | 0SD12FP01 | 415V SWGR O/G MODULE # 0SD12FF | MOTORISED BUTTERFLY VALVE-F (TERRACE) (0.2kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | AD06-L3, AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AD20-03, AD21-03, AD22-02, AR05-02, AR06-02, ZZ99- |  | EPD | PEM
84 | 0SD | D03L2.5 | 10.4.26 | 0SD12HP01 | 415V SWGR O/G MODULE # 0SD12FH | SUPPY AIR FAN FOR MCC ROOM-B (0.75kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
85 | 0SD | D04Q010 | 10.4.22 | 0SD12QP01 | 415V SWGR O/G MODULE # 0SD12RC | PAN HUMIDIFIER FOR AHU ROOM (AHU 1-2) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (6kW) | XLPE-AL UNARMOURED | AD06-L1, AD05-L1, AD04-L1, AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-01, AD21-01, AD22-01, AR05-01, ZZ99- |  | EPD | PEM
86 | 0SD | D02L2.5 | 10.4.24 | 0SD12RP01 | 415V SWGR O/G MODULE # 0SD12RD | MOTORISED BUTTERFLY VALVE-D (PLANT ROOM) (0.2kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | AD06-L3, AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | PEM
87 | 0SD | D02L2.5 | 10.4.24 | 0SD12SP01 | 415V SWGR O/G MODULE # 0SD12RE | MOTORISED BUTTERFLY VALVE-B (PLANT ROOM) (0.2kW) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (0.2kW) | XLPE-CU UNARMOURED | AD06-L3, AD05-L3, AD04-L3, AD03-L3, AD02-L3, AD01-L3, AR01-L3, IL29-L3, IL28-L3, IL30-03, IL31-03, IL32-03, IL33-03, IL34-03, IL35-03, IL36-03, IL37-03, IL38-03, AR02-03, AD15-03, AD16-03, AD17-03, AD18-03, AD19-03, AR03-02, ZZ99- |  | EPD | PEM
88 | 0SD | D04Q010 | 10.4.22 | 0SD12UP01 | 415V SWGR O/G MODULE # 0SD12RG | AIR HANDLING UNIT (AHU 3-4)-B | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (7.5kW) | XLPE-AL UNARMOURED | AD06-L1, AD05-L1, AD04-L1, AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-02, AD21-02, AD22-01, AR05-02, ZZ99- |  | EPD | PEM
89 | 0SD | D04Q010 | 10.4.22 | 0SD12WP01 | 415V SWGR O/G MODULE # 0SD12RI | AIR HANDLING UNIT (AHU 1-2)-B | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | AD06-L1, AD05-L1, AD04-L1, AD03-L1, AD02-L2, AD01-L2, AR01-L2, IL29-L2, IL28-L2, IL30-02, IL31-02, IL32-02, IL33-02, IL34-02, IL35-02, IL36-02, IL37-02, IL38-02, AR02-02, AD15-02, AD16-02, AD17-02, AD18-02, AD19-02, AD20-02, AD21-02, AD22-01, AR05-02, ZZ99- |  | EPD | PEM
1 | 0SE | D03L2.5 | 10.4.26 | 0SE01CP01 | 415V SWGR O/G MODULE # 0SE01FC | SUPPY AIR FAN FOR SWITCHGEAR ROOM (GROUND FLOOR)-B (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
2 | 0SE | D03L2.5 | 10.4.26 | 0SE01DP01 | 415V SWGR O/G MODULE # 0SE01FD | EXHAUST FAN AREA B/W I-L-6-3A, FIRST FLOOR-B (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS02-L2, OS03-L2, OS04-L2, OS05-L2, OS06-L1, OR02-02, OS07-01, ZZ99- |  | EPD | PEM
3 | 0SE | D03L2.5 | 10.4.26 | 0SE01EP01 | 415V SWGR O/G MODULE # 0SE01FE | EXHAUST FAN AREA B/W I-L-6-3A, FIRST FLOOR-D (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS02-L2, OS03-L2, OS04-L2, OS05-L2, OS06-L1, OR02-02, OS07-01, ZZ99- |  | EPD | PEM
4 | 0SE | D02Q010 | 10.4.06 | 0SE01FP01 | 415V SWGR O/G MODULE # 0SE01FF | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-A | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
5 | 0SE | D02Q010 | 10.4.06 | 0SE01GP01 | 415V SWGR O/G MODULE # 0SE01FG | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-C | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
6 | 0SE | D02Q010 | 10.4.06 | 0SE01PP01 | 415V SWGR O/G MODULE # 0SE01RB | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-E | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 55 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
7 | 0SE | D07C1.5 | 10.5.08 | 0SE01QC01 | 415V SWGR MOTOR MODULE # 0SE01RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 72 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
8 | 0SE | D03Q010 | 10.4.11 | 0SE01QP01 | 415V SWGR MOTOR MODULE # 0SE01RC | RE FAN FOR AREA B/W A-K-13A-16, DOUBLE STOREY (HEAVY MATERIA | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS02-L1, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
9 | 0SE | D02Q010 | 10.4.06 | 0SE01RP01 | 415V SWGR O/G MODULE # 0SE01RD | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-G | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
10 | 0SE | D02Q010 | 10.4.06 | 0SE01SP01 | 415V SWGR O/G MODULE # 0SE01RE | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-J | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
11 | 0SE | D02Q010 | 10.4.06 | 0SE01TP01 | 415V SWGR O/G MODULE # 0SE01RF | AREA B/W C-D-6-7 SPLIT AC (RECEIPT ROOM-1 GROUND FLOOR)-A (3 | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
12 | 0SE | D03L2.5 | 10.4.26 | 0SE01UP01 | 415V SWGR O/G MODULE # 0SE01RG | EXHAUST FAN- AREA B/W A-G-1A-3 GROUND FLOOR (GENERAL LIGHT M | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
13 | 0SE | D03L2.5 | 10.4.26 | 0SE01VP01 | 415V SWGR O/G MODULE # 0SE01RH | EXHAUST FAN- AREA B/W A-G-1A-3 GROUND FLOOR (GENERAL LIGHT M | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
14 | 0SE | D3HQ025 | 10.4.18 | 0SE01WP01 | 415V SWGR O/G MODULE # 0SE01RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | EPD
15 | 0SE | D3HQ025 | 10.4.18 | 0SE02CP01 | 415V SWGR O/G MODULE # 0SE02FC | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 86 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS02-L1, OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | EPD
16 | 0SE | D02Q010 | 10.4.06 | 0SE02DP01 | 415V SWGR O/G MODULE # 0SE02FD | AREA B/W C-D-6-7 SPLIT AC (RECEIPT ROOM-1 GROUND FLOOR)-C (3 | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
17 | 0SE | D03L2.5 | 10.4.26 | 0SE02EP01 | 415V SWGR O/G MODULE # 0SE02FE | EXHAUST FAN- AREA B/W A-G-1A-3 (EXCLUDING HOT & COLD STORAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
18 | 0SE | D02Q010 | 10.4.06 | 0SE02FP01 | 415V SWGR O/G MODULE # 0SE02FF | AREA B/W D-F-9-10 SPLIT AC (RECEIPT ROOM-2 GROUND FLOOR)-A ( | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
19 | 0SE | D03L2.5 | 10.4.26 | 0SE02GP01 | 415V SWGR O/G MODULE # 0SE02FG | EXHAUST FAN- AREA B/W A-G-1A-3 (EXCLUDING HOT & COLD STORAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
20 | 0SE | D07C1.5 | 10.5.08 | 0SE02HC01 | 415V SWGR MOTOR MODULE # 0SE02FH | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
21 | 0SE | D03Q010 | 10.4.11 | 0SE02HP01 | 415V SWGR MOTOR MODULE # 0SE02FH | RE FAN FOR AREA B/W A-K-13A-16, DOUBLE STOREY (HEAVY MATERIA | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS02-L1, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
22 | 0SE | D02Q010 | 10.4.06 | 0SE02IP01 | 415V SWGR O/G MODULE # 0SE02FI | AREA B/W D-F-9-10 SPLIT AC (RECEIPT ROOM-2 GROUND FLOOR)-C ( | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
23 | 0SE | D07C1.5 | 10.5.08 | 0SE02PC01 | 415V SWGR MOTOR MODULE # 0SE02RB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
24 | 0SE | D03Q010 | 10.4.11 | 0SE02PP01 | 415V SWGR MOTOR MODULE # 0SE02RB | RE FAN FOR AREA B/W A-K-13A-16, DOUBLE STOREY (HEAVY MATERIA | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS02-L1, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
25 | 0SE | D07C1.5 | 10.5.08 | 0SE02QC01 | 415V SWGR MOTOR MODULE # 0SE02RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 82 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
26 | 0SE | D03Q010 | 10.4.11 | 0SE02QP01 | 415V SWGR MOTOR MODULE # 0SE02RC | AREA B/W G-L-13A-3A, (EXCLUDING AREA B/W I-L-3A-6) DOUBLE ST | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 79 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS02-L1, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
27 | 0SE | D02Q010 | 10.4.06 | 0SE02RP01 | 415V SWGR O/G MODULE # 0SE02RD | AREA B/W C-D-7-9 SPLIT AC (OFFICE-GROUND FLOOR)-A (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
28 | 0SE | D02Q010 | 10.4.06 | 0SE02SP01 | 415V SWGR O/G MODULE # 0SE02RE | AREA B/W C-D-7-9 SPLIT AC (OFFICE-GROUND FLOOR)-C (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
29 | 0SE | D03L2.5 | 10.4.26 | 0SE02VP01 | 415V SWGR O/G MODULE # 0SE02RH | EXHAUST FAN-COLD STORAGE, AREA B/W A-C-1A-1, FIRST FLOOR-B ( | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
30 | 0SE | D3HQ025 | 10.4.18 | 0SE02WP01 | 415V SWGR O/G MODULE # 0SE02RI | WELDING SOCKET 1 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 82 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
31 | 0SE | D02Q010 | 10.4.06 | 0SE03DP01 | 415V SWGR O/G MODULE # 0SE03FD | AREA B/W C-D-7-9 SPLIT AC (OFFICE-GROUND FLOOR)-E (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
32 | 0SE | D02Q010 | 10.4.06 | 0SE03EP01 | 415V SWGR O/G MODULE # 0SE03FE | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 38 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | PEM
33 | 0SE | D02Q010 | 10.4.06 | 0SE03FP01 | 415V SWGR O/G MODULE # 0SE03FF | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | PEM
34 | 0SE | D02Q010 | 10.4.06 | 0SE03GP01 | 415V SWGR O/G MODULE # 0SE03FG | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
35 | 0SE | D03L2.5 | 10.4.26 | 0SE03HP01 | 415V SWGR O/G MODULE # 0SE03FH | EXHAUST FAN-HOT STORAGE, AREA B/W A-C-1A-1, FIRST FLOOR-B (0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 81 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | OS03-L2, OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
36 | 0SE | D02Q010 | 10.4.06 | 0SE03JP01 | 415V SWGR O/G MODULE # 0SE03FJ | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
37 | 0SE | D07C1.5 | 10.5.08 | 0SE03QC01 | 415V SWGR MOTOR MODULE # 0SE03RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS03-L2, OS04-L2, OS05-L2, OS06-L1, OR02-02, ZZ99- |  | EPD | EPD
38 | 0SE | D03Q010 | 10.4.11 | 0SE03QP01 | 415V SWGR MOTOR MODULE # 0SE03RC | RE FAN FOR AREA B/W G-L-13A-3A, (EXCLUDING AREA B/W I-L-3A-6 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
39 | 0SE | D02Q010 | 10.4.06 | 0SE03RP01 | 415V SWGR O/G MODULE # 0SE03RD | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
40 | 0SE | D02Q010 | 10.4.06 | 0SE03SP01 | 415V SWGR O/G MODULE # 0SE03RE | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 57 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
41 | 0SE | D02Q010 | 10.4.06 | 0SE03TP01 | 415V SWGR O/G MODULE # 0SE03RF | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | PEM
42 | 0SE | D02Q010 | 10.4.06 | 0SE03UP01 | 415V SWGR O/G MODULE # 0SE03RG | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | PEM
43 | 0SE | D02Q010 | 10.4.06 | 0SE04DP01 | 415V SWGR O/G MODULE # 0SE04FD | AREA B/W A-B-1A-2, FIRST FLOOR SPLIT AC)-A (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
44 | 0SE | D02Q010 | 10.4.06 | 0SE04EP01 | 415V SWGR O/G MODULE # 0SE04FE | AREA B/W A-B-1A-2, FIRST FLOOR SPLIT AC)-C (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
45 | 0SE | D02Q010 | 10.4.06 | 0SE04FP01 | 415V SWGR O/G MODULE # 0SE04FF | AREA B/W B-C-1A-2, FIRST FLOOR SPLIT AC)-A (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
46 | 0SE | D02Q010 | 10.4.06 | 0SE04GP01 | 415V SWGR O/G MODULE # 0SE04FG | AREA B/W B-C-1A-2, FIRST FLOOR SPLIT AC)-C (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS03-L1, OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
47 | 0SE | D04Q010 | 10.4.22 | 0SE04HP01 | 415V SWGR O/G MODULE # 0SE04FH | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | OS03-L2, OS02-L2, OS01-L1, ZZ99- |  | EPD | PEM
48 | 0SE | D04Q010 | 10.4.22 | 0SE04IP01 | 415V SWGR O/G MODULE # 0SE04FI | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | OS03-L2, OS02-L2, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
49 | 0SE | D3HQ025 | 10.4.18 | 0SE04JP01 | 415V SWGR O/G MODULE # 0SE04FJ | PORTABLE SUMP PUMP A | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS03-L1, OS04-L1, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | PEM
50 | 0SE | D07C1.5 | 10.5.08 | 0SE04QC01 | 415V SWGR MOTOR MODULE # 0SE04RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 60 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS03-L2, OS04-L2, OS05-L2, OS06-L1, OR02-02, ZZ99- |  | EPD | EPD
51 | 0SE | D03Q010 | 10.4.11 | 0SE04QP01 | 415V SWGR MOTOR MODULE # 0SE04RC | RE FAN FOR AREA B/W G-L-13A-3A, (EXCLUDING AREA B/W I-L-3A-6 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 59 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS03-L1, OS04-L2, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
52 | 0SE | D07C1.5 | 10.5.08 | 0SE06VC01 | 415V SWGR MOTOR MODULE # 0SE06RH | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS04-L2, OS05-L2, OS06-L1, OR02-02, ZZ99- |  | EPD | EPD
53 | 0SE | D03Q010 | 10.4.11 | 0SE06VP01 | 415V SWGR MOTOR MODULE # 0SE06RH | RE FAN FOR AREA B/W G-L-13A-3A, (EXCLUDING AREA B/W I-L-3A-6 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 55 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS04-L2, OS05-L2, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
54 | 0SE | D02Q010 | 10.4.06 | 0SE07BP01 | 415V SWGR O/G MODULE # 0SE07FB | AREA PANEL-5 (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
55 | 0SE | D07C1.5 | 10.5.08 | 0SE07QC01 | 415V SWGR MOTOR MODULE # 0SE07RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 82 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS04-L2, OS05-L2, OS06-L1, OR02-02, ZZ99- |  | EPD | EPD
56 | 0SE | D03Q010 | 10.4.11 | 0SE07QP01 | 415V SWGR MOTOR MODULE # 0SE07RC | RE FAN FOR AREA B/W G-L-13A-3A, (EXCLUDING AREA B/W I-L-3A-6 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS04-L2, OS05-L2, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
57 | 0SE | D02Q010 | 10.4.06 | 0SE07RP01 | 415V SWGR O/G MODULE # 0SE07RD | AREA B/W B-C-1A-2, FIRST FLOOR SPLIT AC)-B (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 93 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L1, OS03-L1, OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
58 | 0SE | D02Q010 | 10.4.06 | 0SE07SP01 | 415V SWGR O/G MODULE # 0SE07RE | AREA B/W A-B-1A-2, FIRST FLOOR SPLIT AC)-B (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L1, OS03-L1, OS02-L1, OS01-L1, OR01-L1, IL52-L1, IL51-L1, IL50-L1, IL49-L1, ZZ99- |  | EPD | PEM
59 | 0SE | D04Q010 | 10.4.22 | 0SE07TP01 | 415V SWGR O/G MODULE # 0SE07RF | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 86 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
60 | 0SE | D04Q010 | 10.4.22 | 0SE08BP01 | 415V SWGR O/G MODULE # 0SE08FB | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 62 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
61 | 0SE | D02Q010 | 10.4.06 | 0SE08CP01 | 415V SWGR O/G MODULE # 0SE08FC | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L1, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | PEM
62 | 0SE | D02Q010 | 10.4.06 | 0SE08DP01 | 415V SWGR O/G MODULE # 0SE08FD | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 39 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
63 | 0SE | D02Q010 | 10.4.06 | 0SE08EP01 | 415V SWGR O/G MODULE # 0SE08FE | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 44 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
64 | 0SE | D03L2.5 | 10.4.26 | 0SE08FP01 | 415V SWGR O/G MODULE # 0SE08FF | EXHAUST FAN-HOT STORAGE, AREA B/W A-C-1A-1, FIRST FLOOR-A (0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
65 | 0SE | D03L2.5 | 10.4.26 | 0SE08GP01 | 415V SWGR O/G MODULE # 0SE08FG | EXHAUST FAN-COLD STORAGE, AREA B/W A-C-1A-1, FIRST FLOOR-A ( | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | POWER SUPPLY (0.37kW) | XLPE-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
66 | 0SE | D07C1.5 | 10.5.08 | 0SE08QC01 | 415V SWGR MOTOR MODULE # 0SE08RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 98 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
67 | 0SE | D03Q010 | 10.4.11 | 0SE08QP01 | 415V SWGR MOTOR MODULE # 0SE08RC | RE FAN FOR AREA B/W G-L-13A-3A, (EXCLUDING AREA B/W I-L-3A-6 | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 96 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS04-L2, OS03-L2, OS02-L1, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
68 | 0SE | D02Q010 | 10.4.06 | 0SE08RP01 | 415V SWGR O/G MODULE # 0SE08RD | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 54 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L1, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
69 | 0SE | D02Q010 | 10.4.06 | 0SE08SP01 | 415V SWGR O/G MODULE # 0SE08RE | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L2, OS05-L1, OS06-L1, OR02-01, ZZ99- |  | EPD | PEM
70 | 0SE | D02Q010 | 10.4.06 | 0SE08TP01 | 415V SWGR O/G MODULE # 0SE08RF | AREA B/W I-L-3A-5 SPLIT AC (ELECTRONIC EQUIPMENT/ INSTRUMENT | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | OS04-L2, OS05-L1, OS06-L1, OR02-01, OS07-01, ZZ99- |  | EPD | PEM
71 | 0SE | D3HQ025 | 10.4.18 | 0SE08WP01 | 415V SWGR O/G MODULE # 0SE08RI | PORTABLE SUMP PUMP B | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS04-L1, OS03-L1, OS02-L1, OS08-01, OS09-01, OS10-01, ZZ99- |  | EPD | PEM
72 | 0SE | D07C1.5 | 10.5.08 | 0SE09CC01 | 415V SWGR MOTOR MODULE # 0SE09FC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
73 | 0SE | D03Q010 | 10.4.11 | 0SE09CP01 | 415V SWGR MOTOR MODULE # 0SE09FC | RE FAN FOR AREA B/W A-K-13A-16, DOUBLE STOREY (HEAVY MATERIA | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 102 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS04-L2, OS03-L2, OS02-L1, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
74 | 0SE | D02Q010 | 10.4.06 | 0SE09DP01 | 415V SWGR O/G MODULE # 0SE09FD | AREA B/W C-D-7-9 SPLIT AC (OFFICE-GROUND FLOOR)-D (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
75 | 0SE | D02Q010 | 10.4.06 | 0SE09EP01 | 415V SWGR O/G MODULE # 0SE09FE | AREA B/W C-D-7-9 SPLIT AC (OFFICE-GROUND FLOOR)-B (3kW) | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
76 | 0SE | D02Q010 | 10.4.06 | 0SE09FP01 | 415V SWGR O/G MODULE # 0SE09FF | AREA B/W D-F-9-10 SPLIT AC (RECEIPT ROOM-2 GROUND FLOOR)-D ( | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
77 | 0SE | D03L2.5 | 10.4.26 | 0SE09GP01 | 415V SWGR O/G MODULE # 0SE09FG | EXHAUST FAN- AREA B/W A-G-1A-3 (EXCLUDING HOT & COLD STORAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
78 | 0SE | D3HQ025 | 10.4.18 | 0SE09IP01 | 415V SWGR O/G MODULE # 0SE09FI | WELDING SOCKET 2 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 59 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS04-L1, OS05-L1, OS06-L1, ZZ99- |  | EPD | PEM
79 | 0SE | D07C1.5 | 10.5.08 | 0SE09QC01 | 415V SWGR MOTOR MODULE # 0SE09RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
80 | 0SE | D03Q010 | 10.4.11 | 0SE09QP01 | 415V SWGR MOTOR MODULE # 0SE09RC | RE FAN FOR AREA B/W A-K-13A-16, DOUBLE STOREY (HEAVY MATERIA | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 112 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS04-L2, OS03-L2, OS02-L1, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
81 | 0SE | D02Q010 | 10.4.06 | 0SE09RP01 | 415V SWGR O/G MODULE # 0SE09RD | AREA B/W D-F-9-10 SPLIT AC (RECEIPT ROOM-2 GROUND FLOOR)-B ( | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 70 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
82 | 0SE | D02Q010 | 10.4.06 | 0SE09SP01 | 415V SWGR O/G MODULE # 0SE09RE | AREA B/W C-D-6-7 SPLIT AC (RECEIPT ROOM-1 GROUND FLOOR)-D (3 | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
83 | 0SE | D02Q010 | 10.4.06 | 0SE09TP01 | 415V SWGR O/G MODULE # 0SE09RF | AREA B/W C-D-6-7 SPLIT AC (RECEIPT ROOM-1 GROUND FLOOR)-B (3 | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
84 | 0SE | D03L2.5 | 10.4.26 | 0SE09UP01 | 415V SWGR O/G MODULE # 0SE09RG | EXHAUST FAN- AREA B/W A-G-1A-3 (EXCLUDING HOT & COLD STORAGE | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
85 | 0SE | D03L2.5 | 10.4.26 | 0SE09VP01 | 415V SWGR O/G MODULE # 0SE09RH | EXHAUST FAN- AREA B/W A-G-1A-3 GROUND FLOOR (GENERAL LIGHT M | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS04-L2, OS03-L2, OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
86 | 0SE | D3HQ025 | 10.4.18 | 0SE09WP01 | 415V SWGR O/G MODULE # 0SE09RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 96 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS04-L1, OS03-L1, OS02-L1, OS08-01, OS09-01, OS10-01, ZZ99- |  | EPD | EPD
87 | 0SE | D02Q010 | 10.4.06 | 0SE10CP01 | 415V SWGR O/G MODULE # 0SE10FC | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-K | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 65 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
88 | 0SE | D02Q010 | 10.4.06 | 0SE10DP01 | 415V SWGR O/G MODULE # 0SE10FD | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-H | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
89 | 0SE | D03L2.5 | 10.4.26 | 0SE10EP01 | 415V SWGR O/G MODULE # 0SE10FE | EXHAUST FAN- AREA B/W A-G-1A-3 GROUND FLOOR (GENERAL LIGHT M | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 92 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS05-L2, OS04-L2, OS03-L2, OS02-L2, OS01-L2, OR01-R1, IL52-R1, IL51-R1, IL50-R1, IL49-R1, ZZ99- |  | EPD | PEM
90 | 0SE | D03L2.5 | 10.4.26 | 0SE10FP01 | 415V SWGR O/G MODULE # 0SE10FF | EXHAUST FAN AREA B/W I-L-6-3A, FIRST FLOOR-C (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS05-L2, OS06-L1, OR02-02, OS07-01, ZZ99- |  | EPD | PEM
91 | 0SE | D3HQ025 | 10.4.18 | 0SE10GP01 | 415V SWGR O/G MODULE # 0SE10FG | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS05-L1, OS06-L1, ZZ99- |  | EPD | EPD
92 | 0SE | D07C1.5 | 10.5.08 | 0SE10PC01 | 415V SWGR MOTOR MODULE # 0SE10RB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | OS05-L2, OS04-L2, OS03-L2, OS02-L2, OS08-01, OS09-01, OS10-01, OR03-02, ZZ99- |  | EPD | EPD
93 | 0SE | D03Q010 | 10.4.11 | 0SE10PP01 | 415V SWGR MOTOR MODULE # 0SE10RB | RE FAN FOR AREA B/W A-K-13A-16, DOUBLE STOREY (HEAVY MATERIA | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 134 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | OS05-L2, OS04-L2, OS03-L2, OS02-L2, OS08-01, OS09-01, OS10-01, OR03-01, ZZ99- |  | EPD | PEM
94 | 0SE | D02Q010 | 10.4.06 | 0SE10QP01 | 415V SWGR O/G MODULE # 0SE10RC | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-F | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
95 | 0SE | D02Q010 | 10.4.06 | 0SE10RP01 | 415V SWGR O/G MODULE # 0SE10RD | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-D | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
96 | 0SE | D02Q010 | 10.4.06 | 0SE10SP01 | 415V SWGR O/G MODULE # 0SE10RE | AREA B/W D-E-6-10 SPLIT AC (INSPECTION ROOM GROUND FLOOR)-B | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
97 | 0SE | D03L2.5 | 10.4.26 | 0SE10TP01 | 415V SWGR O/G MODULE # 0SE10RF | EXHAUST FAN AREA B/W I-L-6-3A, FIRST FLOOR-A (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | OS05-L2, OS06-L1, OR02-02, OS07-01, ZZ99- |  | EPD | PEM
98 | 0SE | D03L2.5 | 10.4.26 | 0SE10UP01 | 415V SWGR O/G MODULE # 0SE10RG | SUPPY AIR FAN FOR SWITCHGEAR ROOM (GROUND FLOOR)-A (1.1kW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | SITE ROUTING |  | EPD | PEM
99 | 0SE | D3HQ050 | 10.4.19 | 0SE10VP01 | 415V SWGR O/G MODULE # 0SE10RH | HEAVY METERIAL STORE CRANE (5T) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | OS05-L1, OS04-L1, OS03-L1, OS02-L1, OS08-01, OS09-01, OS10-01, ZZ99- |  | EPD | PEM
1 | 0TA | D3HQ025 | 10.4.18 | 0TA01BP01 | 415V SWGR O/G MODULE # 0TA01FB | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
2 | 0TA | D02Q025 | 10.4.07 | 0TA01CP01 | 415V SWGR O/G MODULE # 0TA01FC | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 95 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, AC07-01, AC08-01, DR05-01, CC07-01, CC08-01, CC17-01, CC18-01, CC27-01, CC28-01, CC37-01, CC38-01, CC47-01, CC48-01, ZZ99- |  | EPD | PEM
3 | 0TA | D02Q025 | 10.4.07 | 0TA01DP01 | 415V SWGR O/G MODULE # 0TA01FD | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 109 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, AC07-01, AC08-01, DR05-01, CC07-01, CC08-01, CC17-01, CC18-01, CC27-01, CC28-01, CC37-01, CC38-01, CC47-01, CC48-01, CC49-01, CC50-01, ZZ99- |  | EPD | PEM
4 | 0TA | D04Q010 | 10.4.22 | 0TA01EP01 | 415V SWGR O/G MODULE # 0TA01FE | PAN HUMIDIFIER FOR AHU ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (8kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, CC90-01, CC80-01, CC32-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-01, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
5 | 0TA | D04Q010 | 10.4.22 | 0TA01FP01 | 415V SWGR O/G MODULE # 0TA01FF | STRIP HEATER FOR AHU ROOM OF CEP VFD ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 59 | [5 empty] | POWER SUPPLY (9kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, ZZ99- |  | EPD | PEM
6 | 0TA | D04Q010 | 10.4.22 | 0TA01GP01 | 415V SWGR O/G MODULE # 0TA01FG | AIR HANDLING UNIT (AHU 1) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, CC90-01, CC80-01, CC32-01, CC33-01, CC42-01, CC43-01, CC52-01, CC71-01, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
7 | 0TA | D02Q025 | 10.4.07 | 0TA01HP01 | 415V SWGR O/G MODULE # 0TA01FH | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 87 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, AC07-01, AC08-01, DR05-01, CC07-01, CC06-01, CC04-01, ZZ99- |  | EPD | PEM
8 | 0TA | D04Q010 | 10.4.22 | 0TA01IP01 | 415V SWGR O/G MODULE # 0TA01FI | AIR HANDLING UNIT (AHU 3) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 122 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, CC90-01, CC80-01, CC32-01, CC33-02, CC42-02, CC43-02, CC52-01, CC71-01, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
9 | 0TA | D3HQ025 | 10.4.18 | 0TA01PP01 | 415V SWGR O/G MODULE # 0TA01RB | SUMP PUMP | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
10 | 0TA | D04Q010 | 10.4.22 | 0TA01QP01 | 415V SWGR O/G MODULE # 0TA01RC | VAM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (8kVA) | XLPE-AL UNARMOURED | AC18-L1, AC19-L1, AC20-L1, AC21-01, AC22-01, AC29-01, AC31-01, AC32-01, ZZ99- |  | EPD | PEM
11 | 0TA | D02Q025 | 10.4.07 | 0TA01RP01 | 415V SWGR O/G MODULE # 0TA01RD | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, AC07-01, AC08-01, DR05-01, CC07-01, CC08-01, CC09-01, CC10-01, CC11-01, CC74-01, CC75-01, ZZ99- |  | EPD | PEM
12 | 0TA | D02C1.5 | 10.5.01 | 0TA01SC01 | 415V SWGR MOTOR MODULE # 0TA01RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 41 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, ZZ99- |  | EPD | EPD
13 | 0TA | D03L2.5 | 10.4.26 | 0TA01SP01 | 415V SWGR MOTOR MODULE # 0TA01RE | DE-SUPERHEATING PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 41 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, ZZ99- |  | EPD | PEM
14 | 0TA | D04Q010 | 10.4.22 | 0TA01TP01 | 415V SWGR O/G MODULE # 0TA01RF | FEEDER FOR CONTROL PANEL | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-02, DC10-02, DC09-02, DC08-02, DC07-03, LR07-01, ZZ99- |  | EPD | PEM
15 | 0TA | D02Q025 | 10.4.07 | 0TA01UP01 | 415V SWGR O/G MODULE # 0TA01RG | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 110 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, AC07-01, AC08-01, DR05-01, CC07-01, CC08-01, CC17-01, CC18-01, CC27-01, CC28-01, CC37-01, CC36-01, CC35-01, CC34-01, CC93-01, CC84-01, CC86-02, ZZ99- |  | EPD | PEM
16 | 0TA | D3HQ025 | 10.4.18 | 0TA01VP01 | 415V SWGR O/G MODULE # 0TA01RH | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
17 | 0TA | D3HQ025 | 10.4.18 | 0TA01WP01 | 415V SWGR O/G MODULE # 0TA01RI | PACKAGED AIR CONDITIONER OF CEP VFD ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 32 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, ZZ99- |  | EPD | PEM
18 | 0TA | D3HQ025 | 10.4.18 | 0TA02CP01 | 415V SWGR O/G MODULE # 0TA02FC | WELDING SOCKET | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
19 | 0TA | D02C1.5 | 10.5.01 | 0TA02DC01 | 415V SWGR MOTOR MODULE # 0TA02FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-03, CC90-03, CC80-02, CC32-03, CC33-03, CC42-03, CC43-03, CC52-02, CC71-02, QR03-L3, BQ20-L3, BQ19-L3, BQ07-R2, BQ26-L2, BQ14-02, BQ21-02, BQ17-02, ZZ99- |  | EPD | EPD
20 | 0TA | D03Q010 | 10.4.11 | 0TA02DP01 | 415V SWGR MOTOR MODULE # 0TA02FD | COOLING TOWER | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 133 | 65 | 03.03.20 | 0 |  |  | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, CC90-01, CC80-01, CC32-01, CC33-02, CC42-02, CC85-01, CC86-02, CC88-01, CC89-02, CC71-01, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ14-02, BQ21-02, BQ17-02, ZZ99- |  | EPD | PEM
21 | 0TA | D3HQ025 | 10.4.18 | 0TA02EP01 | 415V SWGR O/G MODULE # 0TA02FE | AC FUSE DB FOR FIRE DAMPER | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
22 | 0TA | D3HQ025 | 10.4.18 | 0TA02NP01 | 415V SWGR O/G MODULE # 0TA02RA | STRIP HEATER FOR AHU ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (24kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, CC90-01, CC80-01, CC32-01, CC33-01, CC42-01, CC43-01, CC52-02, CC71-01, QR03-L1, BQ20-L1, BQ19-L1, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
23 | 0TA | D3HQ025 | 10.4.18 | 0TA02PP01 | 415V SWGR O/G MODULE # 0TA02RB | PACKAGED AIR CONDITIONER OF CEP VFD ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-02, AC04-02, AC01-02, DR03-02, ZZ99- |  | EPD | PEM
24 | 0TA | D3HQ025 | 10.4.18 | 0TA02RP01 | 415V SWGR O/G MODULE # 0TA02RD | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
25 | 0TA | D3HQ025 | 10.4.18 | 0TA03BP01 | 415V SWGR O/G MODULE # 0TA03FB | AC FUSE DB FOR FIRE DAMPER OF CEP VFD ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-02, AC04-02, AC01-03, ZZ99- |  | EPD | EPD
26 | 0TA | D02C1.5 | 10.5.01 | 0TA03CC01 | 415V SWGR MOTOR MODULE # 0TA03FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 124 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-03, CC90-03, CC80-02, CC32-03, CC33-03, CC42-03, CC85-02, CC86-03, CC88-03, CC89-02, CC71-05, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | EPD
27 | 0TA | D03L2.5 | 10.4.26 | 0TA03CP01 | 415V SWGR MOTOR MODULE # 0TA03FC | PUMP FOR WATER SOFTENING PLANT | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 124 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | AC18-L4, AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-03, CC90-03, CC80-02, CC32-03, CC33-03, CC42-03, CC85-02, CC86-03, CC88-03, CC89-02, CC71-02, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | PEM
28 | 0TA | D3HQ025 | 10.4.18 | 0TA03DP01 | 415V SWGR O/G MODULE # 0TA03FD | HOIST FOR AC PLANT ROOM (5T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (32A) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, ZZ99- |  | EPD | PEM
29 | 0TA | D3HQ025 | 10.4.18 | 0TA03EP01 | 415V SWGR O/G MODULE # 0TA03FE | AC FUSE DB FOR FIRE DAMPER | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
30 | 0TA | D02C1.5 | 10.5.01 | 0TA03FC01 | 415V SWGR MOTOR MODULE # 0TA03FF | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 31 | 24 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC19-L4, AC20-L3, AC21-02, ZZ99- |  | EPD | EPD
31 | 0TA | D03Q025 | 10.4.12 | 0TA03FP01 | 415V SWGR MOTOR MODULE # 0TA03FF | CONDENSER WATER PUMP | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 28 | 41 | 01.03.20 | DR0819_0001 |  |  | POWER SUPPLY (22kW) | XLPE-AL UNARMOURED | AC18-L1, AC19-L1, AC20-L1, AC21-01, ZZ99- |  | EPD | PEM
32 | 0TA | D02C1.5 | 10.5.01 | 0TA03GC01 | 415V SWGR MOTOR MODULE # 0TA03FG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 124 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-03, CC90-03, CC80-02, CC32-03, CC33-03, CC42-03, CC85-02, CC86-03, CC88-03, CC89-02, CC71-05, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | EPD
33 | 0TA | D03L2.5 | 10.4.26 | 0TA03GP01 | 415V SWGR MOTOR MODULE # 0TA03FG | PUMP FOR WATER SOFTENING PLANT | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 124 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | AC18-L4, AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-03, CC90-03, CC80-02, CC32-03, CC33-03, CC42-03, CC85-02, CC86-03, CC88-03, CC89-02, CC71-02, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | PEM
34 | 0TA | D3HQ025 | 10.4.18 | 0TA03NP01 | 415V SWGR O/G MODULE # 0TA03RA | STRIP HEATER FOR AHU ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 129 | [5 empty] | POWER SUPPLY (24kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L2, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, CC90-01, CC80-01, CC32-01, CC33-02, CC42-02, CC85-01, CC86-02, CC88-01, CC89-01, CC71-01, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
35 | 0TA | D02C1.5 | 10.5.01 | 0TA03PC01 | 415V SWGR MOTOR MODULE # 0TA03RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 37 | 24 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC19-L4, AC20-L3, AC21-02, AC22-02, ZZ99- |  | EPD | EPD
36 | 0TA | D03Q025 | 10.4.12 | 0TA03PP01 | 415V SWGR MOTOR MODULE # 0TA03RB | CHILLED WATER PUMP | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 34 | 41 | 01.03.20 | DR0819_0001 |  |  | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | AC18-L1, AC19-L1, AC20-L1, AC21-01, AC22-01, ZZ99- |  | EPD | PEM
37 | 0TA | D02C1.5 | 10.5.01 | 0TA03QC01 | 415V SWGR MOTOR MODULE # 0TA03RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 48 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, AC27-02, AC28-02, ZZ99- |  | EPD | EPD
38 | 0TA | D03L2.5 | 10.4.26 | 0TA03QP01 | 415V SWGR MOTOR MODULE # 0TA03RC | CONDENSATE TRANSFER PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, AC27-02, AC28-02, ZZ99- |  | EPD | PEM
39 | 0TA | D02C1.5 | 10.5.01 | 0TA03RC01 | 415V SWGR MOTOR MODULE # 0TA03RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC18-L4, AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-R3, LV37-R3, LV36-R3, LV35-R3, LV34-R3, LV33-R3, LV65-02, LR09-02, ZZ99- |  | EPD | EPD
40 | 0TA | D03L2.5 | 10.4.26 | 0TA03RP01 | 415V SWGR MOTOR MODULE # 0TA03RD | FRESH AIR FAN FOR AHU ROOM OF CEP VFD ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AC18-L4, AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-R3, LV37-R3, LV36-R3, LV35-R3, LV34-R3, LV33-R3, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
41 | 0TA | D04Q010 | 10.4.22 | 0TA03TP01 | 415V SWGR O/G MODULE # 0TA03RF | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
42 | 0TA | E04V0.5 | 10.7.02 | 0TA04AC01 | 415V SWGR I/C MODULE # 0TA04FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | AC17-R4, AC16-R4, AC15-R4, AC14-R4, DR07-04, AC13-04, AC09-04, AC05-03, AC06-03, AC07-03, AC08-03, DR05-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03, ZZ99- |  | EPD | EDN
43 | 0TA | D02C1.5 | 10.5.01 | 0TA04AC02 | 415V SWGR I/C MODULE # 0TA04FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 90 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, MR08-03, MA07-03, MV45-L2, MV46-L2, MV47-02, MV48-02, MV49-02 |  | EPD | EPD
44 | 0TA | E04V0.5 | 10.7.02 | 0TA04AC03 | 415V SWGR I/C MODULE # 0TA04FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | AC17-R4, AC16-R4, AC15-R4, AC14-R4, DR07-04, AC13-04, AC09-04, AC05-03, AC06-03, AC07-03, AC08-03, DR05-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03, ZZ99- |  | EPD | EDN
45 | 0TA | E04V0.5 | 10.7.02 | 0TA05AC01 | 415V SWGR B/C MODULE # 0TA05FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | AC17-R4, AC16-R4, AC15-R4, AC14-R4, DR07-04, AC13-04, AC09-04, AC05-03, AC06-03, AC07-03, AC08-03, DR05-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03, ZZ99- |  | EPD | EDN
46 | 0TA | E04V0.5 | 10.7.02 | 0TA05AC02 | 415V SWGR B/C MODULE # 0TA05FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | AC17-R4, AC16-R4, AC15-R4, AC14-R4, DR07-04, AC13-04, AC09-04, AC05-03, AC06-03, AC07-03, AC08-03, DR05-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03, ZZ99- |  | EPD | EDN
47 | 0TA | E04V0.5 | 10.7.02 | 0TA06AC01 | 415V SWGR I/C MODULE # 0TA06FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | AC17-R4, AC16-R4, AC15-R4, AC14-R4, DR07-04, AC13-04, AC09-04, AC05-03, AC06-03, AC07-03, AC08-03, DR05-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03, ZZ99- |  | EPD | EDN
48 | 0TA | D02C1.5 | 10.5.01 | 0TA06AC02 | 415V SWGR I/C MODULE # 0TA06FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | AC17-L4, AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, MR08-03, MA07-03, MV45-L2, MV46-L2, MV47-02, MV48-02, MV49-02, MV50-02, MV51-02 |  | EPD | EPD
49 | 0TA | E04V0.5 | 10.7.02 | 0TA06AC03 | 415V SWGR I/C MODULE # 0TA06FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | AC17-R4, AC16-R4, AC15-R4, AC14-R4, DR07-04, AC13-04, AC09-04, AC05-03, AC06-03, AC07-03, AC08-03, DR05-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03, ZZ99- |  | EPD | EDN
50 | 0TA | D3HQ025 | 10.4.18 | 0TA07AP01 | 415V SWGR O/G MODULE # 0TA07FA | STRIP HEATER FOR AHU ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 123 | [5 empty] | POWER SUPPLY (24kW) | XLPE-AL UNARMOURED | AC16-L2, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, CC90-01, CC80-01, CC32-01, CC33-02, CC42-02, CC85-01, CC86-02, CC88-01, CC89-02, CC71-01, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
51 | 0TA | D02Q025 | 10.4.07 | 0TA07BP01 | 415V SWGR O/G MODULE # 0TA07FB | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 79 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, AC07-01, AC08-01, DR05-01, CC07-01, CC08-01, CC09-01, ZZ99- |  | EPD | PEM
52 | 0TA | D3HQ025 | 10.4.18 | 0TA07CP01 | 415V SWGR O/G MODULE # 0TA07FC | AC FUSE DB FOR FIRE DAMPER OF CEP VFD ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 48 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-02, AC04-02, AC01-03, ZZ99- |  | EPD | EPD
53 | 0TA | D3HQ025 | 10.4.18 | 0TA07DP01 | 415V SWGR O/G MODULE # 0TA07FD | PACKAGED AIR CONDITIONER OF CEP VFD ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, AC07-01, ZZ99- |  | EPD | PEM
54 | 0TA | D02C1.5 | 10.5.01 | 0TA07EC01 | 415V SWGR MOTOR MODULE # 0TA07FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 52 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC17-L4, AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, AC27-02, AC28-02, ZZ99- |  | EPD | EPD
55 | 0TA | D03L2.5 | 10.4.26 | 0TA07EP01 | 415V SWGR MOTOR MODULE # 0TA07FE | CONDENSATE TRANSFER PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 52 | [5 empty] | POWER SUPPLY (0.75kW) | XLPE-CU UNARMOURED | AC16-L4, AC17-L4, AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, AC27-02, AC28-02, ZZ99- |  | EPD | PEM
56 | 0TA | D02Q025 | 10.4.07 | 0TA07FP01 | 415V SWGR O/G MODULE # 0TA07FF | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
57 | 0TA | D3HQ025 | 10.4.18 | 0TA07GP01 | 415V SWGR O/G MODULE # 0TA07FG | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
58 | 0TA | D04Q010 | 10.4.22 | 0TA07QP01 | 415V SWGR O/G MODULE # 0TA07RC | PAN HUMIDIFIER FOR AHU ROOM OF CEP VFD ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 55 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC05-01, AC06-01, ZZ99- |  | EPD | PEM
59 | 0TA | D02Q025 | 10.4.07 | 0TA07RP01 | 415V SWGR O/G MODULE # 0TA07RD | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
60 | 0TA | D02Q025 | 10.4.07 | 0TA07SP01 | 415V SWGR O/G MODULE # 0TA07RE | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
61 | 0TA | D02Q025 | 10.4.07 | 0TA07TP01 | 415V SWGR O/G MODULE # 0TA07RF | SPLIT AC FOR POWER HOUSE | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | 0 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | Hold |  | EPD | PEM
62 | 0TA | D02C1.5 | 10.5.01 | 0TA07UC01 | 415V SWGR MOTOR MODULE # 0TA07RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 134 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-03, CC90-03, CC80-02, CC32-03, CC33-03, CC42-02, CC85-02, CC86-03, CC88-03, CC89-02, CC71-05, QR03-L3, BQ20-L3, BQ19-L3, BQ07-R2, BQ26-L2, BQ15-R2, BQ27-02, ZZ99- |  | EPD | EPD
63 | 0TA | D03L2.5 | 10.4.26 | 0TA07UP01 | 415V SWGR MOTOR MODULE # 0TA07RG | FRESH AIR FAN FOR AHU ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV76-03, LV79-03, LR10-R3, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ07-R2, BQ26-L2, BQ15-R2, BQ27-02, ZZ99- |  | EPD | PEM
64 | 0TA | D02C1.5 | 10.5.01 | 0TA07VC01 | 415V SWGR MOTOR MODULE # 0TA07RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV76-03, LV79-03, LR10-R3, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | EPD
65 | 0TA | D03L2.5 | 10.4.26 | 0TA07VP01 | 415V SWGR MOTOR MODULE # 0TA07RH | PUMP FOR WATER SOFTENING PLANT | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV76-03, LV79-03, LR10-R3, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | PEM
66 | 0TA | D04Q010 | 10.4.22 | 0TA07WP01 | 415V SWGR O/G MODULE # 0TA07RI | FEEDER FOR CONTROL PANEL | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC18-L1, AC17-L1, AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, ZZ99- |  | EPD | PEM
67 | 0TA | D02C1.5 | 10.5.01 | 0TA08BC01 | 415V SWGR MOTOR MODULE # 0TA08FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 39 | 28 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC17-L4, AC18-L4, AC19-L4, AC20-L3, AC21-02, AC22-02, ZZ99- |  | EPD | EPD
68 | 0TA | D03Q025 | 10.4.12 | 0TA08BP01 | 415V SWGR MOTOR MODULE # 0TA08FB | CHILLED WATER PUMP | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 38 | 44 | 01.03.20 | DR0819_0001 |  |  | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | AC16-L2, AC17-L1, AC18-L1, AC19-L1, AC20-L1, AC21-01, AC22-01, ZZ99- |  | EPD | PEM
69 | 0TA | D3HQ025 | 10.4.18 | 0TA08DP01 | 415V SWGR O/G MODULE # 0TA08FD | AC FUSE DB FOR FIRE DAMPER | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
70 | 0TA | D02C1.5 | 10.5.01 | 0TA08RC01 | 415V SWGR MOTOR MODULE # 0TA08RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC17-L4, AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, ZZ99- |  | EPD | EPD
71 | 0TA | D03L2.5 | 10.4.26 | 0TA08RP01 | 415V SWGR MOTOR MODULE # 0TA08RD | DE-SUPERHEATING PUMP | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 45 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | AC16-L4, AC17-L4, AC18-L4, AC19-L4, AC20-L3, AC23-02, AC24-02, AC25-02, AC26-02, ZZ99- |  | EPD | PEM
72 | 0TA | D3HQ025 | 10.4.18 | 0TA08SP01 | 415V SWGR O/G MODULE # 0TA08RE | AC FUSE DB FOR FIRE DAMPER | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
73 | 0TA | D3HQ025 | 10.4.18 | 0TA08TP01 | 415V SWGR O/G MODULE # 0TA08RF | SUMP PUMP | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
74 | 0TA | D3HQ025 | 10.4.18 | 0TA08UP01 | 415V SWGR O/G MODULE # 0TA08RG | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
75 | 0TA | D3HQ185 | 10.4.21 | 0TA09BP01 | 415V SWGR O/G MODULE # 0TA09FB | SCREW CHILLER | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 38 | 45 | 04.03.20 | DR2687-1 |  |  | POWER SUPPLY (130kW) | XLPE-AL UNARMOURED | AC16-L1, AC17-L1, AC18-L1, AC19-L1, AC20-L1, AC21-01, AC22-01, AC29-01, AC30-01, ZZ99- |  | EPD | PEM
76 | 0TA | D02C1.5 | 10.5.01 | 0TA09CC01 | 415V SWGR MOTOR MODULE # 0TA09FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV76-03, LV79-03, LR10-R3, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | EPD
77 | 0TA | D03L2.5 | 10.4.26 | 0TA09CP01 | 415V SWGR MOTOR MODULE # 0TA09FC | PUMP FOR WATER SOFTENING PLANT | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV76-03, LV79-03, LR10-R3, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ25-02, ZZ99- |  | EPD | PEM
78 | 0TA | D04Q010 | 10.4.22 | 0TA09DP01 | 415V SWGR O/G MODULE # 0TA09FD | PAN HUMIDIFIER FOR AHU ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 135 | [5 empty] | POWER SUPPLY (8kW) | XLPE-AL UNARMOURED | AC16-R1, AC15-R1, AC14-R1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-02, LV25-L1, LV24-L2, LV43-02, LV09-L1, LV08-L1, LV76-01, LV79-02, LR10-R2, CR01-L1, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
79 | 0TA | D04Q010 | 10.4.22 | 0TA09EP01 | 415V SWGR O/G MODULE # 0TA09FE | ROLLING SHUTTER | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (16A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
80 | 0TA | D04Q010 | 10.4.22 | 0TA09FP01 | 415V SWGR O/G MODULE # 0TA09FF | PAN HUMIDIFIER FOR AHU ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 136 | [5 empty] | POWER SUPPLY (8kW) | XLPE-AL UNARMOURED | AC16-L2, AC15-L1, AC14-L1, DR07-02, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L1, LV24-L2, LV43-02, LV09-L1, LV08-L1, LV76-01, LV79-02, LR10-R2, CR01-L1, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
81 | 0TA | D3HQ025 | 10.4.18 | 0TA09GP01 | 415V SWGR O/G MODULE # 0TA09FG | WELDING SOCKET | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | PEM
82 | 0TA | D02C1.5 | 10.5.01 | 0TA09HC01 | 415V SWGR MOTOR MODULE # 0TA09FH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 39 | 28 | 07.12.19 | DR1150_17PA011685 |  |  | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC17-L4, AC18-L4, AC19-L4, AC20-L3, AC21-02, AC22-02, ZZ99- |  | EPD | EPD
83 | 0TA | D03Q025 | 10.4.12 | 0TA09HP01 | 415V SWGR MOTOR MODULE # 0TA09FH | CONDENSER WATER PUMP | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 36 | 44 | 01.03.20 | DR0819_0001 |  |  | POWER SUPPLY (22kW) | XLPE-AL UNARMOURED | AC16-L1, AC17-L1, AC18-L1, AC19-L1, AC20-L1, AC21-01, AC22-01, ZZ99- |  | EPD | PEM
84 | 0TA | D02C1.5 | 10.5.01 | 0TA09QC01 | 415V SWGR MOTOR MODULE # 0TA09RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-R3, LV37-R3, LV36-R3, LV35-R3, LV34-R3, LV33-R3, LV65-02, LR09-02, ZZ99- |  | EPD | EPD
85 | 0TA | D03L2.5 | 10.4.26 | 0TA09QP01 | 415V SWGR MOTOR MODULE # 0TA09RC | FRESH AIR FAN FOR AHU ROOM OF CEP VFD ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-R3, LV37-R3, LV36-R3, LV35-R3, LV34-R3, LV33-R3, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
86 | 0TA | D04Q010 | 10.4.22 | 0TA09RP01 | 415V SWGR O/G MODULE # 0TA09RD | AIR HANDLING UNIT (AHU 2) | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (15kW) | XLPE-AL UNARMOURED | AC16-L2, AC15-L2, AC14-L2, DR07-02, AC13-02, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L1, LV24-L2, LV43-02, LV09-L1, LV08-L1, LV76-01, LV79-02, LR10-R2, CR01-L1, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ15-L2, BQ27-01, ZZ99- |  | EPD | PEM
87 | 0TA | D02C1.5 | 10.5.01 | 0TA09SC01 | 415V SWGR MOTOR MODULE # 0TA09RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | AC16-L4, AC15-L4, AC14-L4, DR07-03, AC13-03, AC09-03, AC04-03, AC01-03, DR03-03, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV76-03, LV79-03, LR10-R3, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ07-R2, BQ26-L2, BQ14-02, BQ21-02, BQ17-02, ZZ99- |  | EPD | EPD
88 | 0TA | D03Q010 | 10.4.11 | 0TA09SP01 | 415V SWGR MOTOR MODULE # 0TA09RE | COOLING TOWER | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 138 | 87 | 03.03.20 | 0 |  |  | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | AC16-L2, AC15-L2, AC14-L2, DR07-02, AC13-02, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LV74-03, LV25-L1, LV24-L2, LV43-02, LV09-L1, LV08-L1, LV76-01, LV79-02, LR10-R2, CR01-L1, QR03-L2, BQ20-L2, BQ19-L2, BQ07-L2, BQ26-R2, BQ14-02, BQ21-02, BQ17-02, ZZ99- |  | EPD | PEM
89 | 0TA | D3HQ025 | 10.4.18 | 0TA09TP01 | 415V SWGR O/G MODULE # 0TA09RF | PACKAGED AIR CONDITIONER OF CEP VFD ROOM | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY (30kW) | XLPE-AL UNARMOURED | AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, DR06-02, ZZ99- |  | EPD | PEM
90 | 0TA | D3HQ025 | 10.4.18 | 0TA09UP01 | 415V SWGR O/G MODULE # 0TA09RG | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
91 | 0TA | D04Q010 | 10.4.22 | 0TA09VP01 | 415V SWGR O/G MODULE # 0TA09RH | FEEDER FOR CONTROL PANEL | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (3kW) | XLPE-AL UNARMOURED | AC16-L1, AC15-L1, AC14-L1, DR07-01, AC13-01, AC09-03, AC04-03, AC01-03, DR03-02, DC11-03, DC10-03, DC09-03, DC08-03, DC07-03, LR07-01, ZZ99- |  | EPD | PEM
| 0TA | E04V0.5 | 10.7.02 | 0TA7FE-LTUD-001 | 0TA-7FE | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 17 | 78 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA3RC-LTUD-002 | 0TA-3RC | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 80 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA1RC-LTUD-003 | 0TA-1RC | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 82 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA8RD-LTUD-004 | 0TA-8RD | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 76 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA3FE-LTUD-005 | 0TA-3FE | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 80 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA9FH-LTUD-006 | 0TA-9FH | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 75 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA8FB-LTUD-007 | 0TA-8FB | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 75 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA3RB-LTUD-008 | 0TA-3RB | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 80 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA2RD-LTUD-009 | 0TA-2RD | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 82 | 25.10.2019 | DR0720_4798-4G-21
| 0TA | E04V0.5 | 10.7.02 | 0TA9RE-LTUD-010 | 0TA-9RE | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 76 | 25.10.2019 | DR0817_4798-4G-16
| 0TA | E04V0.5 | 10.7.02 | 0TA3FG-LTUD-011 | 0TA-3FG | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 80 | 25.10.2019 | DR0817_4798-4G-16
| 0TA | E04V0.5 | 10.7.02 | 0TA3FC-LTUD-012 | 0TA-3FC | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 80 | 25.10.2019 | DR0817_4798-4G-16
| 0TA | E04V0.5 | 10.7.02 | 0TA7RA-LTUD-001 | 0TA-7RA | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 77 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA3RA-LTUD-002 | 0TA-3RA | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 81 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA2RA-LTUD-003 | 0TA-2RA | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 82 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA1FE-LTUD-004 | 0TA-1FE | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 83 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA7RG-LTUD-005 | 0TA-7RG | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 78 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA1FE-LTUD-006 | 0TA-1FE | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 83 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA7RC-LTUD-007 | 0TA-7RC | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 78 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA3RD-LTUD-008 | 0TA-3RD | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 80 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA9FE-LTUD-009 | 0TA-9FE | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 76 | 25.10.2019 | DR0817_4798-4G-76
| 0TA | E04V0.5 | 10.7.02 | 0TA9FD-LTUD-010 | 0TA-9FD | CVP-62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 75 | 75 | 25.10.2019 | DR0720_4798-4G-20
1 | 1TA | D02C1.5 | 10.5.01 | 1TA01BC01 | 415V SWGR MOTOR MODULE # 1TA01FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 122 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, ZZ99- |  | EPD | EPD
2 | 1TA | D03Q025 | 10.4.12 | 1TA01BP01 | 415V SWGR MOTOR MODULE # 1TA01FB | CENTRIFUGAL PUMP FOR AWU-1 (AW ROOM 8m LVL) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-03, LV75-02, LV24-R1, LV42-01, LV41-02, LV38-L3, LV37-L2, LV36-L2, LV35-L2, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | PEM
3 | 1TA | D03L2.5 | 10.4.26 | 1TA01CP01 | 415V SWGR O/G MODULE # 1TA01FC | EXHAUST AIR FAN FOR CENTRAL LUBE OIL PURIFICATION ROOM (AT 0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
4 | 1TA | D3HQ025 | 10.4.18 | 1TA01DP01 | 415V SWGR O/G MODULE # 1TA01FD | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
5 | 1TA | D02C1.5 | 10.5.01 | 1TA01EC01 | 415V SWGR MOTOR MODULE # 1TA01FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, ZZ99- |  | EPD | EPD
6 | 1TA | D02L2.5 | 10.4.24 | 1TA01EC02 | 415V SWGR MOTOR MODULE # 1TA01FE | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, ZZ99- |  | EPD | PEM
7 | 1TA | D03Q095 | 10.4.15 | 1TA01EP01 | 415V SWGR MOTOR MODULE # 1TA01FE | CENTRIFUGAL FAN FOR AWU-1 (AW ROOM 8m LVL) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-L1, BQ07-R1, BQ19-L2, BQ20-L2, QR03-L2, CC71-02, CC52-01, CC43-01, CC42-01, CC33-01, CC81-01, CC90-01, LR07-01, LV74-02, LV26-R1, LV27-R1, LV41-02, LV38-L3, LV37-L2, LV36-L2, LV35-L1, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | PEM
8 | 1TA | D03L2.5 | 10.4.26 | 1TA01PP01 | 415V SWGR O/G MODULE # 1TA01RB | EXHAUST AIR FAN FOR CENTRAL LUBE OIL PURIFICATION ROOM (AT 0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
9 | 1TA | D03L2.5 | 10.4.26 | 1TA01QP01 | 415V SWGR O/G MODULE # 1TA01RC | EXHAUST AIR FAN FOR CENTRAL LUBE OIL PURIFICATION ROOM (AT 0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
10 | 1TA | D07C1.5 | 10.5.08 | 1TA01TC01 | 415V SWGR MOTOR MODULE # 1TA01RF | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 222 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TR36-02, ZZ99- |  | EPD | EPD
11 | 1TA | D03Q010 | 10.4.11 | 1TA01TP01 | 415V SWGR MOTOR MODULE # 1TA01RF | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 221 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-02, LV24-L2, LV43-02, LV10-R1, LV11-R3, LV12-R2, LV58-02, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP27-01, TP28-01, TP29-01, TP30-01, TP31-01, TP32-01, TP34-01, TR36-01, ZZ99- |  | EPD | PEM
12 | 1TA | D3HQ025 | 10.4.18 | 1TA01UP01 | 415V SWGR O/G MODULE # 1TA01RG | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
13 | 1TA | D03L2.5 | 10.4.26 | 1TA01VP01 | 415V SWGR O/G MODULE # 1TA01RH | SUPPLY AIR FAN FOR MCC ROOM (AT 0m E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 134 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC34-02, CC67-03, CC66-03, CC65-03, CC64-03, CC63-03, CC62-03, CC04-03, CC06-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, AC13-03, DR07-03, AC14-L4, ZZ99- |  | EPD | PEM
14 | 1TA | D07C1.5 | 10.5.08 | 1TA02BC01 | 415V SWGR MOTOR MODULE # 1TA02FB | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 156 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, ZZ99- |  | EPD | EPD
15 | 1TA | D03Q010 | 10.4.11 | 1TA02BP01 | 415V SWGR MOTOR MODULE # 1TA02FB | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 159 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-01, LV24-L2, LV43-02, LV10-R1, LV11-R3, LV12-R2, LV58-02, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, ZZ99- |  | EPD | PEM
16 | 1TA | D3HQ025 | 10.4.18 | 1TA02CP01 | 415V SWGR O/G MODULE # 1TA02FC | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 8m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-01, CC88-01, CC86-02, CC84-01, CC83-01, CC82-01, CC81-01, CC90-01, LR07-01, LV74-02, LV26-R1, LV27-R1, LV41-02, LV38-L3, LV37-L2, LV36-L2, LV35-L2, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | EPD
17 | 1TA | D3HQ025 | 10.4.18 | 1TA02DP01 | 415V SWGR O/G MODULE # 1TA02FD | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 8m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 128 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-01, CC88-01, CC86-02, CC84-01, CC83-01, CC82-01, CC81-01, CC90-01, LR07-01, LV74-02, LV26-R1, LV27-R1, LV41-02, LV38-L3, LV37-L2, LV36-L2, LV35-L2, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | EPD
18 | 1TA | D02C1.5 | 10.5.01 | 1TA02EC01 | 415V SWGR MOTOR MODULE # 1TA02FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 221 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, TD60-02, TD61-02, TD62-02, TD63-02, TD64-02, TD65-02, TD66-02, TD67-02, ZZ99- |  | EPD | EPD
19 | 1TA | D02L2.5 | 10.4.24 | 1TA02EC02 | 415V SWGR MOTOR MODULE # 1TA02FE | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 221 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, TD60-02, TD61-02, TD62-02, TD63-02, TD64-02, TD65-02, TD66-02, TD67-02, ZZ99- |  | EPD | PEM
20 | 1TA | D03Q150 | 10.4.16 | 1TA02EP01 | 415V SWGR MOTOR MODULE # 1TA02FE | CENTRIFUGAL FAN FOR AWU-3 (AW ROOM 21m LVL) | 03C X 150 XLPE-Al FRLS ( 1.1 kV ) | 239 | [5 empty] | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-L1, BQ07-R1, BQ19-L2, BQ20-L2, QR03-L2, CC71-03, CC52-01, CC43-01, CC42-01, CC33-01, CC81-01, CC90-01, LR07-01, LV74-02, LV25-L1, LV24-L2, LV43-02, LV10-L1, LV49-02, LV06-R1, LV05-R1, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP04-01, TR26-01, TR40-01, TD18-01, TR47-01, TD51-01, TD50-01, TD47-01, TD45-01, TD43-01, TR46-01, TD41-01, TD59-01, TD60-01, TD61-01, TD62-01, TD63-01, TD64-01, TD65-01, TD66-01, TD67-01, ZZ99- |  | EPD | PEM
21 | 1TA | D02C1.5 | 10.5.01 | 1TA02PC01 | 415V SWGR MOTOR MODULE # 1TA02RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 116 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, ZZ99- |  | EPD | EPD
22 | 1TA | D03Q025 | 10.4.12 | 1TA02PP01 | 415V SWGR MOTOR MODULE # 1TA02RB | CENTRIFUGAL PUMP FOR AWU-2 (AW ROOM 8m LVL) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-03, LV75-02, LV24-R1, LV42-01, LV41-02, LV38-L3, LV37-L2, LV36-L2, LV35-L2, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | PEM
23 | 1TA | D03L2.5 | 10.4.26 | 1TA02QP01 | 415V SWGR O/G MODULE # 1TA02RC | SUPPLY AIR FAN FOR MCC ROOM (AT 0m E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC34-02, CC67-03, CC66-03, CC65-03, CC64-03, CC63-03, CC62-03, CC04-03, CC06-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, AC13-03, DR07-03, AC14-L4, AC15-L4, AC16-L4, AC17-L4, AC18-L4, ZZ99- |  | EPD | PEM
24 | 1TA | D02C1.5 | 10.5.01 | 1TA02RC01 | 415V SWGR MOTOR MODULE # 1TA02RD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 219 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, TD60-02, TD61-02, TD62-02, TD63-02, TD64-02, TD65-02, TD66-02, ZZ99- |  | EPD | EPD
25 | 1TA | D03Q050 | 10.4.14 | 1TA02RP01 | 415V SWGR MOTOR MODULE # 1TA02RD | CENTRIFUGAL PUMP FOR AWU-3 (AW ROOM 21m LVL) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 219 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-03, LV75-02, LV24-R1, LV43-02, LV10-L1, LV11-L3, LV12-L3, LV58-02, LV59-02, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP23-01, TP24-01, TR29-01, TR39-01, TD59-01, TD60-01, TD61-01, TD62-01, TD63-01, TD64-01, TD65-01, TD66-01, ZZ99- |  | EPD | PEM
26 | 1TA | D02C1.5 | 10.5.01 | 1TA02SC01 | 415V SWGR MOTOR MODULE # 1TA02RE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 216 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, TD60-02, TD61-02, TD62-02, TD63-02, TD64-02, TD65-02, ZZ99- |  | EPD | EPD
27 | 1TA | D03Q050 | 10.4.14 | 1TA02SP01 | 415V SWGR MOTOR MODULE # 1TA02RE | CENTRIFUGAL PUMP FOR AWU-4 (AW ROOM 21m LVL) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 216 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-03, LV75-02, LV24-R1, LV43-02, LV10-L1, LV11-L3, LV12-L3, LV58-02, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP23-01, TP24-01, TR29-01, TR39-01, TD59-01, TD60-01, TD61-01, TD62-01, TD63-01, TD64-01, TD65-01, ZZ99- |  | EPD | PEM
28 | 1TA | D07C1.5 | 10.5.08 | 1TA02TC01 | 415V SWGR MOTOR MODULE # 1TA02RF | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 157 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV79-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TR48-05, TR25-05, TP55-02, TP56-02, TP58-02, ZZ99- |  | EPD | EPD
29 | 1TA | D03Q010 | 10.4.11 | 1TA02TP01 | 415V SWGR MOTOR MODULE # 1TA02RF | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 152 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-02, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-01, LV24-L2, LV43-02, LV10-L2, LV11-R3, LV12-R2, LV58-01, LV04-L1, LV64-03, TR25-01, TP55-01, TP56-01, TP58-01, ZZ99- |  | EPD | PEM
30 | 1TA | D3HQ025 | 10.4.18 | 1TA02UP01 | 415V SWGR O/G MODULE # 1TA02RG | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 21m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 232 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-01, CC88-01, CC86-02, CC84-01, CC83-01, CC82-01, CC81-01, CC79-01, CC77-01, CC75-01, CC73-01, CC01-01, LR08-01, LV73-02, LV39-R1, LV38-R3, LV46-02, LV47-02, LV48-01, LV49-02, LV06-R1, LV05-R1, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP04-01, TR26-01, TR40-01, TD18-01, TR47-01, TD51-01, TD50-01, TD47-01, TD45-01, TD43-01, TR46-01, TD41-01, TD59-01, TD60-01, TD61-01, ZZ99- |  | EPD | EPD
31 | 1TA | D03L2.5 | 10.4.26 | 1TA03BP01 | 415V SWGR O/G MODULE # 1TA03FB | EXHAUST AIR FAN FOR OIL ROOM (AT 5m AB BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC89-03, CC92-03, LR05-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TG65-02, ZZ99- |  | EPD | PEM
32 | 1TA | D03L2.5 | 10.4.26 | 1TA03CP01 | 415V SWGR O/G MODULE # 1TA03FC | EXHAUST AIR FAN FOR OIL ROOM (AT 5m AB BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC89-03, CC92-03, LR05-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TG65-02, ZZ99- |  | EPD | PEM
33 | 1TA | D03L2.5 | 10.4.26 | 1TA03PP01 | 415V SWGR O/G MODULE # 1TA03RB | EXHAUST AIR FAN FOR BATTERY ROOM (AT 8m CD BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV80-02, DC01-02, DC02-02, DC03-02, DC04-02, DC05-02, ZZ99- |  | EPD | PEM
34 | 1TA | D07C1.5 | 10.5.08 | 1TA03QC01 | 415V SWGR MOTOR MODULE # 1TA03RC | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 138 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, ZZ99- |  | EPD | EPD
35 | 1TA | D03Q010 | 10.4.11 | 1TA03QP01 | 415V SWGR MOTOR MODULE # 1TA03RC | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 143 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-01, BQ21-01, BQ14-02, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-01, LV24-L2, LV43-02, LV10-L2, LV11-L3, LV12-L3, LV58-02, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, ZZ99- |  | EPD | PEM
36 | 1TA | D07C1.5 | 10.5.08 | 1TA03RC01 | 415V SWGR MOTOR MODULE # 1TA03RD | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 131 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV79-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TR48-05, TR25-05, TP55-02, ZZ99- |  | EPD | EPD
37 | 1TA | D03Q010 | 10.4.11 | 1TA03RP01 | 415V SWGR MOTOR MODULE # 1TA03RD | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 146 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ18-01, BQ17-02, BQ21-02, BQ14-02, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV79-02, MR10-01, MA05-01, MV68-01, MV10-01, MV11-01, MV12-01, MV81-02, MV21-01, MV20-01, MV97-02, MV98-02, MV99-02, MR16-03, TR48-04, TR25-01, TP55-01, ZZ99- |  | EPD | PEM
38 | 1TA | D03L2.5 | 10.4.26 | 1TA03SP01 | 415V SWGR O/G MODULE # 1TA03RE | EXHAUST AIR FAN FOR BATTERY ROOM (AT 8m CD BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 99 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV80-02, DC01-02, DC02-02, DC03-02, DC04-02, DC05-02, ZZ99- |  | EPD | PEM
39 | 1TA | D03L2.5 | 10.4.26 | 1TA03TP01 | 415V SWGR O/G MODULE # 1TA03RF | EXHAUST AIR FAN FOR BATTERY ROOM (AT 8m CD BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ12-02, BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV80-02, DC01-02, DC02-02, DC03-02, DC04-02, DC05-02, ZZ99- |  | EPD | PEM
40 | 1TA | D3HQ025 | 10.4.18 | 1TA04PP01 | 415V SWGR O/G MODULE # 1TA04RB | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 21m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 228 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ17-01, BQ21-01, BQ14-01, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-01, CC88-01, CC86-02, CC84-01, CC83-01, CC82-01, CC81-01, CC79-01, CC77-01, CC75-01, CC73-01, CC01-01, LR08-01, LV73-02, LV39-R1, LV38-R3, LV46-02, LV47-02, LV48-01, LV49-02, LV06-R1, LV05-R1, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP04-01, TR26-01, TR40-01, TD18-01, TR47-01, TD51-01, TD50-01, TD47-01, TD45-01, TD43-01, TR46-01, TD41-01, TD59-01, TD60-01, TD61-01, ZZ99- |  | EPD | EPD
41 | 1TA | D3HQ025 | 10.4.18 | 1TA04SP01 | 415V SWGR O/G MODULE # 1TA04RE | AC FUSE DB FOR FIRE DAMPER (TG HALL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
42 | 1TA | D03L2.5 | 10.4.26 | 1TA04UP01 | 415V SWGR O/G MODULE # 1TA04RG | EXHAUST AIR FAN FOR AC PLANT ROOM (AT 0m D-E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 127 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC34-02, CC67-03, CC66-03, CC65-03, CC64-03, CC63-03, CC62-03, CC04-03, CC06-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, AC13-03, ZZ99- |  | EPD | PEM
43 | 1TA | D03L2.5 | 10.4.26 | 1TA04VP01 | 415V SWGR O/G MODULE # 1TA04RH | EXHAUST AIR FAN FOR AC PLANT ROOM (AT 0m D-E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ13-02, BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV25-L4, LV74-03, DC07-03, DC08-03, DC09-03, DC10-03, DC11-03, DR03-03, ZZ99- |  | EPD | PEM
44 | 1TA | D03L2.5 | 10.4.26 | 1TA05BP01 | 415V SWGR O/G MODULE # 1TA05FB | EXHAUST AIR FAN FOR AC PLANT ROOM (AT 0m D-E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC34-02, CC67-03, CC66-03, CC65-03, CC64-03, CC63-03, CC62-03, CC04-03, CC06-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, AC13-03, ZZ99- |  | EPD | PEM
45 | 1TA | D03L2.5 | 10.4.26 | 1TA05CP01 | 415V SWGR O/G MODULE # 1TA05FC | EXHAUST FAN FOR NON AC AREA OF SWAS ROOM (AT 9m BC BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV45-03, TR22-03, ZZ99- |  | EPD | PEM
46 | 1TA | D03L2.5 | 10.4.26 | 1TA05EP01 | 415V SWGR O/G MODULE # 1TA05FE | EXHAUST AIR FAN FOR GAS CYLINDER ROOM (AT 0m A-ROW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 206 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, TG39-02, TG41-02, TG42-02, TR08-02, ZZ99- |  | EPD | PEM
47 | 1TA | D3HQ025 | 10.4.18 | 1TA05GP01 | 415V SWGR O/G MODULE # 1TA05FG | AC FUSE DB FOR FIRE DAMPER (TG HALL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 80 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
48 | 1TA | E04V0.5 | 10.7.02 | 1TA06AC01 | 415V SWGR I/C MODULE # 1TA06FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | 93 | 30.11.2019 | DR0720_4798-4G-83 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | BQ13-03, BQ14-03, BQ26-R3, BQ07-L3, BQ19-R3, BQ20-R3, QR03-R3, CC71-06, CC52-04, CC43-04, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
49 | 1TA | D02C1.5 | 10.5.01 | 1TA06AC02 | 415V SWGR I/C MODULE # 1TA06FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV79-03, MR10-03, MA05-03, MV68-05, MV67-05, MV66-05, MV65-05, MV64-02, MV48-02, MV49-02 |  | EPD | EPD
50 | 1TA | E04V0.5 | 10.7.02 | 1TA06AC03 | 415V SWGR I/C MODULE # 1TA06FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | 93 | 30.11.2019 | DR0720_4798-4G-83 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | BQ13-03, BQ14-03, BQ26-R3, BQ07-L3, BQ19-R3, BQ20-R3, QR03-R3, CC71-06, CC52-04, CC43-04, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
51 | 1TA | E04V0.5 | 10.7.02 | 1TA07AC01 | 415V SWGR B/C MODULE # 1TA07FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | 93 | 02.12.2019 | DR0720_4798-4G-83 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | BQ13-03, BQ14-03, BQ26-R3, BQ07-L3, BQ19-R3, BQ20-R3, QR03-R3, CC71-06, CC52-04, CC43-04, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
52 | 1TA | E04V0.5 | 10.7.02 | 1TA07AC02 | 415V SWGR B/C MODULE # 1TA07FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | 93 | 02.12.2019 | DR0720_4798-4G-83 |  |  | DC SUPPLY - 1 & 2 FAIL | OVERALL SCREENED | BQ13-03, BQ14-03, BQ26-R3, BQ07-L3, BQ19-R3, BQ20-R3, QR03-R3, CC71-06, CC52-04, CC43-04, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
53 | 1TA | E04V0.5 | 10.7.02 | 1TA08AC01 | 415V SWGR I/C MODULE # 1TA08FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | 93 | 03.12.2019 | DR0720_4798-4G-82 |  |  | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O | OVERALL SCREENED | BQ13-03, BQ14-03, BQ26-R3, BQ07-L3, BQ19-R3, BQ20-R3, QR03-R3, CC71-06, CC52-04, CC43-04, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
54 | 1TA | D02C1.5 | 10.5.01 | 1TA08AC02 | 415V SWGR I/C MODULE # 1TA08FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | BREAKER ON FEEDBACK | PVC-CU UNARMOURED | BQ13-02, BQ22-02, BQ23-02, BQ06-02, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV79-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV81-03, MV80-03, MV79-03, MV39-02, MV88-03, MV51-02 |  | EPD | EPD
55 | 1TA | E04V0.5 | 10.7.02 | 1TA08AC03 | 415V SWGR I/C MODULE # 1TA08FA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | 93 | 03.12.2019 | DR0720_4798-4G-82 |  |  | BUS N/V, BUS VT IN SERVICE | OVERALL SCREENED | BQ13-03, BQ14-03, BQ26-R3, BQ07-L3, BQ19-R3, BQ20-R3, QR03-R3, CC71-06, CC52-04, CC43-04, CC41-03, CC40-03, CC39-03, ZZ99- |  | EPD | EDN
56 | 1TA | D02C1.5 | 10.5.01 | 1TA09DC01 | 415V SWGR MOTOR MODULE # 1TA09FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 192 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, ZZ99- |  | EPD | EPD
57 | 1TA | D02L2.5 | 10.4.24 | 1TA09DC02 | 415V SWGR MOTOR MODULE # 1TA09FD | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 192 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, ZZ99- |  | EPD | PEM
58 | 1TA | D03Q150 | 10.4.16 | 1TA09DP01 | 415V SWGR MOTOR MODULE # 1TA09FD | CENTRIFUGAL FAN FOR AWU-4 (AW ROOM 21m LVL) | 03C X 150 XLPE-Al FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | BQ17-01, BQ21-01, BQ14-01, BQ26-L1, BQ07-R1, BQ19-L2, BQ20-L2, QR03-L2, CR01-L1, LR10-R2, LV77-02, LV75-01, LV24-L2, LV43-02, LV10-L1, LV11-R3, LV12-R2, LV58-01, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP23-01, TP24-01, TR29-01, TR39-01, TD59-01, ZZ99- |  | EPD | PEM
59 | 1TA | D3HQ025 | 10.4.18 | 1TA10CP01 | 415V SWGR O/G MODULE # 1TA10FC | AC FUSE DB FOR FIRE DAMPER (TG HALL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-02, CC92-01, LR05-01, MR10-01, MA05-01, MV68-01, MV67-01, MV66-01, MV65-02, MV64-03, MV48-01, MV49-01, MV50-01, MV87-01, MV57-R1, MV76-03, ZZ99- |  | EPD | EPD
60 | 1TA | D02C1.5 | 10.5.01 | 1TA10DC01 | 415V SWGR MOTOR MODULE # 1TA10FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-R3, LV37-R3, LV36-R3, LV35-R3, LV34-R3, LV33-R3, LV65-02, ZZ99- |  | EPD | EPD
61 | 1TA | D02L2.5 | 10.4.24 | 1TA10DC02 | 415V SWGR MOTOR MODULE # 1TA10FD | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | SPACE HEATER | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, ZZ99- |  | EPD | PEM
62 | 1TA | D03Q095 | 10.4.15 | 1TA10DP01 | 415V SWGR MOTOR MODULE # 1TA10FD | CENTRIFUGAL FAN FOR AWU-2 (AW ROOM 8m LVL) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 122 | [5 empty] | POWER SUPPLY (55kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-01, CC88-01, CC86-02, CC84-01, CC83-01, CC82-01, CC81-01, CC90-01, LR07-01, LV74-02, LV26-R1, LV27-R1, LV41-02, LV38-L3, LV37-L2, LV36-L2, LV35-L2, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | PEM
63 | 1TA | D03L2.5 | 10.4.26 | 1TA10RP01 | 415V SWGR O/G MODULE # 1TA10RD | EXHAUST AIR FAN FOR GAS CYLINDER ROOM (AT 0m A-ROW) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 204 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TR07-02, TG39-02, TG41-02, TG42-02, TR08-02, ZZ99- |  | EPD | PEM
64 | 1TA | D07C1.5 | 10.5.08 | 1TA10SC01 | 415V SWGR MOTOR MODULE # 1TA10RE | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP02-02, ZZ99- |  | EPD | EPD
65 | 1TA | D03Q010 | 10.4.11 | 1TA10SP01 | 415V SWGR MOTOR MODULE # 1TA10RE | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 148 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-01, LV24-L2, LV43-02, LV10-L2, LV11-L3, LV12-L3, LV58-02, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP02-01, ZZ99- |  | EPD | PEM
66 | 1TA | D03L2.5 | 10.4.26 | 1TA10TP01 | 415V SWGR O/G MODULE # 1TA10RF | EXHAUST FAN FOR NON AC AREA OF SWAS ROOM (AT 9m BC BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 102 | [5 empty] | POWER SUPPLY (0.55kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV24-L3, LV43-03, LV09-L4, LV08-L4, LV45-03, TR22-03, ZZ99- |  | EPD | PEM
67 | 1TA | D03L2.5 | 10.4.26 | 1TA10UP01 | 415V SWGR O/G MODULE # 1TA10RG | EXHAUST AIR FAN FOR AC PLANT ROOM (AT 0m D-E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 93 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV25-L4, LV74-03, DC07-03, DC08-03, DC09-03, DC10-03, DC11-03, DR03-03, ZZ99- |  | EPD | PEM
68 | 1TA | D3HQ025 | 10.4.18 | 1TA10VP01 | 415V SWGR O/G MODULE # 1TA10RH | AC FUSE DB FOR FIRE DAMPER (TG HALL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 107 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-02, CC92-01, LR05-01, MR10-01, MA05-01, MV68-01, MV67-01, MV66-01, MV65-02, MV64-03, MV48-01, MV49-01, MV50-01, MV87-01, MV57-R1, MV76-03, ZZ99- |  | EPD | EPD
69 | 1TA | D03L2.5 | 10.4.26 | 1TA11BP01 | 415V SWGR O/G MODULE # 1TA11FB | EXHAUST AIR FAN FOR AC PLANT ROOM (AT 0m D-E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC34-02, CC67-03, CC66-03, CC65-03, CC64-03, CC63-03, CC62-03, CC04-03, CC06-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, AC13-03, ZZ99- |  | EPD | PEM
70 | 1TA | D03L2.5 | 10.4.26 | 1TA11CP01 | 415V SWGR O/G MODULE # 1TA11FC | EXHAUST AIR FAN FOR AC PLANT ROOM (AT 0m D-E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 93 | [5 empty] | POWER SUPPLY (1.1kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV25-L4, LV74-03, DC07-03, DC08-03, DC09-03, DC10-03, DC11-03, DR03-03, ZZ99- |  | EPD | PEM
71 | 1TA | D02C1.5 | 10.5.01 | 1TA11PC01 | 415V SWGR MOTOR MODULE # 1TA11RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 195 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, TD60-02, ZZ99- |  | EPD | EPD
72 | 1TA | D03Q050 | 10.4.14 | 1TA11PP01 | 415V SWGR MOTOR MODULE # 1TA11RB | CENTRIFUGAL PUMP FOR AWU-4 (AW ROOM 21m LVL) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 195 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-03, LV75-02, LV24-R1, LV43-02, LV10-R1, LV11-R3, LV12-R1, LV58-02, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP23-01, TP24-01, TR29-01, TR39-01, TD59-01, TD60-01, ZZ99- |  | EPD | PEM
73 | 1TA | D3HQ025 | 10.4.18 | 1TA11QP01 | 415V SWGR O/G MODULE # 1TA11RC | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 21m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 203 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-02, LV24-R1, LV43-01, LV10-L1, LV11-L3, LV12-L3, LV58-02, LV59-01, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP23-01, TP24-01, TR29-01, TR39-01, TD59-01, TD60-01, TD61-01, TD62-01, TD63-01, TD64-01, TD65-01, ZZ99- |  | EPD | EPD
74 | 1TA | D07C1.5 | 10.5.08 | 1TA11SC01 | 415V SWGR MOTOR MODULE # 1TA11RE | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP27-02, ZZ99- |  | EPD | EPD
75 | 1TA | D03Q010 | 10.4.11 | 1TA11SP01 | 415V SWGR MOTOR MODULE # 1TA11RE | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 181 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-01, LV24-L2, LV43-02, LV10-L2, LV11-L3, LV12-L3, LV58-01, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP27-01, ZZ99- |  | EPD | PEM
76 | 1TA | D03L2.5 | 10.4.26 | 1TA12DP01 | 415V SWGR O/G MODULE # 1TA12FD | EXHAUST AIR FAN FOR BATTERY ROOM (AT 8m CD BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 94 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV80-02, DC01-02, DC02-02, DC03-02, DC04-02, DC05-02, DC06-02, ZZ99- |  | EPD | PEM
77 | 1TA | D03L2.5 | 10.4.26 | 1TA12EP01 | 415V SWGR O/G MODULE # 1TA12FE | EXHAUST AIR FAN FOR BATTERY ROOM (AT 8m CD BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV80-02, DC01-02, DC02-02, DC03-02, ZZ99- |  | EPD | PEM
78 | 1TA | D03L2.5 | 10.4.26 | 1TA12FP01 | 415V SWGR O/G MODULE # 1TA12FF | EXHAUST AIR FAN FOR BATTERY ROOM (AT 8m CD BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 90 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV25-L4, LV80-02, DC01-02, DC02-02, DC03-02, DC04-02, ZZ99- |  | EPD | PEM
79 | 1TA | D3HQ025 | 10.4.18 | 1TA12GP01 | 415V SWGR O/G MODULE # 1TA12FG | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 21m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 204 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-02, LV24-R1, LV43-02, LV10-L1, LV11-L3, LV12-L3, LV58-02, LV59-02, TR24-01, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP23-01, TP24-01, TR29-01, TR39-01, TD59-01, TD60-01, TD61-01, TD62-01, TD63-01, TD64-01, TD65-01, ZZ99- |  | EPD | EPD
80 | 1TA | D03L2.5 | 10.4.26 | 1TA12PP01 | 415V SWGR O/G MODULE # 1TA12RB | EXHAUST AIR FAN FOR OIL ROOM (AT 5m AB BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC89-03, CC92-03, LR05-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TG65-02, ZZ99- |  | EPD | PEM
81 | 1TA | D03L2.5 | 10.4.26 | 1TA12QP01 | 415V SWGR O/G MODULE # 1TA12RC | EXHAUST AIR FAN FOR OIL ROOM (AT 5m AB BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 114 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC89-03, CC92-03, LR05-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TG65-02, ZZ99- |  | EPD | PEM
82 | 1TA | D07C1.5 | 10.5.08 | 1TA12RC01 | 415V SWGR MOTOR MODULE # 1TA12RD | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, ZZ99- |  | EPD | EPD
83 | 1TA | D03Q010 | 10.4.11 | 1TA12RP01 | 415V SWGR MOTOR MODULE # 1TA12RD | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 144 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R2, BQ07-L2, BQ19-R2, BQ20-R2, QR03-R2, CR01-R1, LR10-L3, LV77-02, LV75-01, LV24-L2, LV43-02, LV10-L2, LV11-L3, LV12-L3, LV58-01, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, ZZ99- |  | EPD | PEM
84 | 1TA | D07C1.5 | 10.5.08 | 1TA12SC01 | 415V SWGR MOTOR MODULE # 1TA12RE | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV79-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TR48-05, TR25-05, TP55-02, ZZ99- |  | EPD | EPD
85 | 1TA | D03Q010 | 10.4.11 | 1TA12SP01 | 415V SWGR MOTOR MODULE # 1TA12RE | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 140 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R2, BQ07-L2, BQ19-R2, BQ20-R2, QR03-R2, CR01-R1, LR10-L3, LV79-02, MR10-01, MA05-01, MV68-01, MV10-01, MV11-01, MV12-01, MV81-02, MV21-01, MV20-01, MV97-02, MV98-02, MV99-02, MR16-03, TR48-04, TR25-01, TP55-01, ZZ99- |  | EPD | PEM
86 | 1TA | D03L2.5 | 10.4.26 | 1TA12TP01 | 415V SWGR O/G MODULE # 1TA12RF | SUPPLY AIR FAN FOR MCC ROOM (AT 0m E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 132 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC34-02, CC67-03, CC66-03, CC65-03, CC64-03, CC63-03, CC62-03, CC04-03, CC06-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, AC13-03, DR07-03, AC14-L4, AC15-L4, AC16-L4, ZZ99- |  | EPD | PEM
87 | 1TA | D03L2.5 | 10.4.26 | 1TA12UP01 | 415V SWGR O/G MODULE # 1TA12RG | SUPPLY AIR FAN FOR MCC ROOM (AT 0m E-F BAY) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 138 | [5 empty] | POWER SUPPLY (1.5kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC34-02, CC67-03, CC66-03, CC65-03, CC64-03, CC63-03, CC62-03, CC04-03, CC06-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, AC13-03, DR07-03, AC14-L4, AC15-L4, AC16-L4, AC17-L4, AC18-L4, AC19-L4, ZZ99- |  | EPD | PEM
88 | 1TA | D3HQ025 | 10.4.18 | 1TA12VP01 | 415V SWGR O/G MODULE # 1TA12RH | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 8m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-02, CC88-01, CC86-02, CC84-01, CC83-01, CC82-01, CC81-01, CC79-01, CC77-01, CC75-01, CC73-01, CC01-01, LR08-01, LV73-02, LV39-R1, LV38-R3, LV37-R2, LV36-R1, LV35-R1, LV34-R1, LV33-R1, LV65-01, ZZ99- |  | EPD | EPD
89 | 1TA | D3HQ025 | 10.4.18 | 1TA12WP01 | 415V SWGR O/G MODULE # 1TA12RI | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER (AW ROOM 8m LVL) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CC71-03, CC89-02, CC88-01, CC86-02, CC84-01, CC83-01, CC82-01, CC81-01, CC79-01, CC77-01, CC75-01, CC73-01, CC01-01, LR08-01, LV73-02, LV39-R1, LV38-R3, LV37-R2, LV36-R1, LV35-R1, LV34-R1, LV33-R1, LV65-01, ZZ99- |  | EPD | EPD
90 | 1TA | D02C1.5 | 10.5.01 | 1TA13DC01 | 415V SWGR MOTOR MODULE # 1TA13FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 197 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV43-03, LV10-L4, LV11-L4, LV12-L4, LV58-02, LV59-02, TR24-02, TP53-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP23-02, TP24-02, TR29-02, TR39-02, TD59-02, TD60-02, TD61-02, ZZ99- |  | EPD | EPD
91 | 1TA | D03Q050 | 10.4.14 | 1TA13DP01 | 415V SWGR MOTOR MODULE # 1TA13FD | CENTRIFUGAL PUMP FOR AWU-3 (AW ROOM 21m LVL) | 03C X 050 XLPE-Al FRLS ( 1.1 kV ) | 197 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-03, LV75-02, LV24-L2, LV43-02, LV10-R1, LV11-R3, LV12-R1, LV58-02, LV59-02, TR24-02, TP53-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP21-01, TP20-01, TP22-01, TP23-01, TP24-01, TR29-01, TR39-01, TD59-01, TD60-01, TD61-01, ZZ99- |  | EPD | PEM
92 | 1TA | D03L2.5 | 10.4.26 | 1TA13EP01 | 415V SWGR O/G MODULE # 1TA13FE | EXHAUST AIR FAN FOR CENTRAL LUBE OIL PURIFICATION ROOM (AT 0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
93 | 1TA | D03L2.5 | 10.4.26 | 1TA13FP01 | 415V SWGR O/G MODULE # 1TA13FF | EXHAUST AIR FAN FOR CENTRAL LUBE OIL PURIFICATION ROOM (AT 0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 119 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CC71-04, CC52-02, CC43-03, CC42-03, CC33-03, CC81-03, CC90-03, LR07-03, LV74-03, LV26-L4, LV27-L4, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
94 | 1TA | D02C1.5 | 10.5.01 | 1TA13PC01 | 415V SWGR MOTOR MODULE # 1TA13RB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-R3, LV37-R3, LV36-R3, LV35-R3, LV34-R3, LV33-R3, LV65-02, ZZ99- |  | EPD | EPD
95 | 1TA | D03Q025 | 10.4.12 | 1TA13PP01 | 415V SWGR MOTOR MODULE # 1TA13RB | CENTRIFUGAL PUMP FOR AWU-2 (AW ROOM 8m LVL) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 113 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-02, LV24-L2, LV42-01, LV41-02, LV38-L3, LV37-L2, LV36-L2, LV35-L2, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | PEM
96 | 1TA | D03L2.5 | 10.4.26 | 1TA13QP01 | 415V SWGR O/G MODULE # 1TA13RC | EXHAUST AIR FAN FOR CENTRAL LUBE OIL PURIFICATION ROOM (AT 0 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY (2.2kW) | XLPE-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99- |  | EPD | PEM
97 | 1TA | D07C1.5 | 10.5.08 | 1TA13RC01 | 415V SWGR MOTOR MODULE # 1TA13RD | EMERGENCY STOP PB | 07C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 191 | [5 empty] | CLOSE/OPEN COMMAND, EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV79-03, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV99-04, MR16-05, TR48-05, TR25-05, TP55-02, TP54-02, TP52-02, TP49-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, ZZ99- |  | EPD | EPD
98 | 1TA | D03Q010 | 10.4.11 | 1TA13RP01 | 415V SWGR MOTOR MODULE # 1TA13RD | ROOF EXTRACTOR (TG HALL) | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 207 | [5 empty] | POWER SUPPLY (5.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R2, BQ07-L2, BQ19-R2, BQ20-R2, QR03-R2, CR01-R1, LR10-L3, LV79-02, MR10-02, MA05-02, MV68-01, MV10-01, MV11-01, MV12-01, MV81-02, MV21-01, MV20-01, MV97-02, MV98-02, MV99-02, MR16-03, TR48-04, TR25-01, TP55-01, TP54-01, TP52-01, TP49-01, TP03-01, TP05-01, TP10-01, TP11-01, TP12-01, TP13-01, TP14-01, TP15-01, TP16-01, TP17-01, TP18-01, ZZ99- |  | EPD | PEM
99 | 1TA | D3HQ025 | 10.4.18 | 1TA13SP01 | 415V SWGR O/G MODULE # 1TA13RE | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
100 | 1TA | D3HQ025 | 10.4.18 | 1TA13TP01 | 415V SWGR O/G MODULE # 1TA13RF | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY (63A) | XLPE-AL UNARMOURED | SITE ROUTING |  | EPD | EPD
101 | 1TA | D02C1.5 | 10.5.01 | 1TA13UC01 | 415V SWGR MOTOR MODULE # 1TA13RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 107 | [5 empty] | EM.STOP NOT OPERATED | PVC-CU UNARMOURED | BQ14-02, BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-R3, LV42-03, LV41-03, LV38-R3, LV37-R3, LV36-R3, LV35-R3, LV34-R3, LV33-R3, LV65-02, ZZ99- |  | EPD | EPD
102 | 1TA | D03Q025 | 10.4.12 | 1TA13UP01 | 415V SWGR MOTOR MODULE # 1TA13RG | CENTRIFUGAL PUMP FOR AWU-1 (AW ROOM 8m LVL) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 115 | [5 empty] | POWER SUPPLY (18.5kW) | XLPE-AL UNARMOURED | BQ16-01, BQ15-L1, BQ26-R1, BQ07-L1, BQ19-R1, BQ20-R1, QR03-R1, CR01-R1, LR10-L3, LV77-02, LV75-01, LV24-L2, LV42-01, LV41-02, LV38-L3, LV37-L3, LV36-L2, LV35-L2, LV34-L1, LV33-L1, LV65-01, ZZ99- |  | EPD | PEM
103 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C001 | 1TA-1FE | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 76 | 15.03.2020 | DR0817_4798-4G-90
104 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C002 | 1TA-19FD | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 68 | 15.03.2020 | DR0817_4798-4G-90
105 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C003 | 1TA-2FE | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 75 | 15.03.2020 | DR0817_4798-4G-90
106 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C004 | 1TA-9FD | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 69 | 15.03.2020 | DR0817_4798-4G-90
107 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C005 | 1TA-1FB | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 76 | 15.03.2020 | DR0817_4798-4G-90
108 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C006 | 1TA-13RG | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 65 | 15.03.2020 | DR0817_4798-4G-90
109 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C007 | 1TA-2RB | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 75 | 15.03.2020 | DR0817_4798-4G-90
110 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C008 | 1TA-18RB | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 65 | 15.03.2020 | DR0817_4798-4G-90
111 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C009 | 1TA-2RD | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 75 | 15.03.2020 | DR0817_4798-4G-90
112 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C010 | 1TA-13FD | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 65 | 15.03.2020 | DR0817_4798-4G-90
113 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C011 | 1TA-2RE | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 75 | 15.03.2020 | DR0817_4798-4G-76
114 | 1TA | E04V0.5 | 10.7.02 | CVP61-LTUD VNT-C012 | 1TA-11RB | CVP-61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 63 | 15.03.2020 | DR0817_4798-4G-76
1 | 1TB | D02C1.5 | 10.5.01 | 1TB01AC01 | 415V SWGR MOTOR MODULE # 1TB01FA | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | 55 | 12.03.20 | DR1150_17PA011556 |  |  | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
2 | 1TB | D02L2.5 | 10.4.24 | 1TB01AC02 | 415V SWGR MOTOR MODULE # 1TB01FA | MOTOR SPACE HEATER | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 63 | 65 | 6.3.20 | DR1095_0005 |  |  | SPACE HEATER |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
3 | 1TB | D03Q025 | 10.4.12 | 1TB01AP01 | 415V SWGR MOTOR MODULE # 1TB01FA | CENTRIFUGAL FAN FOR UAF | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 61 | 65 | 12.03.20 | DR0819_0001 |  |  | POWER SUPPLY (30kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
4 | 1TB | D3HQ025 | 10.4.18 | 1TB01BP01 | 415V SWGR O/G MODULE # 1TB01FB | HOIST FOR ESP CONTROL ROOM BLDG ELEVATOR M/C ROOM (3T) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (32A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
5 | 1TB | D02Q010 | 10.4.06 | 1TB01CP01 | 415V SWGR O/G MODULE # 1TB01FC | SPLIT AC FOR CONTROL ROOM | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 48 | [5 empty] | POWER SUPPLY (4.5kW) |  | ES51-L1, ES52-L2, ES53-L1, ES87-R1, ER07-L1, ES45-R1, ZZ99- |  | EPD | PEM
6 | 1TB | D04Q010 | 10.4.22 | 1TB01DP01 | 415V SWGR O/G MODULE # 1TB01FD | ELEVATOR MOTOR | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 57 | [5 empty] | POWER SUPPLY (16.5kW) |  | ES51-L1, ES93-R1, ER05-L1, ES43-R1, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L2, IR25-L2, ZZ99- |  | EPD | PEM
7 | 1TB | D02Q010 | 10.4.06 | 1TB01EP01 | 415V SWGR O/G MODULE # 1TB01FE | SPLIT AC FOR CONTROL ROOM | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY (4.5kW) |  | ES51-L1, ES93-R1, ER05-L1, ES43-R1, ZZ99- |  | EPD | PEM
8 | 1TB | D3HQ025 | 10.4.18 | 1TB01FP01 | 415V SWGR O/G MODULE # 1TB01FF | HOIST FOR ESP CONTROL ROOM (FOR HANDLING AT 3.7m FLOOR) (10T | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 56 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES94-L1, ES95-L2, ES79-L2, ES74-R1, ES73-R1, ES72-R1, ES71-01, ER04-01, ZZ99- |  | EPD | PEM
9 | 1TB | D02Q010 | 10.4.06 | 1TB01GP01 | 415V SWGR O/G MODULE # 1TB01FG | SPLIT AC FOR CONTROL ROOM | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (4.5kW) |  | ES51-L1, ES94-L1, ES95-L2, ES79-L2, ES74-R1, ES73-R1, ES83-L1, ER03-L1, ES42-01, ZZ99- |  | EPD | PEM
10 | 1TB | D3HQ025 | 10.4.18 | 1TB01QP01 | 415V SWGR O/G MODULE # 1TB01RC | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | EPD
11 | 1TB | D04Q010 | 10.4.22 | 1TB01RP01 | 415V SWGR O/G MODULE # 1TB01RD | STRIP HEATER FOR AHU ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (8kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
12 | 1TB | D3HQ025 | 10.4.18 | 1TB01SP01 | 415V SWGR O/G MODULE # 1TB01RE | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
13 | 1TB | D3HQ025 | 10.4.18 | 1TB01UP01 | 415V SWGR O/G MODULE # 1TB01RG | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
14 | 1TB | D3HQ025 | 10.4.18 | 1TB01VP01 | 415V SWGR O/G MODULE # 1TB01RH | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
15 | 1TB | D3HQ025 | 10.4.18 | 1TB01WP01 | 415V SWGR O/G MODULE # 1TB01RI | WELDING SOCKET | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | PEM
17 | 1TB | D02C1.5 | 10.5.01 | 1TB02BC01 | 415V SWGR MOTOR MODULE # 1TB02FB | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
18 | 1TB | D03Q025 | 10.4.12 | 1TB02BP01 | 415V SWGR MOTOR MODULE # 1TB02FB | AIR HANDLING UNIT (AHU 1) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | 80 | 07.03.20 | DR0819_0001 |  |  | POWER SUPPLY (18.5kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
19 | 1TB | D02C1.5 | 10.5.01 | 1TB02CC01 | 415V SWGR MOTOR MODULE # 1TB02FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 68 | 56 | 12.03.20 | DR1150_17PA011556 |  |  | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
20 | 1TB | D03Q010 | 10.4.11 | 1TB02CP01 | 415V SWGR MOTOR MODULE # 1TB02FC | CENTRIFUGAL PUMP FOR UAF | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 66 | 64 | 13.03.2020 | 20 |  |  | POWER SUPPLY (11kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
21 | 1TB | D02C1.5 | 10.5.01 | 1TB02DC01 | 415V SWGR MOTOR MODULE # 1TB02FD | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | EPD
22 | 1TB | D03L2.5 | 10.4.26 | 1TB02DP01 | 415V SWGR MOTOR MODULE # 1TB02FD | CLEAR WATER TRANSFER PUMP (P2A) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (3.7kW) |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | PEM
23 | 1TB | D02C1.5 | 10.5.01 | 1TB02EC01 | 415V SWGR MOTOR MODULE # 1TB02FE | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | EPD
24 | 1TB | D03L2.5 | 10.4.26 | 1TB02EP01 | 415V SWGR MOTOR MODULE # 1TB02FE | WASTE WATER TRANSFER PUMP (P3A) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (3.7kW) |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | PEM
25 | 1TB | D03L2.5 | 10.4.26 | 1TB02FP01 | 415V SWGR O/G MODULE # 1TB02FF | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | 63 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES52-R2, ES90-02, ER06-02, ES44-L3, ES31-L3, ES25-R2, ES27-L3, ES43-R2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
26 | 1TB | D02C1.5 | 10.5.01 | 1TB02QC01 | 415V SWGR MOTOR MODULE # 1TB02RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
27 | 1TB | D03L2.5 | 10.4.26 | 1TB02QP01 | 415V SWGR MOTOR MODULE # 1TB02RC | FRESH AIR FAN FOR AHU ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
28 | 1TB | D03L2.5 | 10.4.26 | 1TB02RP01 | 415V SWGR O/G MODULE # 1TB02RD | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 63 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
29 | 1TB | D03L2.5 | 10.4.26 | 1TB02TP01 | 415V SWGR O/G MODULE # 1TB02RF | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 63 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
30 | 1TB | D3HQ025 | 10.4.18 | 1TB02UP01 | 415V SWGR O/G MODULE # 1TB02RG | SUMP PUMP | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | PEM
31 | 1TB | D04Q010 | 10.4.22 | 1TB02VP01 | 415V SWGR O/G MODULE # 1TB02RH | STRIP HEATER FOR AHU ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (8kW) |  | ES51-R1, ES52-R1, ES90-01, ER06-01, ES44-L1, ES31-R2, ES25-R1, ES27-L1, ES43-R1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
32 | 1TB | D3HQ025 | 10.4.18 | 1TB02WP01 | 415V SWGR O/G MODULE # 1TB02RI | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 91 | [5 empty] | POWER SUPPLY (63A) |  | ES51-R1, ES52-R1, ES90-01, ER06-01, ES44-L1, ES31-R2, ES25-R1, ES27-L1, ES43-R1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
33 | 1TB | D03L2.5 | 10.4.26 | 1TB02XP01 | 415V SWGR O/G MODULE # 1TB02RJ | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 63 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
34 | 1TB | D3HQ185 | 10.4.21 | 1TB03BP01 | 415V SWGR O/G MODULE # 1TB03FB | CONDENSING UNIT | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 71 | 68 | 11.03.20 | DR2687-1 |  |  | POWER SUPPLY (105kW) |  | ES51-R1, ES93-L2, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
35 | 1TB | D3HQ185 | 10.4.21 | 1TB03CP01 | 415V SWGR O/G MODULE # 1TB03FC | CONDENSING UNIT | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 71 | 60 | 11.03.20 | DR2687-1 |  |  | POWER SUPPLY (105kW) |  | ES51-R1, ES93-L2, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
36 | 1TB | D02C1.5 | 10.5.01 | 1TB03QC01 | 415V SWGR MOTOR MODULE # 1TB03RC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
37 | 1TB | D03Q025 | 10.4.12 | 1TB03QP01 | 415V SWGR MOTOR MODULE # 1TB03RC | AIR HANDLING UNIT (AHU 3) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 81 | 86 | 07.03.20 | DR0819_0001 |  |  | POWER SUPPLY (18.5kW) |  | ES51-R1, ES52-R1, ES90-01, ER06-01, ES44-L1, ES31-R2, ES25-R1, ES27-L1, ES43-R1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
39 | 1TB | D03L2.5 | 10.4.26 | 1TB03SP01 | 415V SWGR O/G MODULE # 1TB03RE | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 63 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
40 | 1TB | D3HQ025 | 10.4.18 | 1TB03TP01 | 415V SWGR O/G MODULE # 1TB03RF | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | EPD
41 | 1TB | E04V0.5 | 10.7.02 | 1TB04AC01 | 415V SWGR I/C MODULE # 1TB04FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 265 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O |  | ES51-R3, ES93-R3, ER05-L3, ES43-R3, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, ZZ99- |  | EPD | EDN
42 | 1TB | D02C1.5 | 10.5.01 | 1TB04AC02 | 415V SWGR I/C MODULE # 1TB04FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 31 | [5 empty] | BREAKER ON FEEDBACK |  | ES51-L3, ES52-L3, ES53-L3, ES54-L3, ZZ99- |  | EPD | EPD
43 | 1TB | E04V0.5 | 10.7.02 | 1TB04AC03 | 415V SWGR I/C MODULE # 1TB04FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 265 | [5 empty] | BUS N/V, BUS VT IN SERVICE |  | ES51-R3, ES93-R3, ER05-L3, ES43-R3, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, ZZ99- |  | EPD | EDN
44 | 1TB | E04V0.5 | 10.7.02 | 1TB05AC01 | 415V SWGR B/C MODULE # 1TB05FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 265 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O |  | ES51-R3, ES93-R3, ER05-L3, ES43-R3, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, ZZ99- |  | EPD | EDN
45 | 1TB | E04V0.5 | 10.7.02 | 1TB05AC02 | 415V SWGR B/C MODULE # 1TB05FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 265 | [5 empty] | DC SUPPLY - 1 & 2 FAIL |  | ES51-R3, ES93-R3, ER05-L3, ES43-R3, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, ZZ99- |  | EPD | EDN
46 | 1TB | E04V0.5 | 10.7.02 | 1TB06AC01 | 415V SWGR I/C MODULE # 1TB06FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 265 | [5 empty] | CLOSE/OPEN COMMAND, BKR STATUS, TRIP RELAY OPTD. (86), 25C O |  | ES51-R3, ES93-R3, ER05-L3, ES43-R3, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, ZZ99- |  | EPD | EDN
47 | 1TB | D02C1.5 | 10.5.01 | 1TB06AC02 | 415V SWGR I/C MODULE # 1TB06FA | UPSTREAM BREAKER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | BREAKER ON FEEDBACK |  | ES51-L3, ES94-L3, ES95-L3, ES65-02, ES80-L3, ES73-R2, ES72-R2, ES70-R2, ZZ99- |  | EPD | EPD
48 | 1TB | E04V0.5 | 10.7.02 | 1TB06AC03 | 415V SWGR I/C MODULE # 1TB06FA | DDCMIS | 04P X 0.5 Paired Screened(O) ( 225 V ) | 265 | [5 empty] | BUS N/V, BUS VT IN SERVICE |  | ES51-R3, ES93-R3, ER05-L3, ES43-R3, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, ZZ99- |  | EPD | EDN
49 | 1TB | D3HQ185 | 10.4.21 | 1TB07BP01 | 415V SWGR O/G MODULE # 1TB07FB | CONDENSING UNIT | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 96 | 71 | 11.03.20 | DR2687-1 |  |  | POWER SUPPLY (105kW) |  | ES51-R1, ES52-R1, ES90-01, ER06-01, ES44-L1, ES31-R2, ES25-R1, ES27-L1, ES43-R1, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
50 | 1TB | D02C1.5 | 10.5.01 | 1TB07CC01 | 415V SWGR MOTOR MODULE # 1TB07FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
51 | 1TB | D03Q025 | 10.4.12 | 1TB07CP01 | 415V SWGR MOTOR MODULE # 1TB07FC | AIR HANDLING UNIT (AHU 2) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 86 | 88 | 07.03.20 | DR0819_0001 |  |  | POWER SUPPLY (18.5kW) |  | ES51-R1, ES52-R1, ES90-01, ER06-01, ES44-L1, ES31-R2, ES25-R1, ES27-L1, ES43-R1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
52 | 1TB | D04Q010 | 10.4.22 | 1TB07DP01 | 415V SWGR O/G MODULE # 1TB07FD | PAN HUMIDIFIER FOR AHU ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 76 | [5 empty] | POWER SUPPLY (6.5kW) |  | ES51-R1, ES52-R1, ES90-01, ER06-01, ES44-L1, ES31-R2, ES25-R1, ES27-L1, ES43-R1, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
53 | 1TB | D02Q010 | 10.4.06 | 1TB07QP01 | 415V SWGR O/G MODULE # 1TB07RC | SPLIT AC FOR CONTROL ROOM | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 44 | [5 empty] | POWER SUPPLY (4.5kW) |  | ES51-L1, ES93-R1, ER05-L1, ES43-R1, ES27-L1, ES28-L1, ES29-L1, ES30-02, ZZ99- |  | EPD | PEM
54 | 1TB | D02Q010 | 10.4.06 | 1TB07RP01 | 415V SWGR O/G MODULE # 1TB07RD | SPLIT AC FOR CONTROL ROOM | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY (4.5kW) |  | ES51-L1, ES94-L1, ES95-L2, ES79-L2, ES74-R1, ES73-R1, ES83-L1, ER03-L1, ES42-01, ZZ99- |  | EPD | PEM
55 | 1TB | D02C1.5 | 10.5.01 | 1TB07UC01 | 415V SWGR MOTOR MODULE # 1TB07RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 63 | 58 | 12.03.20 | DR1150_17PA011556 |  |  | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
56 | 1TB | D03Q010 | 10.4.11 | 1TB07UP01 | 415V SWGR MOTOR MODULE # 1TB07RG | CENTRIFUGAL PUMP FOR UAF | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 61 | 65 | 13.03.2020 | 20 |  |  | POWER SUPPLY (11kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
57 | 1TB | D02C1.5 | 10.5.01 | 1TB07VC01 | 415V SWGR MOTOR MODULE # 1TB07RH | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | EPD
58 | 1TB | D03L2.5 | 10.4.26 | 1TB07VP01 | 415V SWGR MOTOR MODULE # 1TB07RH | WASTE WATER TRANSFER PUMP (P3B) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (3.7kW) |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | PEM
59 | 1TB | D3HQ025 | 10.4.18 | 1TB07WP01 | 415V SWGR O/G MODULE # 1TB07RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | EPD
60 | 1TB | D3HQ025 | 10.4.18 | 1TB07XP01 | 415V SWGR O/G MODULE # 1TB07RJ | SUMP PUMP | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | PEM
61 | 1TB | D3HQ185 | 10.4.21 | 1TB08BP01 | 415V SWGR O/G MODULE # 1TB08FB | CONDENSING UNIT | 3.5C X 185 XLPE-Al FRLS ( 1.1 kV ) | 71 | 87 | 11.03.20 | DR2687-1 |  |  | POWER SUPPLY (105kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
62 | 1TB | D02C1.5 | 10.5.01 | 1TB08CC01 | 415V SWGR MOTOR MODULE # 1TB08FC | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
63 | 1TB | D03L2.5 | 10.4.26 | 1TB08CP01 | 415V SWGR MOTOR MODULE # 1TB08FC | FRESH AIR FAN FOR AHU ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
64 | 1TB | D03L2.5 | 10.4.26 | 1TB08DP01 | 415V SWGR O/G MODULE # 1TB08FD | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 66 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
65 | 1TB | D03L2.5 | 10.4.26 | 1TB08QP01 | 415V SWGR O/G MODULE # 1TB08RC | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 66 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
68 | 1TB | D3HQ025 | 10.4.18 | 1TB08TP01 | 415V SWGR O/G MODULE # 1TB08RF | WELDING SOCKET | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | PEM
69 | 1TB | D02C1.5 | 10.5.01 | 1TB08UC01 | 415V SWGR MOTOR MODULE # 1TB08RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | EPD
70 | 1TB | D03Q025 | 10.4.12 | 1TB08UP01 | 415V SWGR MOTOR MODULE # 1TB08RG | AIR HANDLING UNIT (AHU 4) | 03C X 025 XLPE-Al FRLS ( 1.1 kV ) | 51 | 96 | 07.03.20 | DR0819_0001 |  |  | POWER SUPPLY (18.5kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
71 | 1TB | D3HQ025 | 10.4.18 | 1TB09CP01 | 415V SWGR O/G MODULE # 1TB09FC | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
72 | 1TB | D02Q010 | 10.4.06 | 1TB09DP01 | 415V SWGR O/G MODULE # 1TB09FD | SPLIT AC FOR CONTROL ROOM | 02C X 010 XLPE-Al FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY (4.5kW) |  | ES51-L1, ES93-R1, ER05-L1, ES43-R1, ES27-L1, ES26-L2, ES16-02, ZZ99- |  | EPD | PEM
73 | 1TB | D03L2.5 | 10.4.26 | 1TB09EP01 | 415V SWGR O/G MODULE # 1TB09FE | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 67 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
74 | 1TB | D04Q010 | 10.4.22 | 1TB09GP01 | 415V SWGR O/G MODULE # 1TB09FG | STRIP HEATER FOR AHU ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 51 | [5 empty] | POWER SUPPLY (8kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
75 | 1TB | D03L2.5 | 10.4.26 | 1TB09HP01 | 415V SWGR O/G MODULE # 1TB09FH | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 67 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
76 | 1TB | D3HQ025 | 10.4.18 | 1TB09QP01 | 415V SWGR O/G MODULE # 1TB09RC | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
77 | 1TB | D3HQ025 | 10.4.18 | 1TB09RP01 | 415V SWGR O/G MODULE # 1TB09RD | HOIST FOR ESP CONTROL ROOM (FOR HANDLING AT 12.4m FLOOR) (12 | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES94-L1, ES95-L2, ES79-L2, ES74-R1, ES73-R1, ES72-R1, ES71-01, ER04-01, ZZ99- |  | EPD | PEM
78 | 1TB | D04Q010 | 10.4.22 | 1TB09SP01 | 415V SWGR O/G MODULE # 1TB09RE | 2T A/C FOR ESP CONTROL ROOM BLDG ELEVATOR M/C ROOM | 04C X 010 XLPE-Al FRLS ( 1.1 kV ) | 46 | [5 empty] | POWER SUPPLY (7kW) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | PEM
79 | 1TB | D03L2.5 | 10.4.26 | 1TB09TP01 | 415V SWGR O/G MODULE # 1TB09RF | EXHAUST AIR FAN FOR 24V BATTERY ROOM | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 48 | 67 | 12.03.20 | DR2450_N-467 |  |  | POWER SUPPLY (0.55kW) |  | ES51-L3, ES93-R2, ER05-L2, ES50-02, ER10-02, ZZ99- |  | EPD | PEM
80 | 1TB | D02C1.5 | 10.5.01 | 1TB09UC01 | 415V SWGR MOTOR MODULE # 1TB09RG | EMERGENCY STOP PB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | EM.STOP NOT OPERATED |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | EPD
81 | 1TB | D03L2.5 | 10.4.26 | 1TB09UP01 | 415V SWGR MOTOR MODULE # 1TB09RG | CLEAR WATER TRANSFER PUMP (P2B) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | POWER SUPPLY (3.7kW) |  | ES51-L3, ES93-R2, ER05-L2, ES43-R2, ES14-02, ES15-02, ES16-02, ES96-02, ES01-L3, IR25-L3, IM63-L3, ZZ99- |  | EPD | PEM
82 | 1TB | D3HQ025 | 10.4.18 | 1TB09VP01 | 415V SWGR O/G MODULE # 1TB09RH | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
83 | 1TB | D3HQ025 | 10.4.18 | 1TB09WP01 | 415V SWGR O/G MODULE # 1TB09RI | AC FUSE DB | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY (63A) |  | SITE ROUTING |  | EPD | EPD
84 | 1TB | D3HQ025 | 10.4.18 | 1TB09XP01 | 415V SWGR O/G MODULE # 1TB09RJ | AC FUSE DB FOR MARINE LAMP/ FIRE DAMPER/ EXPANSION VALVE | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | 66 | [5 empty] | POWER SUPPLY (63A) |  | ES51-L1, ES93-R1, ER05-L1, ES50-01, ER10-01, ZZ99- |  | EPD | EPD
84 | 1TB | E04V0.5 | 10.7.02 | CVP63-LTUD-VNT-C001 | 1TB-1FA | CVP-63 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 80 | 44 | 14.03.2020 | DR0817_4798-4G-90
84 | 1TB | E04V0.5 | 10.7.02 | CVP63-LTUD-VNT-C002 | 1TB-2FC | CVP-63 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 80 | 43 | 14.03.2020 | DR0817_4798-4G-90
84 | 1TB | E04V0.5 | 10.7.02 | CVP63-LTUD-VNT-C003 | 1TB-7RG | CVP-63 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 80 | 47 | 14.03.2020 | DR0817_4798-4G-90
1 | 1GD | E04V0.5 | 10.7.02 | 1GD61AC01 | GRP-3 | DDCMIS CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
2 | 1GD | E04V0.5 | 10.7.02 | 1GD61AC02 | GRP-3 | DDCMIS CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
3 | 1GD | E04V0.5 | 10.7.02 | 1GD61AC03 | GRP-4 | DDCMIS CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
4 | 1GD | E04V0.5 | 10.7.02 | 1GD61AC04 | GRP-3 | DDCMIS CRE61 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
5 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC01 | DAVR | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 17 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC49-04 |  | EDN | EDN
6 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC02 | DAVR | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 17 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC49-04 |  | EDN | EDN
7 | 1GD | E08V0.5 | 10.7.04 | 1GD62AC03 | GCB Panel | DDCMIS CRE62 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 190 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | ZZ99- , TR37-02, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | PEM | EDN
8 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC04 | GCB Panel | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 190 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , TR37-02, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC51-04, CC50-04, CC49-04 |  | PEM | EDN
9 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC05 | GRP-2/4 | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
10 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC06 | GRP-4 | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
11 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC07 | GRP-3 | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
12 | 1GD | E08V0.5 | 10.7.04 | 1GD62AC08 | GRP-4 | DDCMIS CRE62 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
13 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC09 | GRP-1 | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
14 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC10 | GRP-3 | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
15 | 1GD | E08V0.5 | 10.7.04 | 1GD62AC11 | GRP-2 | DDCMIS CRE62 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
16 | 1GD | E04V0.5 | 10.7.02 | 1GD62AC12 | GRP-4 | DDCMIS CRE62 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 22 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC50-04, CC49-04 |  | BPL | EDN
17 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC01 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 25 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC45-03, CC46-03 |  | EDN | EDN
18 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC02 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | EDN | EDN
19 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC03 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | EDN | EDN
20 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC04 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 193 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , TR37-02, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | EDN | EDN
21 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC05 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 193 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , TR37-02, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | EDN | EDN
22 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC06 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 193 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , TR37-02, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | EDN | EDN
23 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC07 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 193 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , TR37-02, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | EDN | EDN
24 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC08 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 207 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , IP12-05, IP11-05, IP10-05, IP09-05, IP07-05, IR02-05, IP02-R5, IP01-R5, TY19-R3, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC69-04, CC45-03, CC46-03 |  | EDN | EDN
25 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC09 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 207 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , IP12-05, IP11-05, IP10-05, IP09-05, IP07-05, IR02-05, IP02-R5, IP01-R5, TY19-R3, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC69-04, CC45-03, CC46-03 |  | EDN | EDN
26 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC10 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 207 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , IP12-05, IP11-05, IP10-05, IP09-05, IP07-05, IR02-05, IP02-R5, IP01-R5, TY19-R3, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC69-04, CC45-03, CC46-03 |  | EDN | EDN
27 | 1GD | E08V0.5 | 10.7.04 | 1GD64AC11 | DAVR | DDCMIS CRE64 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 181 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | ZZ99- , IP09-05, IP07-05, IR02-05, IP02-R5, IP01-R5, TY19-R3, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC60-05, CC46-03 |  | EDN | EDN
28 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC12 | DAVR | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 181 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ZZ99- , IP09-05, IP07-05, IR02-05, IP02-R5, IP01-R5, TY19-R3, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC60-05, CC46-03 |  | EDN | EDN
29 | 1GD | E08V0.5 | 10.7.04 | 1GD64AC13 | DAVR | DDCMIS CRE64 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 181 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | ZZ99- , IP09-05, IP07-05, IR02-05, IP02-R5, IP01-R5, TY19-R3, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC60-05, CC46-03 |  | EDN | EDN
30 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC14 | GCB Panel | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 157 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | PEM | EDN
31 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC15 | GCB Panel | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 157 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | PEM | EDN
32 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC16 | GCB Panel | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 157 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | PEM | EDN
33 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC17 | GCB Panel | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 157 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | PEM | EDN
34 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC18 | GRP-2/4 | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 157 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | BPL | EDN
35 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC19 | STANDBY DG CP | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 157 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | ISG | EDN
36 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC20 | STANDBY DG CP | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | ISG | EDN
37 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC21 | STANDBY DG CP | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | ISG | EDN
38 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC22 | UNIT DG CP | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | ISG | EDN
39 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC23 | UNIT DG CP | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | ISG | EDN
40 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC24 | UNIT DG CP | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | ISG | EDN
41 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC25 | UT 1A CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC89-04, CC52-04, CC44-03, CC45-03, CC46-03 |  | JHS | EDN
42 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC26 | UT 1A CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
43 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC27 | UT 1A CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
44 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC28 | UT 1A CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 53 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | LV10-R4, LV43-04, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC35-03, CC59-05, CC39-03 |  | JHS | EDN
45 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC29 | UT 1A CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
46 | 1GD | E08V0.5 | 10.7.04 | 1GD64AC30 | UT 1A CCC | DDCMIS CRE64 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 83 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | MV15-03, MV14-03, MV92-04, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
47 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC31 | UT 1B CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | MV19-03, MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03 |  | JHS | EDN
48 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC32 | UT 1B CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 159 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
49 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC33 | UT 1B CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 159 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY10-03, TY09-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
50 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC34 | UT 1B CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | JHS | EDN
51 | 1GD | E04V0.5 | 10.7.02 | 1GD64AC35 | UT 1B CCC | DDCMIS CRE64 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | JHS | EDN
52 | 1GD | E08V0.5 | 10.7.04 | 1GD64AC36 | UT 1B CCC | DDCMIS CRE64 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 148 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
53 | 1GD | E04V0.5 | 10.7.02 | 1GD65AC01 | 220V CHG-1A | DDCMIS CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 148 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY08-03, TY02-05, TY01-05, YR01-04, TY11-R4, TY12-R4, TY13-R4, LR01-04, LV01-03, LV02-R4, LV03-R4, LV04-R4, LV05-R4, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | PEM | EDN
54 | 1GD | E04V0.5 | 10.7.02 | 1GD65AC02 | 220V CHG-1A | DDCMIS CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 77 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | MV83-03, MV30-R2, MV29-R2, MV28-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | PEM | EDN
55 | 1GD | E04V0.5 | 10.7.02 | 1GD65AC03 | 220V CHG-1B | DDCMIS CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | MV65-06, MV28-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | PEM | EDN
56 | 1GD | E04V0.5 | 10.7.02 | 1GD65AC04 | 220V CHG-1B | DDCMIS CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | MV89-04, MV32-R2, MV31-R2, MV30-R2, MV29-R2, MV28-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | PEM | EDN
57 | 1GD | E04V0.5 | 10.7.02 | 1GD65AC05 | BTS-1 1CA - 0CA | DDCMIS # CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | MV71-04, MV29-R2, MV28-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03, CC39-03, ZZ99- |  | BPL | EDN
58 | 1GD | E04V0.5 | 10.7.02 | 1GD65AC06 | BTS-2 1CB - 0CA | DDCMIS CRE65 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 273 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | ES55-R3, ES54-R3, ES53-R3, ES90-03, ER06-03, ES44-R3, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03 |  | BPL | EDN
59 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC01 | UT 1A CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 249 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | ES74-R3, ES76-03, ER01-03, ES30-03, ES02-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03 |  | JHS | EDN
60 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC02 | UT 1A CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 255 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | ES52-R3, ES93-R3, ER05-L3, ES43-R3, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03 |  | JHS | EDN
61 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC03 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 268 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | ES70-R3, ES72-R3, ES73-R3, ES74-R3, ES76-03, ER01-03, ES30-03, ES02-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM08-03, IR20-03, CC07-04, CC08-04, CC17-04, CC18-04, CC27-04, CC28-04, CC37-04, CC38-04, CC39-03 |  | JHS | EDN
62 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC04 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 341 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CT11-03, IP37-R4, IP36-R4, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IR38-L2, IP19-L2, IP18-L2, IP17-L2, IP16-L2, IP15-L2, IP14-R3, IR03-L2, IP02-L4, IP01-L4, TY19-L2, TY18-L2, TY17-L3, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | JHS | EDN
63 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC05 | UT 1B CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 333 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CT10-03, IP36-R4, IP34-R4, IP33-L8, IP32-L3, IP31-L3, IP30-L3, IP29-L3, IP28-L3, IP27-L8, IP26-L3, IP25-L3, IP24-L3, IP23-L3, IR38-L2, IP19-L2, IP18-L2, IP17-L2, IP16-L2, IP15-L2, IP14-R3, IR03-L2, IP02-L4, IP01-L4, TY19-L2, TY18-L2, TY17-L3, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC68-04, CC40-03, CC39-03 |  | JHS | EDN
64 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC06 | UT 1B CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 48 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
65 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC07 | 0DAT01 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 48 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, CC39-03 |  | JHS | EDN
66 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC08 | 1DAT01 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 24 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC50-04, CC61-05, CC60-05, CC39-03 |  | JHS | EDN
67 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC09 | 0DAT02 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 24 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC50-04, CC61-05, CC60-05, CC39-03 |  | JHS | EDN
68 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC10 | 1DAT02 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 24 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC50-04, CC61-05, CC60-05, CC39-03 |  | JHS | EDN
69 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC11 | 1DBT01 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 24 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC50-04, CC61-05, CC60-05, CC39-03 |  | JHS | EDN
70 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC12 | 1DBT02 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | JHS | EDN
71 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC13 | 1DBT03 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | JHS | EDN
72 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC14 | 1DBT04 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | JHS | EDN
73 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC15 | 1DCT01 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 342 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC39-03, CC59-05, CC58-05, CC30-03, CC31-03, CC81-04, CC90-04, LR07-04, LV74-04, LV26-R4, LV27-R4, LV41-04, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV34-R4, LV33-R4, LV70-04, LR04-04, TY17-R4, TY18-R3, TY19-R3, IP01-R5, IP02-R5, IR03-R3, IP14-L3, IP15-R3, IP16-R3, IP17-R3, IP18-R3, IP19-R3, IR38-R3, IP23-R4, IP24-R4, IP25-R4, IP26-R4, IP27-L8, IP28-L3, IP29-L3, IP30-L3, IP31-L3, IP32-L3, IP33-L8, IP34-L3, IP36-L3, IP37-L3, CT11-03, ZZ99- |  | JHS | EDN
74 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC16 | 1DCT02 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | JHS | EDN
75 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC17 | 220V CHG-A | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | PEM | EDN
76 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC18 | 220V CHG-B | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | PEM | EDN
77 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC19 | DAVR | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EDN | EDN
78 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC20 | DAVR | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EDN | EDN
79 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC21 | DAVR | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EDN | EDN
80 | 1GD | E04W0.5 | 10.8.02 | 1GD66AC22 | DAVR | DDCMIS CRE66 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 28 | [5 empty] | MEASUREMENT | 04P x 0.5 Paired Screened (I) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | EDN | EDN
81 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC23 | GRP-2 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
82 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC24 | GRP-3 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
83 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC25 | GRP-1 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
84 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC26 | GRP-4 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
85 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC27 | GRP-4 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
86 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC28 | GRP-2 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
87 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC29 | GRP-1 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
88 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC30 | GRP-4 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | BPL | EDN
89 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC31 | GRP-1 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | BPL | EDN
90 | 1GD | E08V0.5 | 10.7.04 | 1GD66AC32 | GRP-3 | DDCMIS CRE66 | 08P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 08P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | BPL | EDN
91 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC33 | GRP-2 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | BPL | EDN
92 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC34 | GRP-1 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | BPL | EDN
93 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC35 | GRP-4 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | TY27-03, TY26-04, TY25-04, YR02-04, TY18-R3, TY17-R4, LR04-04, LV70-04, LV33-R4, LV34-R4, LV35-R4, LV36-R4, LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-03, CC67-04, CC35-03, CC59-05, CC39-03 |  | BPL | EDN
94 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC36 | GRP-1 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | BPL | EDN
95 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC37 | GRP-1 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | BPL | EDN
96 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC38 | GRP-3 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 28 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC51-04, CC70-04, CC69-04, CC40-03, CC39-03 |  | BPL | EDN
97 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC39 | GRP-1 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | BPL | EDN
98 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC40 | GRP-3 | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | BPL | EDN
99 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC41 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | JHS | EDN
100 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC42 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | JHS | EDN
101 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC43 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | JHS | EDN
102 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC44 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | JHS | EDN
103 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC45 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | JHS | EDN
104 | 1GD | E04V0.5 | 10.7.02 | 1GD66AC46 | ST 1 CCC | DDCMIS CRE66 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 21 | [5 empty] | STATUS | 04P x 0.5 Paired Screened (O) | CC50-04, CC61-05, CC46-03 |  | JHS | EDN
1 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC01 | GENERATOR RELAY PANEL -1 | LA & VT CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 188 | [5 empty] | PT1 WDG1 SUPPLY FOR PROTECTION & 60PT11 |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, TP36-02, TP37-02, TP38-02, ZZ99- |  | BPL | RUD
2 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC02 | GENERATOR RELAY PANEL-1 | ECP (T , AVT & RELAY PANEL) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | PT1 WDG1 SUPPLY FOR SYNCHRONIZING |  | CC51-03, CC89-03, CC92-03, LR05-03, ZZ99- |  | BPL | EDN
3 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC03 | GENERATOR RELAY PANEL-1 | LA & VT CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 189 | [5 empty] | PT1 WDG2 SUPPLY FOR PROTECTION & 60PT12 |  | CC51-02, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TR30-02, TP36-02, TP37-02, TP38-02, ZZ99- |  | BPL | RUD
4 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC04 | GENERATOR RELAY PANEL-1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | PT1 WDG2 SUPPLY FOR FREQUENCY TRANSDUCER MKA02FE001E |  | SITE ROUTING |  | BPL | EDN
5 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC05 | GENERATOR RELAY PANEL-1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | PT1 WDG2 SUPPLY FOR LOAD TRANSDUCER & LOAD SHEDDING RELAY |  | SITE ROUTING |  | BPL | EDN
6 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC06 | GENERATOR RELAY PANEL-1 | SP & VT CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | PT2 WDG1 SUPPLY FOR PROTECTION & 60PT21 |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TR36-02, ZZ99- |  | BPL | RUD
7 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC07 | GENERATOR RELAY PANEL-1 | ECP (T , AVT & RELAY PANEL) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | PT2 WDG1 SUPPLY FOR SYNCHRONIZING |  | CC51-03, CC89-03, CC92-03, LR05-03, ZZ99- |  | BPL | EDN
8 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC08 | GENERATOR RELAY PANEL-1 | SP & VT CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | PT2 WDG2 SUPPLY FOR PROTECTION & 60PT22 |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TR36-02, ZZ99- |  | BPL | RUD
9 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC09 | GENERATOR RELAY PANEL -1 | AVR THY CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | PT2 WDG2 SUPPLY FOR AVR AUTO-CHANNEL-1 |  | CC51-03, CC50-03 |  | BPL | EDN
10 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC10 | GENERATOR RELAY PANEL -1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | PT2 WDG2 SUPPLY FOR LOAD TRANSDUCER |  | SITE ROUTING |  | BPL | EDN
11 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC11 | GENERATOR RELAY PANEL -1 | SP & VT CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | PT3 WDG1 SUPPLY FOR PROTECTION & 60PT31 |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TR36-02, ZZ99- |  | BPL | RUD
12 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC12 | GENERATOR RELAY PANEL -1 | SP & VT CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | PT3 WDG2 SUPPLY FOR PROTECTION & 60PT32 |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TR36-02, ZZ99- |  | BPL | RUD
13 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC13 | GENERATOR RELAY PANEL -1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | PT3 WDG2 SUPPLY FOR PERFORMANCE TESTING |  | SITE ROUTING |  | BPL | EDN
14 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC14 | GENERATOR RELAY PANEL -1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | PT3 WDG2 SUPPLY FOR LOAD TRANSDUCER |  | SITE ROUTING |  | BPL | EDN
15 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC15 | GENERATOR RELAY PANEL -1 | ECP (T , AVT & RELAY PANEL) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | FOR METERING |  | CC51-03, CC89-03, CC92-03, LR05-03, ZZ99- |  | BPL | EDN
16 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC16 | GENERATOR RELAY PANEL -1 | AVR THY CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | PT3 WDG2 SUPPLY FOR AVR AUTO CHANNEL-2 |  | CC51-03, CC50-03 |  | BPL | EDN
17 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC17 | GENERATOR RELAY PANEL-1 | GEN NEUTRAL BUSDUCT MB1 (CT-2) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR1 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
18 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC18 | GENERATOR RELAY PANEL-1 | GEN NEUTRAL BUSDUCT MB1 (CT-2) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR1 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
19 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC19 | GENERATOR RELAY PANEL-1 | GEN PHASE BUSDUCT MB1 (CT-5) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR1 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
20 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC20 | GENERATOR RELAY PANEL -1 | GEN PHASE BUSDUCT MB1 (CT-5) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR1 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
21 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC21 | GENERATOR RELAY PANEL -1 | NG CUBICLE | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | 100% STATOR E/F PROTECTION (GR2) |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TG43-02, TG48-02, TR09-02, TG49-02, TG50-02, ZZ99- |  | BPL | RUD
22 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC22 | GENERATOR RELAY PANEL-1 | GT CCC (BCT 17) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | 87/51GT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
23 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC23 | GENERATOR RELAY PANEL-1 | GT CCC (BCT 17) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | 87/51GT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
24 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC24 | GENERATOR RELAY PANEL-1 | GT CCC (BCT 18) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | 87/51GT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
25 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC25 | GENERATOR RELAY PANEL-1 | GT CCC (BCT 18) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | 87/51GT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
26 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC26 | GENERATOR RELAY PANEL-1 | GT CCC (BCTN-16 CORE-2) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | 51NGT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
27 | 1GP | D02C1.5 | 10.5.01 | 1GP01AC27 | GENERATOR RELAY PANEL-1 | AVR FS CUBICLE | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | EXCITER FIELD CB AUX 'NO' CONTACT FOR GR1 PROTN INTERLOCK |  | CC51-03, CC50-03 |  | BPL | EDN
28 | 1GP | D02C1.5 | 10.5.01 | 1GP01AC28 | GENERATOR RELAY PANEL-1 | STEAM TURBINE CABINET | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | HP & LV ESV INTERLOCK FOR GEN GR1 PROTECTION FROM STC |  | SITE ROUTING |  | BPL | EDN
29 | 1GP | D05C2.5 | 10.5.07 | 1GP01AC29 | GENERATOR RELAY PANEL-1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | ST TRIPPING RELAY 1 (TURBINE TRIP TO GRP) |  | SITE ROUTING |  | BPL | EDN
30 | 1GP | D02C1.5 | 10.5.01 | 1GP01AC30 | GENERATOR RELAY PANEL -1 | STEAM TURBINE CABINET | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | ST TRIPPING RELAY 2 (TURBINE TRIP TO GRP) |  | SITE ROUTING |  | BPL | EDN
31 | 1GP | D02C1.5 | 10.5.01 | 1GP01AC31 | GENERATOR RELAY PANEL-1 | AVR FS CUBICLE | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | EXCITATION SYSTEM FAULT |  | CC51-03, CC50-03 |  | BPL | EDN
32 | 1GP | D02C1.5 | 10.5.01 | 1GP01AC32 | GENERATOR RELAY PANEL-1 | GT FIRE PROTECTION PANEL | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | GT FIRE PROTECTION |  | SITE ROUTING |  | BPL | BPL
33 | 1GP | D05C1.5 | 10.5.06 | 1GP01AC33 | GENERATOR RELAY PANEL-1 | GT CK | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | GT PROTECTION (OTI, PRV, OCTC TRIP) |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
34 | 1GP | D02C1.5 | 10.5.01 | 1GP01AC34 | GENERATOR RELAY PANEL-1 | 220KV BBRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 229 | [5 empty] | EHV MAIN BUS-1 PROTECTION |  | CC51-03, CC71-05, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-L4, LV42-03, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV70-03, LR04-03, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | TBG
35 | 1GP | D02C1.5 | 10.5.01 | 1GP01AC35 | GENERATOR RELAY PANEL-1 | 220kV BBRP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 229 | [5 empty] | EHV MAIN BUS-2 PROTECTION |  | CC51-03, CC71-05, CR01-L4, LR10-R3, LV77-03, LV75-03, LV24-L4, LV42-03, LV41-03, LV38-L4, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV70-03, LR04-03, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY28-02, TY29-02, TY30-02, TY31-02, TY32-02, TY34-02, TY35-02, ZZ99- |  | BPL | TBG
36 | 1GP | D05C1.5 | 10.5.06 | 1GP01AC36 | GENERATOR RELAY PANEL-1 | 220kV SWYD RP GT HV MAIN CB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV MAIN CB TC-1 INTERLOCK |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
37 | 1GP | D05C1.5 | 10.5.06 | 1GP01AC37 | GENERATOR RELAY PANEL-1 | 220kV SWYD RP GT HV MAIN CB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV MAIN CB TC-2 INTERLOCK |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
38 | 1GP | D05C1.5 | 10.5.06 | 1GP01AC38 | GENERATOR RELAY PANEL-1 | GT MB/ CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | GTMB POWER SUPPLY SOURCE 1 & 2 INTERLOCK |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
39 | 1GP | D05C2.5 | 10.5.07 | 1GP02AC01 | GENERATOR RELAY PANEL-2 | UT TAP OFF BUSDUCT MB2 (CT 10A) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 87/51NUTA PROT |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | RUD
40 | 1GP | D05C2.5 | 10.5.07 | 1GP02AC02 | GENERATOR RELAY PANEL-2 | UT CCC (BCTN 13A CORE-1) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 87/51NUTA PROT |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
41 | 1GP | D05C2.5 | 10.5.07 | 1GP02AC03 | GENERATOR RELAY PANEL -2 | UT TAP OFF BUSDUCT MB2 (CT 10B) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 87/51NUTB PROT |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | RUD
42 | 1GP | D05C2.5 | 10.5.07 | 1GP02AC04 | GENERATOR RELAY PANEL-2 | UT CCC (BCTN 13B CORE-1) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 87/51NUTB PROT |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
43 | 1GP | D02C1.5 | 10.5.01 | 1GP02AC05 | GENERATOR RELAY PANEL-2 | UT-A FIRE PROTECTION PANEL | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | UT-A FIRE PROTECTION |  | SITE ROUTING |  | BPL | JHS
44 | 1GP | D05C1.5 | 10.5.06 | 1GP02AC06 | GENERATOR RELAY PANEL-2 | UT-A CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 146 | [5 empty] | UT A PRV & OTI PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
45 | 1GP | D02C1.5 | 10.5.01 | 1GP02AC07 | GENERATOR RELAY PANEL-2 | UT-B FIRE PROTECTION PANEL | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | UT-B FIRE PROTECTION |  | SITE ROUTING |  | BPL | JHS
46 | 1GP | D05C1.5 | 10.5.06 | 1GP02AC08 | GENERATOR RELAY PANEL-2 | UT-B CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 135 | [5 empty] | UT B PRV & OTI PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | JHS
47 | 1GP | D05C1.5 | 10.5.06 | 1GP02AC09 | GENERATOR RELAY PANEL-2 | UT-A CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 146 | [5 empty] | UT A MK POWER SUPPLY SOURCE1 & 2 INTERLOCK |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
48 | 1GP | D05C1.5 | 10.5.06 | 1GP02AC10 | GENERATOR RELAY PANEL-2 | UT-B CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 135 | [5 empty] | UT B MK POWER SUPPLY SOURCE1 & 2 INTERLOCK |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | JHS
49 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC01 | GENERATOR RELAY PANEL-3 | GEN NEUTRAL BUSDUCT MB1 (CT-3) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR2 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
50 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC02 | GENERATOR RELAY PANEL-3 | GEN NEUTRAL BUSDUCT MB1 (CT-3) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR2 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
51 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC03 | GENERATOR RELAY PANEL-3 | GEN PHASE BUSDUCT MB2 (CT-6) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR2 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
52 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC04 | GENERATOR RELAY PANEL-3 | GEN PHASE BUSDUCT MB2 (CT-6) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | GR2 PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
53 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC05 | GENERATOR RELAY PANEL-3 | NG CUBICLE (CT 9) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | 100% STATOR E/F PROTECTION (GR2) |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, TG24-03, TG25-03, TG26-03, TG27-03, TG28-03, TR05-03, TG29-03, TG30-03, TG36-03, TG37-03, TG38-03, TG43-02, TG48-02, TR09-02, TG49-02, TG50-02, ZZ99- |  | BPL | RUD
54 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC06 | GENERATOR RELAY PANEL-3 | GENERATOR EXCITER | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | FOR ROTOR E/F (GR2) |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | HWR
55 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC07 | GENERATOR RELAY PANEL-3 | GT CCC (BCTN-16 CORE-1) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | 64R/59NGT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
56 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC08 | GENERATOR RELAY PANEL-3 | 220kV SWYD (CT) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | 64R/59NGT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
57 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC09 | GENERATOR RELAY PANEL -3 | GCB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | PROTECTION TRIP TO GCB TC-2 |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, ZZ99- |  | BPL | PEM
58 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC10 | GENERATOR RELAY PANEL-3 | GCB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | PROTECTION TRIP TO GCB CLOSING CKT |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, ZZ99- |  | BPL | PEM
59 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC11 | GENERATOR RELAY PANEL-3 | AVR FS CUBICLE | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | EXCITER FIELD CB AUX 'NO' CONTACT FOR GR2 PROTN INTERLOCK |  | CC51-02, CC50-03 |  | BPL | EDN
60 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC12 | GENERATOR RELAY PANEL-3 | STEAM TURBINE CABINET | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | HP & LV ESV INTERLOCK FOR GEN GR2 PROTECTION FROM STC |  | SITE ROUTING |  | BPL | EDN
61 | 1GP | D05C2.5 | 10.5.07 | 1GP03AC13 | GENERATOR RELAY PANEL-3 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | ST TRIPPING RELAY 1 (TURBINE TRIP TO GRP) |  | SITE ROUTING |  | BPL | EDN
62 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC14 | GENERATOR RELAY PANEL-3 | STEAM TURBINE CABINET | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | ST TRIPPING RELAY 2 (TURBINE TRIP TO GRP) |  | SITE ROUTING |  | BPL | EDN
63 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC15 | GENERATOR RELAY PANEL-3 | AVR FS CUBICLE | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | EXCITATION SYSTEM FAULT |  | CC51-02, CC50-03 |  | BPL | EDN
64 | 1GP | D05C1.5 | 10.5.06 | 1GP03AC16 | GENERATOR RELAY PANEL-3 | GCB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 175 | [5 empty] | GCB CLOSE/ OPEN CONTACT MULTIPLICATION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, ZZ99- |  | BPL | PEM
65 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC17 | GENERATOR RELAY PANEL-3 | 220kV SWYD RP GT HV MAIN CB | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV MAIN CB LBB INTERLOCK |  | CC51-02, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
66 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC18 | GENERATOR RELAY PANEL-3 | STEAM TURBINE CABINET | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | STEAM TURBINE TRIP |  | SITE ROUTING |  | BPL | EDN
67 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC19 | GENERATOR RELAY PANEL-3 | STEAM TURBINE CABINET | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | STEAM TURBINE TRIP |  | SITE ROUTING |  | BPL | EDN
68 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC20 | GENERATOR RELAY PANEL-3 | STEAM TURBINE CABINET | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | STEAM TURBINE TRIP |  | SITE ROUTING |  | BPL | EDN
69 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC21 | GENERATOR RELAY PANEL-3 | 220kV SWYD GT HV MAIN CB BAY | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | LBB PROTECTION SCHEME (PU201A) |  | CC51-02, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
70 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC22 | GENERATOR RELAY PANEL-3 | 220kV SWYD GT HV MAIN CB BAY | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | LBB PROTECTION SCHEME (PU201B) |  | CC51-02, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
71 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC23 | GENERATOR RELAY PANEL-3 | AVR FS CUBICLE | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | DEEXCITATION |  | CC51-02, CC50-03 |  | BPL | EDN
72 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC24 | GENERATOR RELAY PANEL-3 | AVR FS CUBICLE | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | DEEXCITATION |  | CC51-02, CC50-03 |  | BPL | EDN
73 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC25 | GENERATOR RELAY PANEL-3 | 220kV SWYD CP | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | 186/286 TRIPPING ANNUN |  | CC51-02, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
74 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC26 | GENERATOR RELAY PANEL-3 | 220kV SWYD GT HV MIDDLE CB BAY | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV CB CLOSING CKT |  | CC51-02, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
75 | 1GP | D02C1.5 | 10.5.01 | 1GP03AC27 | GENERATOR RELAY PANEL-3 | AVR | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FIELD CB CLOSING CKT |  | CC51-02, CC50-03 |  | BPL | EDN
76 | 1GP | D05C1.5 | 10.5.06 | 1GP03AC28 | GENERATOR RELAY PANEL -3 | AVR | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | GT HV CB OPEN & CLOSE STATUS |  | CC51-03, CC50-03 |  | BPL | EDN
77 | 1GP | D05C1.5 | 10.5.06 | 1GP03AC29 | GENERATOR RELAY PANEL-3 | ATRS | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | GT HV CB CLOSE/OPEN STATUS |  | SITE ROUTING |  | BPL | EDN
78 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC01 | GENERATOR RELAY PANEL-4 | 220kV SWYD CT | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | 51GT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
79 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC02 | GENERATOR RELAY PANEL-4 | GEN PHASE BUSDUCT MB-1 (CT 4) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | 87OA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
80 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC03 | GENERATOR RELAY PANEL-4 | GEN PHASE BUSDUCT MB-1 (CT 4) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | 87OA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
81 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC04 | GENERATOR RELAY PANEL-4 | UT TAP OFF BUSDUCT MB-2 (CT 12A) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 87OA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | RUD
82 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC05 | GENERATOR RELAY PANEL-4 | UT TAP OFF BUSDUCT MB-2 (CT 12A) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 87OA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | RUD
83 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC06 | GENERATOR RELAY PANEL-4 | UT TAP OFF BUSDUCT MB-2 (CT 12B) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | 87OA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | RUD
84 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC07 | GENERATOR RELAY PANEL -4 | UT TAP OFF BUSDUCT MB-2 (CT 12B) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | 87OA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | RUD
85 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC08 | GENERATOR RELAY PANEL -4 | 220kV SWYD | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | 87OA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
86 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC09 | GENERATOR RELAY PANEL -4 | UT TAP OFF BUSDUCT MB-2 (CT 11A) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 50/51/64RUTA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | RUD
87 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC10 | GENERATOR RELAY PANEL -4 | UT CCC (BCTN 13A, CORE-2) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 50/51/64RUTA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
88 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC11 | GENERATOR RELAY PANEL-4 | UT CCC (BCTN 13A, CORE-2) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | 50/51/64RUTA PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
89 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC12 | GENERATOR RELAY PANEL-4 | UT TAP OFF BUSDUCT MB-2 (CT 11B) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | 50/51/64RUTB PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | RUD
90 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC13 | GENERATOR RELAY PANEL -4 | UT CCC (BCTN 13B, CORE-2) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | 50/51/64RUTB PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | JHS
91 | 1GP | D05C2.5 | 10.5.07 | 1GP04AC14 | GENERATOR RELAY PANEL -4 | UT CCC (BCTN 13B, CORE-2) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | 50/51/64RUTB PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | JHS
92 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC15 | GENERATOR RELAY PANEL-4 | GT CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | GT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
93 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC16 | GENERATOR RELAY PANEL-4 | UT-A CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 146 | [5 empty] | UT-A PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
94 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC17 | GENERATOR RELAY PANEL-4 | UT-A CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 146 | [5 empty] | UT-A PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | BPL | JHS
95 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC18 | GENERATOR RELAY PANEL-4 | UT-B CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 135 | [5 empty] | UT-B PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | JHS
96 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC19 | GENERATOR RELAY PANEL-4 | UT-B CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 135 | [5 empty] | UT-B PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | BPL | JHS
97 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC20 | GENERATOR RELAY PANEL -4 | GT MB/ CCC | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 166 | [5 empty] | GT PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY03-02, TY04-02, TY05-02, TY06-02, TY07-02, ZZ99- |  | BPL | BPL
98 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC21 | GENERATOR RELAY PANEL-4 | 220kV SWYD GT HV MAIN CB BAY | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV CB CLOSE/ OPEN CONTACT MULTIPLICATION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
99 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC22 | GENERATOR RELAY PANEL-4 | 220kV SWYD RP GT HV MAIN CB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV MAIN CB ISOL (89L) CONTACT MULTIPLICATION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
100 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC23 | GENERATOR RELAY PANEL-4 | 230kV SWYD RP GT HV MAIN CB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV MAIN CB ISOL (89A) CONTACT MULTIPLICATION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
101 | 1GP | D05C1.5 | 10.5.06 | 1GP04AC24 | GENERATOR RELAY PANEL-4 | 220kV SWYD RP GT HV MAIN CB | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | GT HV MAIN CB ISOL (89B) CONTACT MULTIPLICATION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
102 | 1GP | D02C1.5 | 10.5.01 | 1GP04AC25 | GENERATOR RELAY PANEL-4 | 220kV SWYD GT HV MAIN CB BAY | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | POLE DISC PROTECTION |  | CC51-02, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, ZZ99- |  | BPL | TBG
103 | 1GP | D05C2.5 | 10.5.07 | 1GP05AC01 | GENERATOR RELAY PANEL- 5 | GEN PHASE BUSDUCT MB-1 | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | CT-8 SUPPLY FOR METERING & PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, LV76-03, LV07-L4, LV06-L4, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP15-02, TP16-02, TP17-02, TP18-02, TP19-02, TP22-02, TP27-02, TP28-02, TP29-02, TP30-02, TP31-02, TP32-02, TP34-02, TP35-02, TP40-02, TR37-01, ZZ99- |  | BPL | RUD
104 | 1GP | D05C2.5 | 10.5.07 | 1GP05AC02 | GENERATOR RELAY PANEL- 5 | ECP (T , AVT & RELAY PANEL) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | CT-8 SUPPLY FOR METERING & PROTECTION |  | CC51-03, CC89-03, CC92-03, LR05-03, ZZ99- |  | BPL | EDN
1 | ECP | E08V0.5 | 10.7.04 | 1EC01AC01 | GRP-5 | ELECTRICAL CONTROL PANEL (CWB01) | 08P X 0.5 Paired Screened(O) ( 225 V ) | 53 | [5 empty] | DISTURBANCE RECORDER CHANNEL FOR MW, MVAR & Hz | 08P x 0.5 Paired Screened(O) | CC51-04, CC89-04, CC88-02, CC86-04, CC84-04, CC83-02, CC91-04, ZZ99- |  | BPL | EDN
2 | ECP | D05C2.5 | 10.5.07 | 1EC01AC02 | STEAM TURBINE CABINET | ELECTRICAL CONTROL PANEL (CWB01) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CT-8 SUPPLY FOR LOAD TRANSDUCER | 5C X 2.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | SITE ROUTING |  | EDN | EDN
3 | ECP | D05C2.5 | 10.5.07 | 1EC01AC03 | 220 kV SYWD CONTROL PANEL | ELECTRICAL CONTROL PANEL (CWB01) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 258 | [5 empty] | 220 kV GIS BUS-I CVT (209-B-VT) SUPPLY FOR METERING | 5C X 2.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | ZZ99- , TY35-02, TY34-02, TY32-02, TY31-02, TY30-02, TY29-02, TY28-02, TY26-03, TY25-03, YR02-03, TY18-L3, TY17-L4, LR04-03, LV70-03, LV33-L4, LV34-L4, LV35-L4, LV36-L4, LV37-L4, LV46-04, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC73-03, CC75-03, CC77-03, CC79-03, CC81-03, CC33-03, CC34-02, CC68-03, CC69-03, CC70-03, CC51-02, ZZ99- |  | TBG | EDN
4 | ECP | D05C2.5 | 10.5.07 | 1EC01AC04 | 220 kV SYWD CONTROL PANEL | ELECTRICAL CONTROL PANEL (CWB01) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 258 | [5 empty] | 220 kV GIS BUS-II CVT (210-B-VT) SUPPLY FOR METERING | 5C X 2.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | ZZ99- , TY35-02, TY34-02, TY32-02, TY31-02, TY30-02, TY29-02, TY28-02, TY26-03, TY25-03, YR02-03, TY18-L3, TY17-L4, LR04-03, LV70-03, LV33-L4, LV34-L4, LV35-L4, LV36-L4, LV37-L4, LV46-04, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC73-03, CC75-03, CC77-03, CC79-03, CC81-03, CC33-03, CC34-02, CC68-03, CC69-03, CC70-03, CC51-02, ZZ99- |  | TBG | EDN
5 | ECP | D05C2.5 | 10.5.07 | 1EC01AC05 | UT-1A BUS-DUCT MB-2 | ELECTRICAL CONTROL PANEL (CWB01) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 224 | [5 empty] | CT-19A SUPPLY FOR METERING | 5C X 2.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | ZZ99- , TY10-02, TY09-02, TY02-04, TY01-04, YR01-03, TY11-L4, TY12-L4, TY13-L4, LR01-03, MR01-03, MV01-03, MV02-R1, MV98-04, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV68-05, MA05-03, MR10-03, LR05-02, CC92-02, CC88-03, CC86-03, CC84-03, CC83-03, CC91-03, ZZ99- |  | JHS | EDN
6 | ECP | D05C2.5 | 10.5.07 | 1EC01AC06 | UT-1B BUS-DUCT MB-2 | ELECTRICAL CONTROL PANEL (CWB01) | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 214 | [5 empty] | CT-19B SUPPLY FOR METERING | 5C X 2.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | ZZ99- , TY08-02, TY02-04, TY01-04, YR01-03, TY11-L4, TY12-L4, TY13-L4, LR01-03, MR01-03, MV01-03, MV02-R1, MV98-04, MV14-02, MV13-02, MV12-02, MV11-02, MV10-02, MV68-05, MA05-03, MR10-03, LR05-02, CC92-02, CC88-03, CC86-03, CC84-03, CC83-03, CC91-03, ZZ99- |  | JHS | EDN
7 | ECP | D02C1.5 | 10.5.01 | 1EC01AC07 | 220 kV SYWD CONTROL PANEL | ELECTRICAL CONTROL PANEL (CWB02) | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 244 | [5 empty] | 220 kV GIS GT-1 CVT (201-VT) SUPPLY FOR SYNCHRONIZATION | 2C X 1.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | ZZ99- , TY35-02, TY34-02, TY32-02, TY31-02, TY30-02, TY29-02, TY28-02, TY26-03, TY25-03, YR02-03, TY18-L3, TY17-L4, LR04-03, LV70-03, LV33-L4, LV34-L4, LV35-L4, LV36-L4, LV37-L4, LV46-04, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC73-03, CC75-03, CC77-03, CC79-03, CC81-03, CC82-02, CC91-03, ZZ99- |  | TBG | EDN
8 | ECP | D02C1.5 | 10.5.01 | 1EC01AC08 | 220 kV SYWD CONTROL PANEL | ELECTRICAL CONTROL PANEL (CWB02) | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 244 | [5 empty] | 220 kV SELECTED BUS CVT SUPPLY FOR SYNCHRONIZATION FOR 1AA01 | 2C X 1.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | ZZ99- , TY35-02, TY34-02, TY32-02, TY31-02, TY30-02, TY29-02, TY28-02, TY26-03, TY25-03, YR02-03, TY18-L3, TY17-L4, LR04-03, LV70-03, LV33-L4, LV34-L4, LV35-L4, LV36-L4, LV37-L4, LV46-04, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC73-03, CC75-03, CC77-03, CC79-03, CC81-03, CC82-02, CC91-03, ZZ99- |  | TBG | EDN
9 | ECP | D05C1.5 | 10.5.06 | 1EC01AC09 | TURBINE CONTROL PANEL | ELECTRICAL CONTROL PANEL (CWB02) | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | TO 25A FOR SYNCHRONIZATION | 5C X 1.5 PVC-Cu(UA) FRLS ( 1.1 kV ) | SITE ROUTING |  | EDN | EDN
1 | DAVR | E04W0.5 | 10.8.02 | 1AV01AC01 | DAVR | ELECTRICAL CONTROL DESK - 1 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 62 | [5 empty] | METERING | 04P X 0.5 Paired Screen (I) ( 225V ) | CC50-04, CC61-05, CC60-05, CC59-04, CC58-04, CC57-04, CC25-03, CC24-03, CC80-03, CC81-02, CC82-03, CC91-02, ZZ99- |  | EDN | EDN
2 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC02 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
3 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC03 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
4 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC04 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
5 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC05 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
6 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC06 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
7 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC07 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
8 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC08 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
9 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC09 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
10 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC10 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
11 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC11 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
12 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC12 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
13 | DAVR | D12C1.5 | 10.5.12 | 1AV01AC13 | DAVR | ELECTRICAL CONTROL DESK - 1 | 12C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | INDICATION | 12C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
14 | DAVR | D05C2.5 | 10.5.07 | 1AV01AC14 | GEN NEUTRAL BUS-DUCT MB1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | CT1 SUPPLY FOR LOAD TRANSDUCER | 5C X 2.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , TR37-01, TP40-02, TR30-02, TP36-02, TP37-02, TP38-02, TP39-02, TR38-01, TY39-03, TY38-03, TY37-03, TY36-03, TY11-L4, TY12-L4, TY13-L4, TY14-L4, LR02-03, LV71-03, LV18-L4, LV19-L4, LV20-L4, LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC24-02, CC25-02, CC57-03, ZZ99- |  | EDN | EDN
15 | DAVR | D05C2.5 | 10.5.07 | 1AV01AC15 | GEN PHASE BUS-DUCT MB1 | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | CT7A SUPPLY FOR AVR LOAD TRANSDUCER & LOAD SHEDDING RELAY | 5C X 2.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , TR37-01, TP40-02, TR30-02, TP36-02, TP37-02, TP38-02, TP39-02, TR38-01, TY39-03, TY38-03, TY37-03, TY36-03, TY11-L4, TY12-L4, TY13-L4, TY14-L4, LR02-03, LV71-03, LV18-L4, LV19-L4, LV20-L4, LV21-L4, LV22-L4, LV23-L4, LV24-L3, LV25-L4, LV74-03, LR07-03, CC90-03, CC80-02, CC24-02, CC25-02, CC57-03, ZZ99- |  | EDN | EDN
16 | DAVR | D05C2.5 | 10.5.07 | 1AV01AC16 | DAVR | STEAM TURBINE CABINET | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | CT7A SUPPLY FOR AVR AUTO CHANNEL-1 | 5C X 2.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | SITE ROUTING |  | EDN | EDN
17 | DAVR | D05C2.5 | 10.5.07 | 1AV01AC17 | DAVR | GEN PHASE BUS-DUCT MB1 | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 172 | [5 empty] | CT7B SUPPLY FOR AVR AUTO CHANNEL-2 | 5C X 2.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC50-03, CC51-02, CC89-02, CC92-02, LR05-02, LV76-04, LV07-L4, LV06-L3, LV05-L4, LV04-L4, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-01, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, ZZ99- |  | EDN | EDN
18 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC18 | DAVR | STEAM TURBINE CABINET | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GEN VOLTAGE >90% | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | SITE ROUTING |  | EDN | EDN
19 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC19 | DAVR | STEAM TURBINE CABINET | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GEN SPEED >90% | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | SITE ROUTING |  | EDN | EDN
20 | DAVR | D03L2.5 | 10.4.26 | 1AV01AC20 | DAVR | QUADRATURE AXIS COIL | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 185 | [5 empty] | QUADRATURE AXIS COIL VOLTAGE | 3C X 2.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC50-03, CC51-02, CC89-02, CC92-02, LR05-02, LV76-04, LV07-L4, LV06-L3, LV05-L4, LV04-L3, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-01, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP40-02, TR37-01, ZZ99- |  | EDN | EDN
21 | DAVR | D12C1.5 | 10.5.12 | 1AV01AC21 | DAVR | STEAM TURBINE CABINET | 12C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GEN. VOLATGE LOWER RAISE COMMAND | 12C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | SITE ROUTING |  | EDN | EDN
22 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC22 | DAVR | ELECTRICAL CONTROL DESK - 1 | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 64 | [5 empty] | FB AUTO TRIP | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | CC50-03, CC61-04, CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC81-03, CC82-02, CC91-03, ZZ99- |  | EDN | EDN
23 | DAVR | D12C1.5 | 10.5.12 | 1AV01AC23 | DAVR | INTERPOSING RELAY PANEL- DDCMIS | 12C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | CH-1 /CH-2 RAISE/LOWER, EXCITATION ON | 12C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC50-03, CC61-04, CC60-04, ZZ99- |  | EDN | EDN
24 | DAVR | D12C1.5 | 10.5.12 | 1AV01AC24 | DAVR | INTERPOSING RELAY PANEL- DDCMIS | 12C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | EXCITATION OFF, CH-1/ CH-2 AUTO/ MANUAL | 12C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC50-03, CC61-04, CC60-04, ZZ99- |  | EDN | EDN
25 | DAVR | D05C1.5 | 10.5.06 | 1AV01AC25 | DAVR | INTERPOSING RELAY PANEL- DDCMIS | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | CH-1/ CH-2 ON | 5C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC50-03, CC61-04, CC60-04, ZZ99- |  | EDN | EDN
26 | DAVR | D12C1.5 | 10.5.12 | 1AV01AC26 | INTERPOSING RELAY PANEL- DDCMIS | UNIT DG CP | 12C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 208 | [5 empty] | START/ STOP, SPEED RAISE/ LOWER | 12C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC59-02, CC35-02, CC34-02, CC33-03, CC81-03, CC79-03, CC77-03, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L4, LV46-04, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, ZZ99- |  | EDN | EDN
27 | DAVR | D05C1.5 | 10.5.06 | 1AV01AC27 | INTERPOSING RELAY PANEL- DDCMIS | UNIT DG CP | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 213 | [5 empty] | VOLTAGE RAISE/ LOWER | 5C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC79-03, CC77-03, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L4, LV46-04, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, ZZ99- |  | EDN | EDN
28 | DAVR | D12C1.5 | 10.5.12 | 1AV01AC28 | INTERPOSING RELAY PANEL- DDCMIS | STAND-BY DG CP | 12C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 229 | [5 empty] | START/ STOP, SPEED RAISE/ LOWER | 12C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC59-02, CC35-02, CC34-02, CC33-03, CC81-03, CC79-03, CC77-03, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L4, LV46-04, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EDN | EDN
29 | DAVR | D05C1.5 | 10.5.06 | 1AV01AC29 | INTERPOSING RELAY PANEL- DDCMIS | STAND-BY DG CP | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 234 | [5 empty] | VOLTAGE RAISE/ LOWER | 5C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC79-03, CC77-03, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L4, LV46-04, LV37-L4, LV72-04, LR11-L3, TY24-L3, TY23-L3, TY22-L3, TY21-L3, TY20-L3, IP01-R4, IP02-R4, IR02-04, IP07-04, IP09-04, IP10-04, IP11-04, IP12-04, IP13-04, ZZ99- |  | EDN | EDN
30 | DAVR | D05C1.5 | 10.5.06 | 1AV01AC30 | INTERPOSING RELAY PANEL- DDCMIS | UT-1A OLTC DM | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 197 | [5 empty] | OLTC RAISE/ LOWER | 5C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV02-R1, MV01-03, MR01-03, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY09-02, TY10-02, ZZ99- |  | EDN | EDN
31 | DAVR | D05C1.5 | 10.5.06 | 1AV01AC31 | INTERPOSING RELAY PANEL- DDCMIS | UT-1B OLTC DM | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 186 | [5 empty] | OLTC RAISE/ LOWER | 5C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV02-R1, MV01-03, MR01-03, LR01-03, TY13-L4, TY12-L4, TY11-L4, YR01-03, TY01-04, TY02-04, TY08-02, ZZ99- |  | EDN | EDN
32 | DAVR | D05C1.5 | 10.5.06 | 1AV01AC32 | INTERPOSING RELAY PANEL- DDCMIS | ST-1 OLTC DM | 05C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 190 | [5 empty] | OLTC RAISE/ LOWER | 5C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC59-02, CC58-03, CC57-03, CC25-02, CC24-02, CC80-02, CC79-03, CC77-03, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L4, LV46-04, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV70-03, LR04-03, TY17-L4, TY18-L3, YR02-03, TY25-03, TY26-03, TY27-02, ZZ99- |  | EDN | EDN
33 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC33 | INTERPOSING RELAY PANEL- DDCMIS | 1CA I/C CB | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | UT-1A EMERGENCY STOP | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV13-02, MV14-02, MV98-04, MV02-R1, MV16-L2, ZZ99- |  | EDN | EDN
34 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC34 | INTERPOSING RELAY PANEL- DDCMIS | 1CB I/C CB | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | UT-1B EMERGENCY STOP | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV81-03, MV21-02, MV20-02, MV19-02, MV18-L2, ZZ99- |  | EDN | EDN
35 | DAVR | D03C1.5 | 10.5.03 | 1AV01AC35 | INTERPOSING RELAY PANEL- DDCMIS | 0CA I/C CB | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | ST-1 EMERGENCY STOP | 3C X 1.5 PVC-Cu (UA) FRLS ( 1.1 kV ) | ZZ99- , CC60-04, CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV12-02, MV81-03, MV80-03, MV79-03, MV39-02, MV38-02, ZZ99- |  | EDN | EDN
36 | DAVR | D03Q050 | NA | 1AV01AC36 | DAVR | EXCITER FIELD | 03C X 050 PVC-Cu FRLS ( 1.1 kV ) | 185 | [5 empty] | OUTPUT TO EXCITER FIELD | 03C X 050 PVC-Cu FRLS ( 1.1 kV )(EDN SCOPE) | ZZ99- , CC50-03, CC51-02, CC89-02, CC92-02, LR05-02, LV76-04, LV07-L4, LV06-L3, LV05-L4, LV04-L3, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-01, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP40-02, TR37-01, ZZ99- |  | EDN | EDN
37 | DAVR | D03Q050 | NA | 1AV01AC37 | DAVR | PMG | 03C X 050 PVC-Cu FRLS ( 1.1 kV ) | 185 | [5 empty] | PMG INPUT SUPPLY 220V, 3PH | 03C X 050 PVC-Cu FRLS ( 1.1 kV )(EDN SCOPE) | ZZ99- , CC50-03, CC51-02, CC89-02, CC92-02, LR05-02, LV76-04, LV07-L4, LV06-L3, LV05-L4, LV04-L3, LV03-L4, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, TR38-01, TP39-02, TP38-02, TP37-02, TP36-02, TR30-02, TP40-02, TR37-01, ZZ99- |  | EDN | EDN
38 | DAVR | D01C050 | NA | 1AV01AC38 | DAVR | SCREEN BUS | 01C X 050 PVC-Cu FRLS ( 1.1 kV ) | 70 | [9 empty] | EDN | EDN
39 | DAVR | D01C050 | NA | 1AV01AC39 | DAVR | ZERO BUS | 01C X 050 PVC-Cu FRLS ( 1.1 kV ) | 70 | [9 empty] | EDN | EDN
20 | HTUD BOP | E04V0.5 | 10.7.02 | CVP01-HT-D001 | 1HLB01AN001, SWBD.#1CA, PANEL 37, MF2 | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 39 | 51 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | FD-A | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | BPL | EDN
21 | HTUD BOP | E02W0.5 | 10.8.01 | CVP01-HT-D002 | 1HLB01AN001, SWBD.#1CA, PANEL 37, MF2 | CVP01, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 39 | 51 | 05.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | FD-A | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | BPL | EDN
20 | HTUD BOP | E04V0.5 | 10.7.02 | CVP01-HT-D001A | 1HLB01AN001, SWBD.#1CA, PANEL 37, MF2 | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 39 | 51 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | FD-A | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | BPL | EDN
39 | HTUD BOP | E04V0.5 | 10.7.02 | CVP02-HT-D001 | 1HLB02AN001, SWBD.#1CB, PANEL 2, MF2 | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 43 | 50 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | FD-B | ZZ99- , MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | BPL | EDN
40 | HTUD BOP | E02W0.5 | 10.8.01 | CVP02-HT-D002 | 1HLB02AN001, SWBD.#1CB, PANEL 2, MF2 | CVP02, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 43 | 54 | 02.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | FD-B | ZZ99- , MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | BPL | EDN
39 | HTUD BOP | E04V0.5 | 10.7.02 | CVP02-HT-D001A | 1HLB02AN001, SWBD.#1CB, PANEL 2, MF2 | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 43 | 50 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | FD-B | ZZ99- , MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | BPL | EDN
63 | HTUD BOP | E04V0.5 | 10.7.02 | CVP03-HT-D001 | 1HFE01AN001, SWBD.#1CA, PANEL 36, MF1 | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 45 | 54 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | PA-A | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | BPL | EDN
64 | HTUD BOP | E02W0.5 | 10.8.01 | CVP03-HT-D002 | 1HFE01AN001, SWBD.#1CA, PANEL 36, MF1 | CVP03, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 45 | 54 | 02.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | PA-A | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | BPL | EDN
63 | HTUD BOP | E04V0.5 | 10.7.02 | CVP03-HT-D001A | 1HFE01AN001, SWBD.#1CA, PANEL 36, MF1 | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 45 | 54 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | PA-A | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | BPL | EDN
94 | HTUD BOP | E04V0.5 | 10.7.02 | CVP04-HT-D001 | 1HFE02AN001, SWBD.#1CB, PANEL 3, MF1 | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 49 | 54 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | PA-B | ZZ99- , MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | BPL | EDN
95 | HTUD BOP | E02W0.5 | 10.8.01 | CVP04-HT-D002 | 1HFE02AN001, SWBD.#1CB, PANEL 3, MF1 | CVP04, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 49 | 55 | 02.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | PA-B | ZZ99- , MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | BPL | EDN
94 | HTUD BOP | E04V0.5 | 10.7.02 | CVP04-HT-D001A | 1HFE02AN001, SWBD.#1CB, PANEL 3, MF1 | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 49 | 54 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | PA-B | ZZ99- , MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | BPL | EDN
195 | HTUD BOP | E04V0.5 | 10.7.02 | CVP11-HT-D001 | 1LAC10AP001, SWBD.#1CA, PANEL 19, MFD1 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | 60 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | MDBFP-A | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
196 | HTUD BOP | E02W0.5 | 10.8.01 | CVP11-HT-D002 | 1LAC10AP001, SWBD.#1CA, PANEL 19, MFD1 | CVP11, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 61 | 62 | 02.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | MDBFP-A | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
195 | HTUD BOP | E04V0.5 | 10.7.02 | CVP11-HT-D001A | 1LAC10AP001, SWBD.#1CA, PANEL 19, MFD1 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | 60 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | MDBFP-A | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
197 | HTUD BOP | E04V0.5 | 10.7.02 | CVP11-HT-D003 | 1PCB31AP001, SWBD.#1CA, PANEL 23, MF5A | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | 58 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | ACW-A | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
198 | HTUD BOP | E02W0.5 | 10.8.01 | CVP11-HT-D004 | 1PCB31AP001, SWBD.#1CA, PANEL 23, MF5A | CVP11, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 61 | 70 | 02.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | ACW-A | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
197 | HTUD BOP | E04V0.5 | 10.7.02 | CVP11-HT-D003A | 1PCB31AP001, SWBD.#1CA, PANEL 23, MF5A | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | 58 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | ACW-A | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
199 | HTUD BOP | E04V0.5 | 10.7.02 | CVP11-HT-D005 | 1PCC11AP001, SWBD.#1CA, PANEL 10, MF3 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 72 | 70 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
200 | HTUD BOP | E02W0.5 | 10.8.01 | CVP11-HT-D006 | 1PCC11AP001, SWBD.#1CA, PANEL 10, MF3 | CVP11, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 72 | 66 | 05.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | CWP-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
199 | HTUD BOP | E04V0.5 | 10.7.02 | CVP11-HT-D005A | 1PCC11AP001, SWBD.#1CA, PANEL 10, MF3 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 72 | 70 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
233 | HTUD BOP | E04V0.5 | 10.7.02 | CVP12-HT-D001 | 1LAC20AP001, SWBD.#1CB, PANEL 19, MFD1 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | 71 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | BFP-B | ZZ99- , MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
234 | HTUD BOP | E02W0.5 | 10.8.01 | CVP12-HT-D002 | 1LAC20AP001, SWBD.#1CB, PANEL 19, MFD1 | CVP12, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 61 | 58 | 02.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | BFP-B | ZZ99- , MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
233 | HTUD BOP | E04V0.5 | 10.7.02 | CVP12-HT-D001A | 1LAC20AP001, SWBD.#1CB, PANEL 19, MFD1 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | 70 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | BFP-B | ZZ99- , MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
235 | HTUD BOP | E04V0.5 | 10.7.02 | CVP12-HT-D003 | 1PCB32AP001, SWBD.#1CB, PANEL 15, MF5A | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 62 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | ACW-B | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
236 | HTUD BOP | E02W0.5 | 10.8.01 | CVP12-HT-D004 | 1PCB32AP001, SWBD.#1CB, PANEL 15, MF5A | CVP12, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 59 | 58 | 04.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | ACW-B | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
235 | HTUD BOP | E04V0.5 | 10.7.02 | CVP12-HT-D003A | 1PCB32AP001, SWBD.#1CB, PANEL 15, MF5A | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 59 | 62 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | ACW-B | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
237 | HTUD BOP | E04V0.5 | 10.7.02 | CVP12-HT-D005 | 1PCC12AP001, SWBD.#1CB, PANEL 28, MF3 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 76 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-B | ZZ99- , MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
238 | HTUD BOP | E02W0.5 | 10.8.01 | CVP12-HT-D006 | 1PCC12AP001, SWBD.#1CB, PANEL 28, MF3 | CVP12, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 70 | 72 | 04.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | CWP-B | ZZ99- , MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
237 | HTUD BOP | E04V0.5 | 10.7.02 | CVP12-HT-D005A | 1PCC12AP001, SWBD.#1CB, PANEL 28, MF3 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | 76 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-B | ZZ99- , MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC42-04, CC41-03 |  | BPL | EDN
263 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D001 | 1LAC30AP001AXB32, SWBD.#1CA, PANEL 21, MFD2 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 66 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | BFP-C | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
264 | HTUD BOP | E02W0.5 | 10.8.01 | CVP13-HT-D002 | 1LAC30AP001AXQ01, SWBD.#1CA, PANEL 21, MFD2 | CVP13, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 65 | 65 | 04.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | BFP-C | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
263 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D001A | 1LAC30AP001AXB32, SWBD.#1CA, PANEL 21, MFD2 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | 66 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | BFP-C | ZZ99- , MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
265 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D004 | 1PCC13AP001AXB32, SWBD.#1CA, PANEL 9, MF3A | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 76 | 75 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-C | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
266 | HTUD BOP | E02W0.5 | 10.8.01 | CVP13-HT-D003 | 1PCC13AP001AXQ01, SWBD.#1CA, PANEL 9, MF3A | CVP13, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 76 | 75 | 04.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | CWP-C | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
265 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D004A | 1PCC13AP001AXB32, SWBD.#1CA, PANEL 9, MF3A | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 76 | 75 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-C | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
267 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D006 | 1LAC30AP001BXB32, SWBD.#1CB, PANEL 17, MFD1 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 63 | 60 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | MDBFP-C | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
268 | HTUD BOP | E02W0.5 | 10.8.01 | CVP13-HT-D005 | 1LAC30AP001BXQ01, SWBD.#1CB, PANEL 17, MFD1 | CVP13, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 63 | 62 | 04.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | MDBFP-C | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
267 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D006A | 1LAC30AP001BXB32, SWBD.#1CB, PANEL 17, MFD1 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 63 | 60 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | MDBFP-C | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
269 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D008 | 1PCC13AP001BXB32, SWBD.#1CB, PANEL 30, MF3 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 74 | 75 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-1C | ZZ99- , MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
270 | HTUD BOP | E02W0.5 | 10.8.01 | CVP13-HT-D007 | 1PCC13AP001BXQ01, SWBD.#1CB, PANEL 30, MF3 | CVP13, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 74 | 68 | 04.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | CWP-1C | ZZ99- , MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
269 | HTUD BOP | E04V0.5 | 10.7.02 | CVP13-HT-D008A | 1PCC13AP001BXB32, SWBD.#1CB, PANEL 30, MF3 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 74 | 75 | 25.10.2019 | DR0817_4798-4G-17 |  |  | CONTROL AND MONITORING | CWP-1C | ZZ99- , MV20-03, MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
284 | HTUD BOP | E04V0.5 | 10.7.02 | CVP14-HT-C001 | 1PGC01AP001, SWBD.#1CA, PANEL 16, MF5 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 76 | 65 | 25.10.2019 | DR0817_4798-4G-16 |  |  | CONTROL AND MONITORING | DMCW-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
283 | HTUD BOP | E02W0.5 | 10.8.01 | CVP14-HT-C002 | 1PGC01AP001, SWBD.#1CA, PANEL 16, MF5 | CVP14, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 76 | 68 | 05.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | DMCW-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
284 | HTUD BOP | E04V0.5 | 10.7.02 | CVP14-HT-C001A | 1PGC01AP001, SWBD.#1CA, PANEL 16, MF5 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 76 | 65 | 25.10.2019 | DR0720_4798-4G-21 |  |  | CONTROL AND MONITORING | DMCW-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
284 | HTUD BOP | E04V0.5 | 10.7.02 | CVP15-HT-C001 | 1PGC02AP001, SWBD.#1CB, PANEL 16, MF5 | CVP15, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 76 | 63 | 25.10.2019 | DR0817_4798-4G-76 |  |  | CONTROL AND MONITORING | DMCW-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
292 | HTUD BOP | E02W0.5 | 10.8.01 | CVP15-HT-D002 | 1PGC02AP001, SWBD.#1CB, PANEL 16, MF5 | CVP15, EER, 15.5 Mtr | 02P X 0.5 Paired Screened(I) ( 225 V ) | 63 | 65 | 04.02.20 | DR0897_4794-2F-111 |  |  | CONTROL AND MONITORING | DMCW-A | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
284 | HTUD BOP | E04V0.5 | 10.7.02 | CVP15-HT-C001A | 1PGC02AP001, SWBD.#1CB, PANEL 16, MF5 | CVP15, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 76 | 63 | 25.10.2019 | DR0817_4798-4G-76 |  |  | CONTROL AND MONITORING | DMCW-A | ZZ99- , MV14-03, MV13-03, MV12-03, MV11-03, MV10-03, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC40-01 |  | BPL | EDN
22 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D001 | 1HLB01AP002, EMR MCC#1DG, COMPT NO.1-R-E | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 35 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01 |  | EPD | EDN
23 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D002 | 1HNC01AN002, BLR MCC#1HA, COMPT NO.1-R-B | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
24 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D003 | 1HNC01AN003, BLR MCC#1HA, COMPT NO.12-F-G | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
25 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D004 | 1HNC01AP002, EMR MCC#1DG, COMPT NO.1-R-D | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 35 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01 |  | EPD | EDN
26 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D005 | 1HLB01AP001, BLR MCC#1HA, COMPT NO.2-R-D | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
27 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D006 | 1HNC01AP001, BLR MCC#1HA, COMPT NO. 1-R-F | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
28 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D007 | 1HTA10AN001, BLR MCC#1HA, COMPT NO.2-F-B | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
29 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D008 | 1HTA20AN002, BLR MCC#1HA, COMPT NO.11-R-G | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
30 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D009 | 1HTA30AN002, BLR MCC#1HA, COMPT NO. 12-R-F | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
31 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D010 | 1HTA10AN002, BLR MCC#1HA, COMPT NO. 11-R-E | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
32 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D011 | 1HTA20AN001, BLR MCC#1HA, COMPT NO. 3-R-I | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
33 | LTUD BOP | E04V0.5 | 10.7.02 | CVP01-LT-D012 | 1HTA30AN001, BLR MCC#1HA, COMPT NO.1-F-B | CVP-01 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
41 | LTUD BOP | E04V0.5 | 10.7.02 | CVP02-LT-D001 | 1HLB02AP002, EMR MCC#1DG, COMPT NO.14-F-H | CVP-02 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 47 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01 |  | EPD | EDN
42 | LTUD BOP | E04V0.5 | 10.7.02 | CVP02-LT-D002 | 1HNC02AN002, BLR MCC#1HA, COMPT NO.1-R-C | CVP-02 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
43 | LTUD BOP | E04V0.5 | 10.7.02 | CVP02-LT-D003 | 1HNC02AN003, BLR MCC#1HA, COMPT NO. 11-F-E | CVP-02 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
44 | LTUD BOP | E04V0.5 | 10.7.02 | CVP02-LT-D004 | 1HNC02AP002, EMR MCC#1DG, COMPT NO.13-R-E | CVP-02 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 47 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01 |  | EPD | EDN
45 | LTUD BOP | E04V0.5 | 10.7.02 | CVP02-LT-D005 | 1HLB02AP001, BLR MCC#1HA, COMPT NO. 11-F-C | CVP-02 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
46 | LTUD BOP | E04V0.5 | 10.7.02 | CVP02-LT-D006 | 1HNC02AP001, BLR MCC#1HA, COMPT NO. 12-F-E | CVP-02 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 60 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01 |  | EPD | EDN
65 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D001 | 1HLD01AP002, EMR MCC#1DG, COMPT NO.4-R-E | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 41 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
66 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D002 | 1HLD01AP004, EMR MCC#1DG, COMPT NO.4-R-D | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 41 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
67 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D003 | 1HNA15AN002, BLR MCC#1HA, COMPT NO.12-R-E | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
68 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D004 | 1HLD01AP001, BLR MCC#1HA, COMPT NO. 4-F-B | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
69 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D005 | 1HLD01AP003, BLR MCC#1HA, COMPT NO. 1-R-D | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
70 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D006 | 1HNA15AN001, BLR MCC#1HA, COMPT NO.3-F-B | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
71 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D007 | 1HFE01AP002, EMR MCC#1DG, COMPT NO.3-R-D | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 41 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
72 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D008 | 1HFE30AN002, BLR MCC#1HA, COMPT NO. 12-F-H | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
73 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D009 | 1HLA30AN002, BLR MCC#1HA, COMPT NO. 12-R-C | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
74 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D010 | 1HFE01AP001, BLR MCC#1HA, COMPT NO. 3-R-F | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
75 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D011 | 1HFE30AN001, BLR MCC#1HA, COMPT NO. 1-R-H | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
76 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D012 | 1HLA30AN001, BLR MCC#1HA, COMPT NO. 1-F-D | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
77 | LTUD BOP | E04V0.5 | 10.7.02 | CVP03-LT-D013 | 1HLD01AE002, EMR MCC#1DG, COMPT NO.4-F-G | CVP-03 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 41 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
96 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D001 | 1HLD02AP002, EMR MCC#1DG, COMPT NO.15-R-D | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 53 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
97 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D002 | 1HLD02AP004, EMR MCC#1DG, COMPT NO.15-R-E | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 53 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
98 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D003 | 1HNA25AN002, BLR MCC#1HA, COMPT NO. 11-R-D | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
99 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D004 | 1HLD02AP001, BLR MCC#1HA, COMPT NO. 9-R-C | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 63 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
100 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D005 | 1HLD02AP003, BLR MCC#1HA, COMPT NO. 12-R-D | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
101 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D006 | 1HNA25AN001, BLR MCC#1HA, COMPT NO.3-F-C | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
102 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D007 | 1HFE02AP002, EMR MCC#1DG, COMPT NO.12-R-E | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
103 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D008 | 1HFE40AN002, BLR MCC#1HA, COMPT NO. 11-R-H | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
104 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D009 | 1HLA40AN002, BLR MCC#1HA, COMPT NO. 9-F-D | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 63 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
105 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D010 | 1HFE02AP001, BLR MCC#1HA, COMPT NO. 11-F-B | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 66 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV15-R4, LV14-R4, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
106 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D011 | 1HFE40AN001, BLR MCC#1HA, COMPT NO.2-R-F | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
107 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D012 | 1HLA40AN001, BLR MCC#1HA, COMPT NO. 1-F-E | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 61 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03 |  | EPD | EDN
108 | LTUD BOP | E04V0.5 | 10.7.02 | CVP04-LT-D013 | 1HLD02AE002, EMR MCC#1DG, COMPT NO.4-F-B | CVP-04 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 41 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC30-03 |  | EPD | EDN
205 | LTUD BOP | E04V0.5 | 10.7.02 | CVP11-LT-D001 | 1LAC10AP002, EMR MCC#1DG, COMPT NO.1-R-B | CVP-11 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 41 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03 |  | EPD | EDN
206 | LTUD BOP | E04V0.5 | 10.7.02 | CVP11-LT-D002 | 1PCA01AE001, Near SCS-A | CVP-11 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 112 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , TG80-02, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02 |  | EPD | EDN
245 | LTUD BOP | E04V0.5 | 10.7.02 | CVP12-LT-D001 | 1LAC20AP002, EMR MCC#1DG, COMPT NO.15-F-B | CVP-12 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 53 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV37-R4, LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03 |  | EPD | EDN
246 | LTUD BOP | E04V0.5 | 10.7.02 | CVP12-LT-D002 | 1PCA02AE001, Near SCS-B | CVP-12 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , TG83-02, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02 |  | EPD | EDN
275 | LTUD BOP | E04V0.5 | 10.7.02 | CVP13-LT-D001 | 1LAC30AP002, EMR MCC#1DG, COMPT NO.11-R-B | CVP-13 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 54 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC67-02, CC68-02, CC40-01 |  | EPD | EDN
276 | LTUD BOP | E04V0.5 | 10.7.02 | CVP13-LT-D002 | 1LCR23AP001, ETP PMCC#1DE COMP NO. 14-F-E | CVP-13 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 432 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , ET04-R4, ET03-R4, ET02-R4, ET01-R4, PR01-04, IL09-04, IL08-04, IL07-04, IL06-04, IL05-04, IL04-04, IL03-04, IL02-04, IL01-04, IR37-04, IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01 |  | EPD | EDN
285 | LTUD BOP | E04V0.5 | 10.7.02 | CVP14-LT-C001 | 1PGC31AP001, EMR MCC#1DG, COMPT NO.3-F-B | CVP-14 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV39-R4, LV81-R4, LV26-L3, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC67-02, CC68-02, CC40-01 |  | EPD | EDN
286 | LTUD BOP | E04V0.5 | 10.7.02 | CVP14-LT-D002 | 1LCR24AP001, ETP PMCC#1DE COMP NO. 5-F-C | CVP-14 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 439 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , ET06-R4, ET05-R4, ET04-R4, ET03-R4, ET02-R4, ET01-R4, PR01-04, IL09-04, IL08-04, IL07-04, IL06-04, IL05-04, IL04-04, IL03-04, IL02-04, IL01-04, IR37-04, IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01 |  | EPD | EDN
290 | LTUD BOP | E04V0.5 | 10.7.02 | CVP15-LT-D003 | 1LCR20AP001, ETP PMCC#1DE, COMPT NO. 1-F-F | CVP-15 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 442 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , ET07-R4, ET06-R4, ET05-R4, ET04-R4, ET03-R4, ET02-R4, ET01-R4, PR01-04, IL09-04, IL08-04, IL07-04, IL06-04, IL05-04, IL04-04, IL03-04, IL02-04, IL01-04, IR37-04, IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01 |  | EPD | EDN
291 | LTUD BOP | E02W0.5 | 10.8.01 | CVP15-LT-D004 | 1LCR20AP001, ETP PMCC#1DE, COMPT NO. 1-F-F | CVP-15 | 02P X 0.5 Paired Screened(I) ( 225 V ) | 442 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC40-01 |  | EPD | EDN
293 | LTUD BOP | E04V0.5 | 10.7.02 | CVP15-LT-D001 | 1LCR25AP001, ETP PMCC#1DE COMP NO. 17-F-I | CVP-15 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 432 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , ET04-R4, ET03-R4, ET02-R4, ET01-R4, PR01-04, IL09-04, IL08-04, IL07-04, IL06-04, IL05-04, IL04-04, IL03-04, IL02-04, IL01-04, IR37-04, IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01 |  | EPD | EDN
294 | LTUD BOP | E04V0.5 | 10.7.02 | CVP15-LT-D002 | 1PGC32AP001, EMR MCC#1DG, COMPT NO.12-F-B | CVP-15 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 54 | [5 empty] | CONTROL AND MONITORING | LTUD | ZZ99- , LV38-R4, LV41-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC67-02, CC68-02, CC40-01 |  | EPD | EDN
1 | LTUD TG | E04V0.5 | 10.7.02 | CCA6006 | CCA-55 | #1DA COMPT NO: 2-F-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 73 | 0 | 28.09.2019 | DR0817_4798-4G-34 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC64-02, CC63-02, CC62-04, CC03-04, IR18-03, IM04-03, IM03-03, IM02-L6, MR06-06, MV62-06, MV60-R2, MV61-R2, ZZ99- |  | EDN | EPD
2 | LTUD TG | E02W0.5 | 10.8.01 | CCA6007 | CCA-55 | #1DA COMPT NO: 2-F-B | 02P X 0.5 Paired Screened(I) ( 225 V ) | 73 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC64-02, CC63-02, CC62-04, CC03-04, IR18-03, IM04-03, IM03-03, IM02-L6, MR06-06, MV62-06, MV60-R2, MV61-R2, ZZ99- |  | EDN | EPD
3 | LTUD TG | E04V0.5 | 10.7.02 | CCA6008 | CCA-55 | #1KA COMPT NO: 1-F-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 54 | 28.09.2019 | DR0720_4798-4G-19 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
4 | LTUD TG | E04V0.5 | 10.7.02 | CCA6009 | CCA-55 | #1DA COMPT NO: 11-F-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 73 | 0 | 28.09.2019 | DR0720_4798-4G-19 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC64-02, CC63-02, CC62-04, CC03-04, IR18-03, IM04-03, IM03-03, IM02-L6, MR06-06, MV62-06, MV60-R2, MV61-R2, ZZ99- |  | EDN | EPD
5 | LTUD TG | E02W0.5 | 10.8.01 | CCA6010 | CCA-55 | #1DA COMPT NO: 11-F-B | 02P X 0.5 Paired Screened(I) ( 225 V ) | 73 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC64-02, CC63-02, CC62-04, CC03-04, IR18-03, IM04-03, IM03-03, IM02-L6, MR06-06, MV62-06, MV60-R2, MV61-R2, ZZ99- |  | EDN | EPD
6 | LTUD TG | E04V0.5 | 10.7.02 | CCA6011 | CCA-55 | #1KA COMPT NO: 9-F-D | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 49 | 28.09.2019 | DR0817_4798-4G-16 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
7 | LTUD TG | E04V0.5 | 10.7.02 | CCA6028 | CCA-53 | #1KA COMPT NO: 1-F-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | 54 | 28.09.2019 | DR0720_4798-4G-19 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
8 | LTUD TG | E02W0.5 | 10.8.01 | CCA6029 | CCA-53 | #1KA COMPT NO: 1-F-C | 02P X 0.5 Paired Screened(I) ( 225 V ) | 82 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
9 | LTUD TG | E04V0.5 | 10.7.02 | CCA6030 | CCA-53 | #1DG COMPT NO: 2-F-E | 04P X 0.5 Paired Screened(O) ( 225 V ) | 46 | 41 | 28.09.2019 | DR0720_4798-4G-19 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
10 | LTUD TG | E02W0.5 | 10.8.01 | CCA6031 | CCA-53 | #1DG COMPT NO: 2-F-E | 02P X 0.5 Paired Screened(I) ( 225 V ) | 46 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
11 | LTUD TG | E04V0.5 | 10.7.02 | CCA6037 | CCA-53 | #1DG COMPT NO: 12-F-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 46 | 54 | 30.09.2019 | DR0720_4798-4G-19 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
12 | LTUD TG | E02W0.5 | 10.8.01 | CCA6038 | CCA-53 | #1DG COMPT NO: 12-F-C | 02P X 0.5 Paired Screened(I) ( 225 V ) | 46 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
13 | LTUD TG | E04V0.5 | 10.7.02 | CCA6045 | CCA-53 | #1KA COMPT NO: 2-F-E | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | 52 | 30.09.2019 | DR0720_4798-4G-19 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
14 | LTUD TG | E04V0.5 | 10.7.02 | CCA6046 | CCA-53 | #1DG COMPT NO: 1-R-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 46 | 39 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
15 | LTUD TG | E04V0.5 | 10.7.02 | CCA6047 | CCA-53 | #1KA COMPT NO: 7-R-D | 04P X 0.5 Paired Screened(O) ( 225 V ) | 82 | 52 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC76-03, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
16 | LTUD TG | E04V0.5 | 10.7.02 | CCA6055 | CCA-55 | #1KA COMPT NO: 1-R-F | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 56 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
17 | LTUD TG | E04V0.5 | 10.7.02 | CCA6056 | CCA-55 | #1KA COMPT NO: 8-R-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | 48 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
18 | LTUD TG | E04V0.5 | 10.7.02 | CJJ6057 | CJJ-53 | #1KA COMPT NO: 9-F-G | 04P X 0.5 Paired Screened(O) ( 225 V ) | 87 | 49 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
19 | LTUD TG | E04V0.5 | 10.7.02 | CJJ6058 | CJJ-53 | #1KA COMPT NO: 1-R-D | 04P X 0.5 Paired Screened(O) ( 225 V ) | 87 | 52 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
20 | LTUD TG | E04V0.5 | 10.7.02 | CJJ6059 | CJJ-53 | #1KA COMPT NO: 2-R-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 87 | 53 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
21 | LTUD TG | E04V0.5 | 10.7.02 | CJJ6060 | CJJ-53 | #1KA COMPT NO: 7-F-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 87 | 50 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
22 | LTUD TG | E04V0.5 | 10.7.02 | CJJ6061 | CJJ-53 | #1KA COMPT NO: 8-R-D | 04P X 0.5 Paired Screened(O) ( 225 V ) | 87 | 58 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
23 | LTUD TG | E04V0.5 | 10.7.02 | CJJ6062 | CJJ-53 | #1KA COMPT NO: 2-F-G | 04P X 0.5 Paired Screened(O) ( 225 V ) | 87 | 52 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
24 | LTUD TG | E04V0.5 | 10.7.02 | CJJ6063 | CJJ-53 | #1KA COMPT NO: 1-R-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 87 | 60 | 30.09.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
25 | LTUD TG | E04V0.5 | 10.7.02 | CCA6064 | CCA-51 | #1DG COMPT NO: 4-R-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 58 | 56 | 01.10.2019 | DR0720_4798-4G-32 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC25-03, CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
26 | LTUD TG | E04V0.5 | 10.7.02 | CCA6065 | CCA-51 | #1DG COMPT NO: 13-F-D | 04P X 0.5 Paired Screened(O) ( 225 V ) | 58 | 49 | 01.10.2019 | DR0817_4798-4G-38 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC25-03, CC24-03, CC80-03, CC79-04, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
27 | LTUD TG | E04V0.5 | 10.7.02 | CCA6066 | CCA-56 | #1KA COMPT NO: 8-R-E | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 54 | 01.10.2019 | DR0817_4798-4G-38 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
28 | LTUD TG | E04V0.5 | 10.7.02 | CCA6067 | CCA-56 | MCC COMPT NO: AIR DRIER | 04P X 0.5 Paired Screened(O) ( 225 V ) | 120 | 0 | 01.10.2019 | DR0817_4798-4G-38 |  |  | FRLS PVC | DRIVE CONTROLS | SITE ROUTING |  | EDN | EPD
29 | LTUD TG | E04V0.5 | 10.7.02 | CCA6068 | CCA-56 | #1KA COMPT NO: 2-F-F | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 58 | 01.10.2019 | DR0817_4798-4G-38 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
30 | LTUD TG | E04V0.5 | 10.7.02 | CCA6069 | CCA-56 | #1KA COMPT NO: 9-F-E | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 50 | 01.10.2019 | DR0817_4798-4G-38 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
31 | LTUD TG | E04V0.5 | 10.7.02 | CCA6070 | CCA-56 | #1KA COMPT NO: 7-R-G | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 55 | 01.10.2019 | DR0817_4798-4G-38 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
32 | LTUD TG | E04V0.5 | 10.7.02 | CCA6071 | CCA-56 | #1KA COMPT NO: 2-F-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 61 | 01.10.2019 | DR0817_4798-4G-38 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
33 | LTUD TG | E04V0.5 | 10.7.02 | CCA6072 | CCA-56 | #1KA COMPT NO: 9-F-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 52 | 01.10.2019 | DR0720_4798-4G-32 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
34 | LTUD TG | E04V0.5 | 10.7.02 | CCA6073 | CCA-56 | #1KA COMPT NO: 1-R-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 60 | 01.10.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
35 | LTUD TG | E04V0.5 | 10.7.02 | CCA6074 | CCA-56 | #1KA COMPT NO: 7-R-B | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 56 | 01.10.2019 | DR0720_4798-4G-32 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
36 | LTUD TG | E02W0.5 | 10.8.01 | CCA6075 | CCA-56 | #1KA COMPT NO: 7-R-B | 02P X 0.5 Paired Screened(I) ( 225 V ) | 91 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
37 | LTUD TG | E04V0.5 | 10.7.02 | CCA6076 | CCA-56 | #1KA COMPT NO: 9-F-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | 52 | 01.10.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV24-R4, LV43-04, LV09-R4, LV08-R4, LV07-R2, LV06-R2, ZZ99- |  | EDN | EPD
38 | LTUD TG | E04V0.5 | 10.7.02 | CCA6077 | CCA-56 | #1DG COMPT NO: 3-R-C | 04P X 0.5 Paired Screened(O) ( 225 V ) | 56 | 47 | 01.10.2019 | DR0720_4798-4G-83 |  |  | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
39 | LTUD TG | E02W0.5 | 10.8.01 | CCA6078 | CCA-56 | #1DG COMPT NO: 3-R-C | 02P X 0.5 Paired Screened(I) ( 225 V ) | 56 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC77-04, CC75-04, CC73-04, CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, ZZ99- |  | EDN | EPD
77 | LTUD TG | E04V0.5 | 10.7.02 | CCA6032 | CCA-53 | DC EOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
78 | LTUD TG | E04V0.5 | 10.7.02 | CCA6033 | CCA-53 | DC EOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
79 | LTUD TG | E04V0.5 | 10.7.02 | CCA6034 | CCA-53 | DC EOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
80 | LTUD TG | E02W0.5 | 10.8.01 | CCA6035 | CCA-53 | DC EOP:DCSC | 02P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-04, LR07-02, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
81 | LTUD TG | E04V0.5 | 10.7.02 | CCA6036 | CCA-53 | AC EOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | EPD
82 | LTUD TG | E04V0.5 | 10.7.02 | CCA6039 | CCA-53 | DC JOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
83 | LTUD TG | E04V0.5 | 10.7.02 | CCA6040 | CCA-53 | DC JOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
84 | LTUD TG | E04V0.5 | 10.7.02 | CCA6041 | CCA-53 | DC JOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
85 | LTUD TG | E02W0.5 | 10.8.01 | CCA6042 | CCA-53 | DC JOP:DCSC | 02P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC22-04, CC78-03, CC79-04, CC90-04, LR07-02, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
86 | LTUD TG | E04V0.5 | 10.7.02 | CCA6079 | CCA-56 | DC SOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 137 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC79-04, CC90-02, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
87 | LTUD TG | E04V0.5 | 10.7.02 | CCA6080 | CCA-56 | DC SOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 135 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC79-04, CC90-04, LR07-04, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
88 | LTUD TG | E04V0.5 | 10.7.02 | CCA6081 | CCA-56 | DC SOP:DCSC | 04P X 0.5 Paired Screened(O) ( 225 V ) | 137 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC79-04, CC90-04, LR07-02, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
89 | LTUD TG | E02W0.5 | 10.8.01 | CCA6082 | CCA-56 | DC SOP:DCSC | 02P X 0.5 Paired Screened(I) ( 225 V ) | 137 | [5 empty] | FRLS PVC | DRIVE CONTROLS | ZZ99- , CC20-03, CC21-03, CC78-03, CC79-04, CC90-04, LR07-02, LV74-04, LV25-R3, LV24-R4, LV23-R4, LV48-05, LV11-R4, LV12-R4, LV58-03, LV04-R4, LV64-07, TR48-06, TG71-03, TG72-03, TR16-03, TG73-03, TG74-03, TG75-03, TG76-03, ZZ99- |  | EDN | HWR
1 | LTUD DC | D07C2.5 | 10.5.09 | DCSB-LPBS-CC-01 (9ZT01AC01) | LPBS EL 20300 : NEAR S2R | DC STARTER BOX LTMCC ROOM | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | INTERCONNECTION DETAILS FOR LPBS AND DC STARTER BOX | TRICHY SCOPE CABLE | ZZ99- , BD10-02, BR03-03, BR02-01, IC47-02, IC46-02, IR06-02, IC02-R5, IC01-R5, CR01-R3, QR03-L3, BQ20-L3, BQ19-L3, BQ07-R2, BQ26-L2, ZZ99- |  | EDN | HWR
2 | LTUD DC | D02L2.5 | 10.4.24 | DCSB-CBL-P-01 (9ZT01AC02) | DC PDB CONTROL EQUIPMENT ROOM (CER) | DC STARTER BOX LTMCC ROOM | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 51 | [5 empty] | INTERCONNECTION DETAILS FOR LPBS AND DC STARTER BOX | PEM SCOPE CABLE | ZZ99- , CC71-05, QR03-L3, BQ20-L3, BQ19-L3, BQ07-R2, BQ26-L2, ZZ99- |  | EDN | HWR
3 | LTUD DC | D03L2.5 | 10.4.26 | DCSB-CBL-P-02 (9ZT01AC03) | DC STARTER BOX LTMCC ROOM | DC MOTOR EL 20300 : NEAR S2R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DETAILS FOR LPBS AND DC STARTER BOX | TRICHY SCOPE CABLE | ZZ99- , BQ26-L2, BQ07-R2, BQ19-L3, BQ20-L3, QR03-L3, CR01-L2, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-01, BR03-03, BD10-02, ZZ99- |  | EDN | HWR
4 | LTUD DC | E04W0.5 | 10.8.02 | DCSB-CBL-SC-01 (9ZT01AC04) | DC STARTER BOX LTMCC ROOM | DCS/ CONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | INTERCONNECTION DETAILS FOR LPBS AND DC STARTER BOX | TRICHY SCOPE CABLE | ZZ99- , BQ26-R3, BQ07-L3, BQ19-R3, BQ20-R3, QR03-R3, CC71-07, ZZ99- |  | EDN | HWR
5 | LTUD DC | E04W0.5 | 10.8.02 | DCSB-CBL-SC-02 (9ZT01AC05) | DCS / CONTROL EQUIPMENT ROOM (CER) | DC STARTER BOX LTMCC ROOM | 04P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | INTERCONNECTION DETAILS FOR LPBS AND DC STARTER BOX | TRICHY SCOPE CABLE | ZZ99- , CC71-07, QR03-R3, BQ20-R3, BQ19-R3, BQ07-L3, BQ26-R3, ZZ99- |  | EDN | HWR
1 | 1DB1A | D03Q095 | 10.4.15 | 1DB1 05FA P01 (1DB1 05FA P01) | 415V SWGR O/G MODULE #1DB1 05FA | FEEDER TO LDB - ESP SWGR ROOM (1UE) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 10 | [5 empty] | MLDB SUPPLY |  |  |  | RPT | PEM
1 | 1DB1A | D01Q630 | 10.4.05 | 1DB1 02RB P01 | 415V SWGR O/G MODULE #1DB1 02RB | ESP AC-VENT MCC # 1TB SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 28.11.2019 | DR1050_0011 | [6 empty] | RPT | PEM
2 | 1DB1A | D01Q630 | 10.4.05 | 1DB1 02RB P02 | 415V SWGR O/G MODULE #1DB1 02RB | ESP AC-VENT MCC # 1TB SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 28.11.2019 | DR1050_0011 | [6 empty] | RPT | PEM
3 | 1DB1A | D01Q630 | 10.4.05 | 1DB1 02RB P03 | 415V SWGR O/G MODULE #1DB1 02RB | ESP AC-VENT MCC # 1TB SEC-A | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 28.11.2019 | DR1050_0011 | [6 empty] | RPT | PEM
4 | 1DB1A | D01Q400 | 10.4.04 | 1DB1 02RB P04 (1DB1 02RB P04) | 415V SWGR O/G MODULE #1DB1 02RB | ESP AC-VENT MCC # 1TB SEC-A | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 30 | [9 empty] | RPT | PEM
1 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-04FA-P01 | ESP SWGR-A PANEL-04FA | EC -01 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 50 | 19.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
2 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-04FA-P02 | ESP SWGR-A PANEL-04FA | EC -01 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 50 | 19.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
3 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-07FA-P01 | ESP SWGR-A PANEL-07FA | EC -02 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 49 | 19.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
4 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-07FA-P02 | ESP SWGR-A PANEL-07FA | EC -02 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 49 | 19.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
5 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-08RA-P01 | ESP SWGR-A PANEL-08RA | EC -03 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 45 | 19.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
6 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-08RA-P02 | ESP SWGR-A PANEL-08RA | EC -03 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 45 | 19.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
7 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-06RA-P01 | ESP SWGR-A PANEL-06RA | EC -04 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 37 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
8 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-06RA-P02 | ESP SWGR-A PANEL-06RA | EC -04 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 37 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
9 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-05RA-P01 | ESP SWGR-A PANEL-05RA | EC -05 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 36 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
10 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-05RA-P02 | ESP SWGR-A PANEL-05RA | EC -05 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 36 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
11 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-04RA-P01 | ESP SWGR-A PANEL-04RA | EC -06 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 37 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
12 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-04RA-P02 | ESP SWGR-A PANEL-04RA | EC -06 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 37 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
13 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-03RB-P01 | ESP SWGR-A PANEL-03RB | EC -07 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 36 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
14 | 1DB1A | D02G120 | 10.4.10 | LTMCC1-03RB-P02 | ESP SWGR-A PANEL-03RB | EC -07 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 36 | 20.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
1 | 1DB1A | D02G120 | 10.4.10 | ECTP-A01-P01 | EC -01 PASS-A | HV TXR RECT TRF-01 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 100 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
2 | 1DB1A | D02G120 | 10.4.10 | ECTP-A01-P02 | EC -01 PASS-A | HV TXR RECT TRF-01 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 100 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
3 | 1DB1A | D10C1.5 | 10.5.10 | ECTP-A01-C01 | EC -01 PASS-A | HV TXR RECT TRF-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
4 | 1DB1A | D03C1.5 | 10.5.03 | ECTP-A01-C02 | EC -01 PASS-A | HV TXR RECT TRF-01 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
5 | 1DB1A | D02W1.5 | 10.4.27 | ECTP-A01-C03 | EC -01 PASS-A | HV TXR RECT TRF-01 PASS-A | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
6 | 1DB1A | D02G120 | 10.4.10 | ECTP-A02-P01 | EC -02 PASS-A | HV TXR RECT TRF-02 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
7 | 1DB1A | D02G120 | 10.4.10 | ECTP-A02-P02 | EC -02 PASS-A | HV TXR RECT TRF-02 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
8 | 1DB1A | D10C1.5 | 10.5.10 | ECTP-A02-C01 | EC -02 PASS-A | HV TXR RECT TRF-02 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
9 | 1DB1A | D03C1.5 | 10.5.03 | ECTP-A02-C02 | EC -02 PASS-A | HV TXR RECT TRF-02 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
10 | 1DB1A | D02W1.5 | 10.4.27 | ECTP-A02-C03 | EC -02 PASS-A | HV TXR RECT TRF-02 PASS-A | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
11 | 1DB1A | D02G120 | 10.4.10 | ECTP-A03-P01 | EC -03 PASS-A | HV TXR RECT TRF-03 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
12 | 1DB1A | D02G120 | 10.4.10 | ECTP-A03-P02 | EC -03 PASS-A | HV TXR RECT TRF-03 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
13 | 1DB1A | D10C1.5 | 10.5.10 | ECTP-A03-C01 | EC -03 PASS-A | HV TXR RECT TRF-03 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
14 | 1DB1A | D03C1.5 | 10.5.03 | ECTP-A03-C02 | EC -03 PASS-A | HV TXR RECT TRF-03 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
15 | 1DB1A | D02W1.5 | 10.4.27 | ECTP-A03-C03 | EC -03 PASS-A | HV TXR RECT TRF-03 PASS-A | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
16 | 1DB1A | D02G120 | 10.4.10 | ECTP-A04-P01 | EC -04 PASS-A | HV TXR RECT TRF-04 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
17 | 1DB1A | D02G120 | 10.4.10 | ECTP-A04-P02 | EC -04 PASS-A | HV TXR RECT TRF-04 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
18 | 1DB1A | D10C1.5 | 10.5.10 | ECTP-A04-C01 | EC -04 PASS-A | HV TXR RECT TRF-04 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
19 | 1DB1A | D03C1.5 | 10.5.03 | ECTP-A04-C02 | EC -04 PASS-A | HV TXR RECT TRF-04 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
20 | 1DB1A | D02W1.5 | 10.4.27 | ECTP-A04-C03 | EC -04 PASS-A | HV TXR RECT TRF-04 PASS-A | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
21 | 1DB1A | D02G120 | 10.4.10 | ECTP-A05-P01 | EC -05 PASS-A | HV TXR RECT TRF-05 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
22 | 1DB1A | D02G120 | 10.4.10 | ECTP-A05-P02 | EC -05 PASS-A | HV TXR RECT TRF-05 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
23 | 1DB1A | D10C1.5 | 10.5.10 | ECTP-A05-C01 | EC -05 PASS-A | HV TXR RECT TRF-05 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
24 | 1DB1A | D03C1.5 | 10.5.03 | ECTP-A05-C02 | EC -05 PASS-A | HV TXR RECT TRF-05 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
25 | 1DB1A | D02W1.5 | 10.4.27 | ECTP-A05-C03 | EC -05 PASS-A | HV TXR RECT TRF-05 PASS-A | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
26 | 1DB1A | D02G120 | 10.4.10 | ECTP-A06-P01 | EC -06 PASS-A | HV TXR RECT TRF-06 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
27 | 1DB1A | D02G120 | 10.4.10 | ECTP-A06-P02 | EC -06 PASS-A | HV TXR RECT TRF-06 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
28 | 1DB1A | D10C1.5 | 10.5.10 | ECTP-A06-C01 | EC -06 PASS-A | HV TXR RECT TRF-06 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
29 | 1DB1A | D03C1.5 | 10.5.03 | ECTP-A06-C02 | EC -06 PASS-A | HV TXR RECT TRF-06 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
30 | 1DB1A | D02W1.5 | 10.4.27 | ECTP-A06-C03 | EC -06 PASS-A | HV TXR RECT TRF-06 PASS-A | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
31 | 1DB1A | D02G120 | 10.4.10 | ECTP-A07-P01 | EC -07 PASS-A | HV TXR RECT TRF-07 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
32 | 1DB1A | D02G120 | 10.4.10 | ECTP-A07-P02 | EC -07 PASS-A | HV TXR RECT TRF-07 PASS-A | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
33 | 1DB1A | D10C1.5 | 10.5.10 | ECTP-A07-C01 | EC -07 PASS-A | HV TXR RECT TRF-07 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
34 | 1DB1A | D03C1.5 | 10.5.03 | ECTP-A07-C02 | EC -07 PASS-A | HV TXR RECT TRF-07 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
35 | 1DB1A | D02W1.5 | 10.4.27 | ECTP-A07-C03 | EC -07 PASS-A | HV TXR RECT TRF-07 PASS-A | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
1 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-03RC-P01 | ESP SWGR-A PANEL-03RC | CERM-01 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
2 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-03RD-P01 | ESP SWGR-A PANEL-03RD | CERM-02 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
3 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-03RE-P01 | ESP SWGR-A PANEL-03RE | CERM-03 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
4 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-04RB-P01 | ESP SWGR-A PANEL-04RB | CERM-04 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
5 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-04RC-P01 | ESP SWGR-A PANEL-04RC | CERM-05 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
6 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-04RD-P01 | ESP SWGR-A PANEL-04RD | CERM-06 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
7 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-05RB-P01 | ESP SWGR-A PANEL-05RB | CERM-07 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
8 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-05RC-P01 | ESP SWGR-A PANEL-05RC | EERM-01 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
9 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-05RD-P01 | ESP SWGR-A PANEL-05RD | EERM-02 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
10 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-06RB-P01 | ESP SWGR-A PANEL-06RB | EERM-03 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
11 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-07RB-P01 | ESP SWGR-A PANEL-07RB | EERM-04 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
12 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-07RC-P01 | ESP SWGR-A PANEL-07RC | EERM-05 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
13 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-07RD-P01 | ESP SWGR-A PANEL-07RD | EERM-06 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
14 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-08RB-P01 | ESP SWGR-A PANEL-08RB | EERM-07 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
15 | 1DB1A | D03C2.5 | 10.5.04 | 1DB1-08RC-P01 | ESP SWGR-A PANEL-08RC | GDRM-01 PASS-A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | GDRM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
16 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05RA-C01 | ESP SWGR-A PANEL-05RA | CERM LPBJB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
17 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05RA-C02 | ESP SWGR-A PANEL-05RA | CERM LPBJB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
18 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05RA-C03 | ESP SWGR-A PANEL-05RA | CERM LPBJB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
19 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05RA-C04 | ESP SWGR-A PANEL-05RA | EERM LPBJB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
20 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05RA-C05 | ESP SWGR-A PANEL-05RA | EERM LPBJB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
21 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05RA-C06 | ESP SWGR-A PANEL-05RA | EERM LPBJB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-CERM-L01 | CERM LPBJB-01 PASS-A | CERM LPB-01 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-CERM-L02 | CERM LPBJB-01 PASS-A | CERM LPB-02 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-CERM-L03 | CERM LPBJB-01 PASS-A | CERM LPB-03 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-CERM-L04 | CERM LPBJB-01 PASS-A | CERM LPB-04 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-CERM-L05 | CERM LPBJB-01 PASS-A | CERM LPB-05 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-CERM-L06 | CERM LPBJB-01 PASS-A | CERM LPB-06 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-CERM-L07 | CERM LPBJB-01 PASS-A | CERM LPB-07 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-GDRM-L01 | CERM LPBJB-01 PASS-A | GDRM LPB-01 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | GDRM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-EERM-L01 | EERM LPBJB-01 PASS-A | EERM LPB-01 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-EERM-L02 | EERM LPBJB-01 PASS-A | EERM LPB-02 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-EERM-L03 | EERM LPBJB-01 PASS-A | EERM LPB-03 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-EERM-L04 | EERM LPBJB-01 PASS-A | EERM LPB-04 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-EERM-L05 | EERM LPBJB-01 PASS-A | EERM LPB-05 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-EERM-L06 | EERM LPBJB-01 PASS-A | EERM LPB-06 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-EERM-L07 | EERM LPBJB-01 PASS-A | EERM LPB-07 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
1 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-04FB-P01 | ESP SWGR-A PANEL-04FB | HH PJB-01 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | 96 | 13.03.2020 | 20 |  |  | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB01 A-L01 | HH PJB-01 PASS-A | HOPR2 FLD-1 PASS-A CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB01 A-L02 | HH PJB-01 PASS-A | HOPR2 FLD-1 PASS-A CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB01 A-L03 | HH PJB-01 PASS-A | HOPR2 FLD-1 PASS-A CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
2 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-04FC-P01 | ESP SWGR-A PANEL-04FC | HH PJB-02 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | 103 | 13.03.2020 | 20 |  |  | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB02 A-L01 | HH PJB-02 PASS-A | HOPR2 FLD-2 PASS-A CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB02 A-L02 | HH PJB-02 PASS-A | HOPR2 FLD-2 PASS-A CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB02 A-L03 | HH PJB-02 PASS-A | HOPR2 FLD-2 PASS-A CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
3 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-04FD-P01 | ESP SWGR-A PANEL-04FD | HH PJB-03 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | 108 | 13.03.2020 | 1543 |  |  | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB03 A-L01 | HH PJB-03 PASS-A | HOPR2 FLD-3 PASS-A CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB03 A-L02 | HH PJB-03 PASS-A | HOPR2 FLD-3 PASS-A CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB03 A-L03 | HH PJB-03 PASS-A | HOPR2 FLD-3 PASS-A CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
4 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-04FE-P01 | ESP SWGR-A PANEL-04FE | HH PJB-04 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | 114 | 14.03.2020 | 1543 |  |  | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB04 A-L01 | HH PJB-04 PASS-A | HOPR2 FLD-4 PASS-A CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB04 A-L02 | HH PJB-04 PASS-A | HOPR2 FLD-4 PASS-A CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB04 A-L03 | HH PJB-04 PASS-A | HOPR2 FLD-4 PASS-A CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
5 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-05FB-P01 | ESP SWGR-A PANEL-05FB | HH PJB-05 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | 120 | 14.03.2020 | 1543 |  |  | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB05 A-L01 | HH PJB-05 PASS-A | HOPR2 FLD-5 PASS-A CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB05 A-L02 | HH PJB-05 PASS-A | HOPR2 FLD-5 PASS-A CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB05 A-L03 | HH PJB-05 PASS-A | HOPR2 FLD-5 PASS-A CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
6 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-07FB-P01 | ESP SWGR-A PANEL-07FB | HH PJB-06 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | 127 | 14.03.2020 | 1543 |  |  | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB06 A-L01 | HH PJB-06 PASS-A | HOPR2 FLD-6 PASS-A CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB06 A-L02 | HH PJB-06 PASS-A | HOPR2 FLD-6 PASS-A CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB06 A-L03 | HH PJB-06 PASS-A | HOPR2 FLD-6 PASS-A CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
7 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-07FC-P01 | ESP SWGR-A PANEL-07FC | HH PJB-07 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | 134 | 14.03.2020 | 1543 |  |  | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB07 A-L01 | HH PJB-07 PASS-A | HOPR2 FLD-7 PASS-A CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB07 A-L02 | HH PJB-07 PASS-A | HOPR2 FLD-7 PASS-A CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | HHPJB07 A-L03 | HH PJB-07 PASS-A | HOPR2 FLD-7 PASS-A CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
8 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05FA-C01 | ESP SWGR-A PANEL-05FA | HH TH JB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | 104 | 19.2.20 | DR0400_1570 |  |  | HH CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
9 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05FA-C02 | ESP SWGR-A PANEL-05FA | HH TH JB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | 104 | 19.2.20 | DR0400_1570 |  |  | HH CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-HH-L01 | HH TH JB-01 PASS-A | THERMOSTAT-HH-1 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-HH-L02 | HH TH JB-01 PASS-A | THERMOSTAT-HH-2 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-HH-L03 | HH TH JB-01 PASS-A | THERMOSTAT-HH-3 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-HH-L04 | HH TH JB-01 PASS-A | THERMOSTAT-HH-4 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-HH-L05 | HH TH JB-01 PASS-A | THERMOSTAT-HH-5 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-HH-L06 | HH TH JB-01 PASS-A | THERMOSTAT-HH-6 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | PASS-A-HH-L07 | HH TH JB-01 PASS-A | THERMOSTAT-HH-7 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
10 | 1DB1A | D03Q035 | 10.4.13 | 1DB1-03FC-P01 | ESP SWGR-A PANEL-03FC | SUPP HTR JB01 VAR-P2 PASS-A | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | SUPP HTR POWER | RPT LT CABLE 1DRUM |  |  | RPT | RPT
| 1DB1A | D03Q035 | 10.4.13 | SUPPHTR L01 | SUPP HTR JB01 VAR-P2 PASS-A | SUPP HTR JB02 VAR-P3 PASS-A | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | SUPP HTR POWER |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB01 L01 | SUPP HTR JB01 VAR-P2 PASS-A | SUHTR ROW1 PASS-A JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB01 L02 | SUPP HTR JB01 VAR-P2 PASS-A | SUHTR ROW1 PASS-A JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB01 L03 | SUPP HTR JB01 VAR-P2 PASS-A | SUHTR ROW1 PASS-A JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB01 L04 | SUPP HTR JB01 VAR-P2 PASS-A | SUHTR ROW1 PASS-A JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB01 L05 | SUPP HTR JB01 VAR-P2 PASS-A | SUHTR ROW1 PASS-A JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB01 L06 | SUPP HTR JB01 VAR-P2 PASS-A | SUHTR ROW1 PASS-A JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB01 L07 | SUPP HTR JB01 VAR-P2 PASS-A | SUHTR ROW1 PASS-A JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB02 L01 | SUPP HTR JB02 VAR-P3 PASS-A | SUHTR ROW2 PASS-A JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB02 L02 | SUPP HTR JB02 VAR-P3 PASS-A | SUHTR ROW2 PASS-A JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB02 L03 | SUPP HTR JB02 VAR-P3 PASS-A | SUHTR ROW2 PASS-A JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB02 L04 | SUPP HTR JB02 VAR-P3 PASS-A | SUHTR ROW2 PASS-A JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB02 L05 | SUPP HTR JB02 VAR-P3 PASS-A | SUHTR ROW2 PASS-A JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB02 L06 | SUPP HTR JB02 VAR-P3 PASS-A | SUHTR ROW2 PASS-A JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SUHTR-A JB02 L07 | SUPP HTR JB02 VAR-P3 PASS-A | SUHTR ROW2 PASS-A JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
11 | 1DB1A | D03C1.5 | 10.5.03 | 1DB1-05FA-C03 | ESP SWGR-A PANEL-05FA | SUPP HTR TH-P1 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | SUPP HTR CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
12 | 1DB1A | D03Q010 | 10.4.11 | 1DB1-03FB-P01 | ESP SWGR-A PANEL-03FB | SHFT HTR VAR-P1 PASS-A | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | SHFT HTR POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SHTR-A L01 | SHFT HTR VAR-P1 PASS-A | SHFT HTR PASS-A JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SHTR-A L02 | SHFT HTR VAR-P1 PASS-A | SHFT HTR PASS-A JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SHTR-A L03 | SHFT HTR VAR-P1 PASS-A | SHFT HTR PASS-A JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SHTR-A L04 | SHFT HTR VAR-P1 PASS-A | SHFT HTR PASS-A JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SHTR-A L05 | SHFT HTR VAR-P1 PASS-A | SHFT HTR PASS-A JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SHTR-A L06 | SHFT HTR VAR-P1 PASS-A | SHFT HTR PASS-A JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1A | D02L2.5 | 10.4.24 | SHTR-A L07 | SHFT HTR VAR-P1 PASS-A | SHFT HTR PASS-A JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
13 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05FA-C04 | ESP SWGR-A PANEL-05FA | ALI LOW JB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | 110 | 19.2.20 | DR0400_1570 |  |  | ALI LOW CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L01 | ALI LOW JB-01 PASS-A | ALI L HOPPER-1 FLD-1 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L02 | ALI LOW JB-01 PASS-A | ALI L HOPPER-2 FLD-1 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L03 | ALI LOW JB-01 PASS-A | ALI L HOPPER-1 FLD-2 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L04 | ALI LOW JB-01 PASS-A | ALI L HOPPER-2 FLD-2 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L05 | ALI LOW JB-01 PASS-A | ALI L HOPPER-1 FLD-3 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L06 | ALI LOW JB-01 PASS-A | ALI L HOPPER-2 FLD-3 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L07 | ALI LOW JB-01 PASS-A | ALI L HOPPER-1 FLD-4 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L08 | ALI LOW JB-01 PASS-A | ALI L HOPPER-2 FLD-4 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L09 | ALI LOW JB-01 PASS-A | ALI L HOPPER-1 FLD-5 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L10 | ALI LOW JB-01 PASS-A | ALI L HOPPER-2 FLD-5 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L11 | ALI LOW JB-01 PASS-A | ALI L HOPPER-1 FLD-6 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L12 | ALI LOW JB-01 PASS-A | ALI L HOPPER-2 FLD-6 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L13 | ALI LOW JB-01 PASS-A | ALI L HOPPER-1 FLD-7 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-L PASS-A L14 | ALI LOW JB-01 PASS-A | ALI L HOPPER-2 FLD-7 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
14 | 1DB1A | D10C1.5 | 10.5.10 | 1DB1-05RA-C07 | ESP SWGR-A PANEL-05RA | ALI HIGH JB-01 PASS-A | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L01 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-1 FLD-1 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L02 | ALI HIGH JB-01 PASS-A | ALI L HOPPER-2 FLD-1 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L03 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-1 FLD-2 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L04 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-2 FLD-2 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L05 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-1 FLD-3 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L06 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-2 FLD-3 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L07 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-1 FLD-4 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L08 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-2 FLD-4 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L09 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-1 FLD-5 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L10 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-2 FLD-5 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L11 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-1 FLD-6 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L12 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-2 FLD-6 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L13 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-1 FLD-7 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1A | D03C1.5 | 10.5.03 | ALI-H PASS-A L14 | ALI HIGH JB-01 PASS-A | ALI H HOPPER-2 FLD-7 PASS-A | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
15 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-10FE-P01 | ESP SWGR-A PANEL-10FE | EC -01 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 46 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
16 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-10FE-P02 | ESP SWGR-A PANEL-10FE | EC -01 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 46 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
17 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11FB-P01 | ESP SWGR-A PANEL-11FB | EC -02 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 46 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
18 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11FB-P02 | ESP SWGR-A PANEL-11FB | EC -02 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 46 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
19 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11FE-P01 | ESP SWGR-A PANEL-11FE | EC -03 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 45 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
20 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11FE-P02 | ESP SWGR-A PANEL-11FE | EC -03 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 45 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
21 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-12FD-P01 | ESP SWGR-A PANEL-12FD | EC -04 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 45 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
22 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-12FD-P02 | ESP SWGR-A PANEL-12FD | EC -04 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 45 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
23 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-10RB-P01 | ESP SWGR-A PANEL-10RB | EC -05 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 43 | 23.11.2019 | DR0345_1533 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
24 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-10RB-P02 | ESP SWGR-A PANEL-10RB | EC -05 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 43 | 23.11.2019 | DR0345_1534 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
25 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11RB-P01 | ESP SWGR-A PANEL-11RB | EC -06 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 41 | 23.11.2019 | DR0345_1534 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
26 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11RB-P02 | ESP SWGR-A PANEL-11RB | EC -06 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 41 | 23.11.2019 | DR0345_1534 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
27 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11RE-P01 | ESP SWGR-A PANEL-11RE | EC -07 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 40 | 20.11.2019 | DR0345_1534 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
28 | 1DB1B | D02G120 | 10.4.10 | LTMCC1-11RE-P02 | ESP SWGR-A PANEL-11RE | EC -07 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | 40 | 20.11.2019 | DR0345_1534 |  |  | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | JHS
1 | 1DB1B | D02G120 | 10.4.10 | ECTP-B01-P01 | EC -01 PASS-B | HV TXR RECT TRF-01 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 100 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
2 | 1DB1B | D02G120 | 10.4.10 | ECTP-B01-P02 | EC -01 PASS-B | HV TXR RECT TRF-01 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 100 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
3 | 1DB1B | D10C1.5 | 10.5.10 | ECTP-B01-C01 | EC -01 PASS-B | HV TXR RECT TRF-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
4 | 1DB1B | D03C1.5 | 10.5.03 | ECTP-B01-C02 | EC -01 PASS-B | HV TXR RECT TRF-01 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
5 | 1DB1B | D02W1.5 | 10.4.27 | ECTP-B01-C03 | EC -01 PASS-B | HV TXR RECT TRF-01 PASS-B | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
6 | 1DB1B | D02G120 | 10.4.10 | ECTP-B02-P01 | EC -02 PASS-B | HV TXR RECT TRF-02 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
7 | 1DB1B | D02G120 | 10.4.10 | ECTP-B02-P02 | EC -02 PASS-B | HV TXR RECT TRF-02 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
8 | 1DB1B | D10C1.5 | 10.5.10 | ECTP-B02-C01 | EC -02 PASS-B | HV TXR RECT TRF-02 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
9 | 1DB1B | D03C1.5 | 10.5.03 | ECTP-B02-C02 | EC -02 PASS-B | HV TXR RECT TRF-02 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
10 | 1DB1B | D02W1.5 | 10.4.27 | ECTP-B02-C03 | EC -02 PASS-B | HV TXR RECT TRF-02 PASS-B | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
11 | 1DB1B | D02G120 | 10.4.10 | ECTP-B03-P01 | EC -03 PASS-B | HV TXR RECT TRF-03 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
12 | 1DB1B | D02G120 | 10.4.10 | ECTP-B03-P02 | EC -03 PASS-B | HV TXR RECT TRF-03 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
13 | 1DB1B | D10C1.5 | 10.5.10 | ECTP-B03-C01 | EC -03 PASS-B | HV TXR RECT TRF-03 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
14 | 1DB1B | D03C1.5 | 10.5.03 | ECTP-B03-C02 | EC -03 PASS-B | HV TXR RECT TRF-03 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
15 | 1DB1B | D02W1.5 | 10.4.27 | ECTP-B03-C03 | EC -03 PASS-B | HV TXR RECT TRF-03 PASS-B | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
16 | 1DB1B | D02G120 | 10.4.10 | ECTP-B04-P01 | EC -04 PASS-B | HV TXR RECT TRF-04 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
17 | 1DB1B | D02G120 | 10.4.10 | ECTP-B04-P02 | EC -04 PASS-B | HV TXR RECT TRF-04 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
18 | 1DB1B | D10C1.5 | 10.5.10 | ECTP-B04-C01 | EC -04 PASS-B | HV TXR RECT TRF-04 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
19 | 1DB1B | D03C1.5 | 10.5.03 | ECTP-B04-C02 | EC -04 PASS-B | HV TXR RECT TRF-04 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
20 | 1DB1B | D02W1.5 | 10.4.27 | ECTP-B04-C03 | EC -04 PASS-B | HV TXR RECT TRF-04 PASS-B | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
21 | 1DB1B | D02G120 | 10.4.10 | ECTP-B05-P01 | EC -05 PASS-B | HV TXR RECT TRF-05 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
22 | 1DB1B | D02G120 | 10.4.10 | ECTP-B05-P02 | EC -05 PASS-B | HV TXR RECT TRF-05 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
23 | 1DB1B | D10C1.5 | 10.5.10 | ECTP-B05-C01 | EC -05 PASS-B | HV TXR RECT TRF-05 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
24 | 1DB1B | D03C1.5 | 10.5.03 | ECTP-B05-C02 | EC -05 PASS-B | HV TXR RECT TRF-05 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
25 | 1DB1B | D02W1.5 | 10.4.27 | ECTP-B05-C03 | EC -05 PASS-B | HV TXR RECT TRF-05 PASS-B | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
26 | 1DB1B | D02G120 | 10.4.10 | ECTP-B06-P01 | EC -06 PASS-B | HV TXR RECT TRF-06 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
27 | 1DB1B | D02G120 | 10.4.10 | ECTP-B06-P02 | EC -06 PASS-B | HV TXR RECT TRF-06 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
28 | 1DB1B | D10C1.5 | 10.5.10 | ECTP-B06-C01 | EC -06 PASS-B | HV TXR RECT TRF-06 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
29 | 1DB1B | D03C1.5 | 10.5.03 | ECTP-B06-C02 | EC -06 PASS-B | HV TXR RECT TRF-06 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
30 | 1DB1B | D02W1.5 | 10.4.27 | ECTP-B06-C03 | EC -06 PASS-B | HV TXR RECT TRF-06 PASS-B | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
31 | 1DB1B | D02G120 | 10.4.10 | ECTP-B07-P01 | EC -07 PASS-B | HV TXR RECT TRF-07 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
32 | 1DB1B | D02G120 | 10.4.10 | ECTP-B07-P02 | EC -07 PASS-B | HV TXR RECT TRF-07 PASS-B | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 50 | [5 empty] | POWER | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
33 | 1DB1B | D10C1.5 | 10.5.10 | ECTP-B07-C01 | EC -07 PASS-B | HV TXR RECT TRF-07 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | TRF PROTECTION | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
34 | 1DB1B | D03C1.5 | 10.5.03 | ECTP-B07-C02 | EC -07 PASS-B | HV TXR RECT TRF-07 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | PRI VOLT FDBK | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
35 | 1DB1B | D02W1.5 | 10.4.27 | ECTP-B07-C03 | EC -07 PASS-B | HV TXR RECT TRF-07 PASS-B | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | 100 | [5 empty] | HV VOLT/CURRENT | EC | ER-02 OTHER TRAYS TO MARK |  | JHS | JHS
1 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-10RC-P01 | ESP SWGR-A PANEL-10RC | CERM-01 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
2 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-10RD-P01 | ESP SWGR-A PANEL-10RD | CERM-02 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
3 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-11RC-P01 | ESP SWGR-A PANEL-11RC | CERM-03 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
4 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-11RD-P01 | ESP SWGR-A PANEL-11RD | CERM-04 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
5 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-12RB-P01 | ESP SWGR-A PANEL-12RB | CERM-05 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
6 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-12RC-P01 | ESP SWGR-A PANEL-12RC | CERM-06 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
7 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-12RD-P01 | ESP SWGR-A PANEL-12RD | CERM-07 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
8 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-12RE-P01 | ESP SWGR-A PANEL-12RE | EERM-01 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
9 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-12RF-P01 | ESP SWGR-A PANEL-12RF | EERM-02 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
10 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-13RB-P01 | ESP SWGR-A PANEL-13RB | EERM-03 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
11 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-13RC-P01 | ESP SWGR-A PANEL-13RC | EERM-04 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
12 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-13RD-P01 | ESP SWGR-A PANEL-13RD | EERM-05 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
13 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-13RE-P01 | ESP SWGR-A PANEL-13RE | EERM-06 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
14 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-13RF-P01 | ESP SWGR-A PANEL-13RF | EERM-07 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
15 | 1DB1B | D03C2.5 | 10.5.04 | 1DB1-14RC-P01 | ESP SWGR-A PANEL-14RC | GDRM-01 PASS-B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | GDRM POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
16 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12RA-C01 | ESP SWGR-A PANEL-12RA | CERM LPBJB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
17 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12RA-C02 | ESP SWGR-A PANEL-12RA | CERM LPBJB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
18 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12RA-C03 | ESP SWGR-A PANEL-12RA | CERM LPBJB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
19 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12RA-C04 | ESP SWGR-A PANEL-12RA | EERM LPBJB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
20 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12RA-C05 | ESP SWGR-A PANEL-12RA | EERM LPBJB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
21 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12RA-C06 | ESP SWGR-A PANEL-12RA | EERM LPBJB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LPB CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-CERM-L01 | CERM LPBJB-01 PASS-B | CERM LPB-01 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-CERM-L02 | CERM LPBJB-01 PASS-B | CERM LPB-02 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-CERM-L03 | CERM LPBJB-01 PASS-B | CERM LPB-03 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-CERM-L04 | CERM LPBJB-01 PASS-B | CERM LPB-04 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-CERM-L05 | CERM LPBJB-01 PASS-B | CERM LPB-05 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-CERM-L06 | CERM LPBJB-01 PASS-B | CERM LPB-06 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-CERM-L07 | CERM LPBJB-01 PASS-B | CERM LPB-07 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | CERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-GDRM-L01 | CERM LPBJB-01 PASS-B | GDRM LPB-01 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | GDRM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-EERM-L01 | EERM LPBJB-01 PASS-B | EERM LPB-01 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-EERM-L02 | EERM LPBJB-01 PASS-B | EERM LPB-02 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-EERM-L03 | EERM LPBJB-01 PASS-B | EERM LPB-03 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-EERM-L04 | EERM LPBJB-01 PASS-B | EERM LPB-04 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-EERM-L05 | EERM LPBJB-01 PASS-B | EERM LPB-05 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-EERM-L06 | EERM LPBJB-01 PASS-B | EERM LPB-06 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-EERM-L07 | EERM LPBJB-01 PASS-B | EERM LPB-07 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | EERM LOOP |  | SITE ROUTE |  | RPT | RPT
1 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-12FA-P01 | ESP SWGR-A PANEL-10FB | HH PJB-01 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB01 B-L01 | HH PJB-01 PASS-B | HOPR2 FLD-1 PASS-B CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB01 B-L02 | HH PJB-01 PASS-B | HOPR2 FLD-1 PASS-B CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB01 B-L03 | HH PJB-01 PASS-B | HOPR2 FLD-1 PASS-B CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
2 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-10FC-P01 | ESP SWGR-A PANEL-10FC | HH PJB-02 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB02 B-L01 | HH PJB-02 PASS-B | HOPR2 FLD-2 PASS-B CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB02 B-L02 | HH PJB-02 PASS-B | HOPR2 FLD-2 PASS-B CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB02 B-L03 | HH PJB-02 PASS-B | HOPR2 FLD-2 PASS-B CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
3 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-10FD-P01 | ESP SWGR-A PANEL-10FD | HH PJB-03 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB03 B-L01 | HH PJB-03 PASS-B | HOPR2 FLD-3 PASS-B CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB03 B-L02 | HH PJB-03 PASS-B | HOPR2 FLD-3 PASS-B CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB03 B-L03 | HH PJB-03 PASS-B | HOPR2 FLD-3 PASS-B CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
4 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-11RC-P01 | ESP SWGR-A PANEL-11RC | HH PJB-04 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB04 B-L01 | HH PJB-04 PASS-B | HOPR2 FLD-4 PASS-B CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB04 B-L02 | HH PJB-04 PASS-B | HOPR2 FLD-4 PASS-B CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB04 B-L03 | HH PJB-04 PASS-B | HOPR2 FLD-4 PASS-B CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
5 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-11FD-P01 | ESP SWGR-A PANEL-11FD | HH PJB-05 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB05 B-L01 | HH PJB-05 PASS-B | HOPR2 FLD-5 PASS-B CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB05 B-L02 | HH PJB-05 PASS-B | HOPR2 FLD-5 PASS-B CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB05 B-L03 | HH PJB-05 PASS-B | HOPR2 FLD-5 PASS-B CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
6 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-12FB-P01 | ESP SWGR-A PANEL-12FB | HH PJB-06 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB06 B-L01 | HH PJB-06 PASS-B | HOPR2 FLD-6 PASS-B CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB06 B-L02 | HH PJB-06 PASS-B | HOPR2 FLD-6 PASS-B CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB06 B-L03 | HH PJB-06 PASS-B | HOPR2 FLD-6 PASS-B CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
7 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-15FB-P01 | ESP SWGR-A PANEL-15FB | HH PJB-07 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | HH POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB07 B-L01 | HH PJB-07 PASS-B | HOPR2 FLD-7 PASS-B CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB07 B-L02 | HH PJB-07 PASS-B | HOPR2 FLD-7 PASS-B CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | HHPJB07 B-L03 | HH PJB-07 PASS-B | HOPR2 FLD-7 PASS-B CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 5 | [5 empty] | HH POWER LOOP |  |  |  | RPT | RPT
8 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12FA-C01 | ESP SWGR-A PANEL-12FA | HH TH JB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | HH CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
9 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12FA-C02 | ESP SWGR-A PANEL-12FA | HH TH JB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | HH CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-HH-L01 | HH TH JB-01 PASS-B | THERMOSTAT-HH-1 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-HH-L02 | HH TH JB-01 PASS-B | THERMOSTAT-HH-2 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-HH-L03 | HH TH JB-01 PASS-B | THERMOSTAT-HH-3 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-HH-L04 | HH TH JB-01 PASS-B | THERMOSTAT-HH-4 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-HH-L05 | HH TH JB-01 PASS-B | THERMOSTAT-HH-5 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-HH-L06 | HH TH JB-01 PASS-B | THERMOSTAT-HH-6 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | PASS-B-HH-L07 | HH TH JB-01 PASS-B | THERMOSTAT-HH-7 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | THERMOSTAT LOOP |  | SITE ROUTE |  | RPT | RPT
10 | 1DB1B | D03Q035 | 10.4.13 | 1DB1-14FA-P01 | ESP SWGR-A PANEL-14FA | SUPP HTR JB01 VAR-P2 PASS-B | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 100 | [5 empty] | SUPP HTR POWER | RPT LT CABLE 1DRUM |  |  | RPT | RPT
| 1DB1B | D03Q035 | 10.4.13 | SUPPHTR L02 | SUPP HTR JB01 VAR-P2 PASS-B | SUPP HTR JB02 VAR-P3 PASS-B | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | SUPP HTR POWER |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB01 L01 | SUPP HTR JB01 VAR-P2 PASS-B | SUHTR ROW1 PASS-B JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB01 L02 | SUPP HTR JB01 VAR-P2 PASS-B | SUHTR ROW1 PASS-B JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB01 L03 | SUPP HTR JB01 VAR-P2 PASS-B | SUHTR ROW1 PASS-B JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB01 L04 | SUPP HTR JB01 VAR-P2 PASS-B | SUHTR ROW1 PASS-B JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB01 L05 | SUPP HTR JB01 VAR-P2 PASS-B | SUHTR ROW1 PASS-B JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB01 L06 | SUPP HTR JB01 VAR-P2 PASS-B | SUHTR ROW1 PASS-B JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB01 L07 | SUPP HTR JB01 VAR-P2 PASS-B | SUHTR ROW1 PASS-B JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB02 L01 | SUPP HTR JB02 VAR-P3 PASS-B | SUHTR ROW2 PASS-B JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB02 L02 | SUPP HTR JB02 VAR-P3 PASS-B | SUHTR ROW2 PASS-B JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB02 L03 | SUPP HTR JB02 VAR-P3 PASS-B | SUHTR ROW2 PASS-B JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB02 L04 | SUPP HTR JB02 VAR-P3 PASS-B | SUHTR ROW2 PASS-B JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB02 L05 | SUPP HTR JB02 VAR-P3 PASS-B | SUHTR ROW2 PASS-B JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB02 L06 | SUPP HTR JB02 VAR-P3 PASS-B | SUHTR ROW2 PASS-B JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SUHTR-B JB02 L07 | SUPP HTR JB02 VAR-P3 PASS-B | SUHTR ROW2 PASS-B JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SUPP HTR POWER LOOP |  |  |  | RPT | RPT
11 | 1DB1B | D03C1.5 | 10.5.03 | 1DB1-12FA-C03 | ESP SWGR-A PANEL-12FA | SUPP HTR TH-P1 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | SUPP HTR CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
12 | 1DB1B | D03Q010 | 10.4.11 | 1DB1-14FB-P01 | ESP SWGR-A PANEL-14FB | SHFT HTR VAR-P1 PASS-B | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | SHFT HTR POWER | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SHTR-B L01 | SHFT HTR VAR-P1 PASS-B | SHFT HTR PASS-B JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SHTR-B L02 | SHFT HTR VAR-P1 PASS-B | SHFT HTR PASS-B JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SHTR-B L03 | SHFT HTR VAR-P1 PASS-B | SHFT HTR PASS-B JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SHTR-B L04 | SHFT HTR VAR-P1 PASS-B | SHFT HTR PASS-B JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SHTR-B L05 | SHFT HTR VAR-P1 PASS-B | SHFT HTR PASS-B JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SHTR-B L06 | SHFT HTR VAR-P1 PASS-B | SHFT HTR PASS-B JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
| 1DB1B | D02L2.5 | 10.4.24 | SHTR-B L07 | SHFT HTR VAR-P1 PASS-B | SHFT HTR PASS-B JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | SHFT HTR POWER LOOP |  |  |  | RPT | RPT
13 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12FA-C04 | ESP SWGR-A PANEL-12FA | ALI LOW JB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | ALI LOW CONTROL | EC | ER-02 OTHER TRAYS TO MARK |  | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L01 | ALI LOW JB-01 PASS-B | ALI L HOPPER-1 FLD-1 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L02 | ALI LOW JB-01 PASS-B | ALI L HOPPER-2 FLD-1 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L03 | ALI LOW JB-01 PASS-B | ALI L HOPPER-1 FLD-2 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L04 | ALI LOW JB-01 PASS-B | ALI L HOPPER-2 FLD-2 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L05 | ALI LOW JB-01 PASS-B | ALI L HOPPER-1 FLD-3 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L06 | ALI LOW JB-01 PASS-B | ALI L HOPPER-2 FLD-3 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L07 | ALI LOW JB-01 PASS-B | ALI L HOPPER-1 FLD-4 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L08 | ALI LOW JB-01 PASS-B | ALI L HOPPER-2 FLD-4 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L09 | ALI LOW JB-01 PASS-B | ALI L HOPPER-1 FLD-5 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L10 | ALI LOW JB-01 PASS-B | ALI L HOPPER-2 FLD-5 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L11 | ALI LOW JB-01 PASS-B | ALI L HOPPER-1 FLD-6 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L12 | ALI LOW JB-01 PASS-B | ALI L HOPPER-2 FLD-6 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L13 | ALI LOW JB-01 PASS-B | ALI L HOPPER-1 FLD-7 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-L PASS-B L14 | ALI LOW JB-01 PASS-B | ALI L HOPPER-2 FLD-7 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
14 | 1DB1B | D10C1.5 | 10.5.10 | 1DB1-12RA-C07 | ESP SWGR-A PANEL-12RA | ALI HIGH JB-01 PASS-B | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L01 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-1 FLD-1 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L02 | ALI HIGH JB-01 PASS-B | ALI L HOPPER-2 FLD-1 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L03 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-1 FLD-2 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L04 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-2 FLD-2 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L05 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-1 FLD-3 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L06 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-2 FLD-3 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L07 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-1 FLD-4 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L08 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-2 FLD-4 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L09 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-1 FLD-5 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L10 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-2 FLD-5 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L11 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-1 FLD-6 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L12 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-2 FLD-6 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L13 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-1 FLD-7 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
| 1DB1B | D03C1.5 | 10.5.03 | ALI-H PASS-B L14 | ALI HIGH JB-01 PASS-B | ALI H HOPPER-2 FLD-7 PASS-B | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [9 empty] | RPT | RPT
1 | 1DB2C | D03Q095 | 10.4.15 | 1DB2 05FA P01 (1DB2 05FA P01) | 415V SWGR O/G MODULE #1DB2 05FA | FEEDER TO LDB - ESP SWGR ROOM (1UE) (100kVA) | 03C X 095 XLPE-Al FRLS ( 1.1 kV ) | 10 | [5 empty] | MLDB SUPPLY |  |  |  | RPT | PEM
1 | 1DB2C | D01Q630 | 10.4.05 | 1DB2 03RB P01 | 415V SWGR O/G MODULE #1DB2 03RB | ESP AC-VENT MCC # 1TB SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 30 | 25 | 28.11.2019 | DR1050_0011 | [6 empty] | RPT | PEM
2 | 1DB2C | D01Q630 | 10.4.05 | 1DB2 03RB P02 | 415V SWGR O/G MODULE #1DB2 03RB | ESP AC-VENT MCC # 1TB SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 30 | 25 | 28.11.2019 | DR1050_0011 | [6 empty] | RPT | PEM
3 | 1DB2C | D01Q630 | 10.4.05 | 1DB2 03RB P03 | 415V SWGR O/G MODULE #1DB2 03RB | ESP AC-VENT MCC # 1TB SEC-B | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 30 | 25 | 28.11.2019 | DR1050_0011 | [6 empty] | RPT | PEM
4 | 1DB2C | D01Q400 | 10.4.04 | 1DB2 03RB P04 (1DB2 03RB P04) | 415V SWGR O/G MODULE #1DB2 03RB | ESP AC-VENT MCC # 1TB SEC-B | 01C X 400 XLPE-Al FRLS ( 1.1 kV ) | 30 | [9 empty] | RPT | PEM
1 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-04FA-P01 | ESP SWGR-B PANEL-04FA | EC -01 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 27 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
2 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-04FA-P02 | ESP SWGR-B PANEL-04FA | EC -01 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 27 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
3 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-07FA-P01 | ESP SWGR-B PANEL-07FA | EC -02 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 30 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
4 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-07FA-P02 | ESP SWGR-B PANEL-07FA | EC -02 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 30 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
5 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-08RA-P01 | ESP SWGR-B PANEL-08RA | EC -03 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 31 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
6 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-08RA-P02 | ESP SWGR-B PANEL-08RA | EC -03 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 31 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
7 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-06RA-P01 | ESP SWGR-B PANEL-06RA | EC -04 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 28 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
8 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-06RA-P02 | ESP SWGR-B PANEL-06RA | EC -04 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 28 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
9 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-05RA-P01 | ESP SWGR-B PANEL-05RA | EC -05 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 26 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
10 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-05RA-P02 | ESP SWGR-B PANEL-05RA | EC -05 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 26 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
11 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-04RA-P01 | ESP SWGR-B PANEL-04RA | EC -06 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 24 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
12 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-04RA-P02 | ESP SWGR-B PANEL-04RA | EC -06 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 24 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
13 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-02RB-P01 | ESP SWGR-B PANEL-02RB | EC -07 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 24 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
14 | 1DB2C | D02G120 | 10.4.10 | LTMCC2-02RB-P02 | ESP SWGR-B PANEL-02RB | EC -07 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 24 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
15 | 1DB2C | D02G120 | 10.4.10 | ECTP-C01-P01 | EC -01 PASS-C | HV TXR RECT TRF-01 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
16 | 1DB2C | D02G120 | 10.4.10 | ECTP-C01-P02 | EC -01 PASS-C | HV TXR RECT TRF-01 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
17 | 1DB2C | D10C1.5 | 10.5.10 | ECTP-C01-C01 | EC -01 PASS-C | HV TXR RECT TRF-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
18 | 1DB2C | D03C1.5 | 10.5.03 | ECTP-C01-C02 | EC -01 PASS-C | HV TXR RECT TRF-01 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
19 | 1DB2C | D02W1.5 | 10.4.27 | ECTP-C01-C03 | EC -01 PASS-C | HV TXR RECT TRF-01 PASS-C | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
20 | 1DB2C | D02G120 | 10.4.10 | ECTP-C02-P01 | EC -02 PASS-C | HV TXR RECT TRF-02 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
21 | 1DB2C | D02G120 | 10.4.10 | ECTP-C02-P02 | EC -02 PASS-C | HV TXR RECT TRF-02 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
22 | 1DB2C | D10C1.5 | 10.5.10 | ECTP-C02-C01 | EC -02 PASS-C | HV TXR RECT TRF-02 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
23 | 1DB2C | D03C1.5 | 10.5.03 | ECTP-C02-C02 | EC -02 PASS-C | HV TXR RECT TRF-02 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
24 | 1DB2C | D02W1.5 | 10.4.27 | ECTP-C02-C03 | EC -02 PASS-C | HV TXR RECT TRF-02 PASS-C | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
25 | 1DB2C | D02G120 | 10.4.10 | ECTP-C03-P01 | EC -03 PASS-C | HV TXR RECT TRF-03 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
26 | 1DB2C | D02G120 | 10.4.10 | ECTP-C03-P02 | EC -03 PASS-C | HV TXR RECT TRF-03 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
27 | 1DB2C | D10C1.5 | 10.5.10 | ECTP-C03-C01 | EC -03 PASS-C | HV TXR RECT TRF-03 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
28 | 1DB2C | D03C1.5 | 10.5.03 | ECTP-C03-C02 | EC -03 PASS-C | HV TXR RECT TRF-03 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
29 | 1DB2C | D02W1.5 | 10.4.27 | ECTP-C03-C03 | EC -03 PASS-C | HV TXR RECT TRF-03 PASS-C | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
30 | 1DB2C | D02G120 | 10.4.10 | ECTP-C04-P01 | EC -04 PASS-C | HV TXR RECT TRF-04 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
31 | 1DB2C | D02G120 | 10.4.10 | ECTP-C04-P02 | EC -04 PASS-C | HV TXR RECT TRF-04 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
32 | 1DB2C | D10C1.5 | 10.5.10 | ECTP-C04-C01 | EC -04 PASS-C | HV TXR RECT TRF-04 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
33 | 1DB2C | D03C1.5 | 10.5.03 | ECTP-C04-C02 | EC -04 PASS-C | HV TXR RECT TRF-04 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
34 | 1DB2C | D02W1.5 | 10.4.27 | ECTP-C04-C03 | EC -04 PASS-C | HV TXR RECT TRF-04 PASS-C | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
35 | 1DB2C | D02G120 | 10.4.10 | ECTP-C05-P01 | EC -05 PASS-C | HV TXR RECT TRF-05 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
36 | 1DB2C | D02G120 | 10.4.10 | ECTP-C05-P02 | EC -05 PASS-C | HV TXR RECT TRF-05 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
37 | 1DB2C | D10C1.5 | 10.5.10 | ECTP-C05-C01 | EC -05 PASS-C | HV TXR RECT TRF-05 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
38 | 1DB2C | D03C1.5 | 10.5.03 | ECTP-C05-C02 | EC -05 PASS-C | HV TXR RECT TRF-05 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
39 | 1DB2C | D02W1.5 | 10.4.27 | ECTP-C05-C03 | EC -05 PASS-C | HV TXR RECT TRF-05 PASS-C | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
40 | 1DB2C | D02G120 | 10.4.10 | ECTP-C06-P01 | EC -06 PASS-C | HV TXR RECT TRF-06 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
41 | 1DB2C | D02G120 | 10.4.10 | ECTP-C06-P02 | EC -06 PASS-C | HV TXR RECT TRF-06 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
42 | 1DB2C | D10C1.5 | 10.5.10 | ECTP-C06-C01 | EC -06 PASS-C | HV TXR RECT TRF-06 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
43 | 1DB2C | D03C1.5 | 10.5.03 | ECTP-C06-C02 | EC -06 PASS-C | HV TXR RECT TRF-06 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
44 | 1DB2C | D02W1.5 | 10.4.27 | ECTP-C06-C03 | EC -06 PASS-C | HV TXR RECT TRF-06 PASS-C | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
45 | 1DB2C | D02G120 | 10.4.10 | ECTP-C07-P01 | EC -07 PASS-C | HV TXR RECT TRF-07 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
46 | 1DB2C | D02G120 | 10.4.10 | ECTP-C07-P02 | EC -07 PASS-C | HV TXR RECT TRF-07 PASS-C | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
47 | 1DB2C | D10C1.5 | 10.5.10 | ECTP-C07-C01 | EC -07 PASS-C | HV TXR RECT TRF-07 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
48 | 1DB2C | D03C1.5 | 10.5.03 | ECTP-C07-C02 | EC -07 PASS-C | HV TXR RECT TRF-07 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
49 | 1DB2C | D02W1.5 | 10.4.27 | ECTP-C07-C03 | EC -07 PASS-C | HV TXR RECT TRF-07 PASS-C | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
50 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-02RC-P01 | ESP SWGR-B PANEL-02RC | CERM-01 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
51 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-02RD-P01 | ESP SWGR-B PANEL-02RD | CERM-02 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
52 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-02RE-P01 | ESP SWGR-B PANEL-02RE | CERM-03 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
53 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-04RB-P01 | ESP SWGR-B PANEL-04RB | CERM-04 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
54 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-04RC-P01 | ESP SWGR-B PANEL-04RC | CERM-05 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
55 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-04RD-P01 | ESP SWGR-B PANEL-04RD | CERM-06 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
56 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-05RB-P01 | ESP SWGR-B PANEL-05RB | CERM-07 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
57 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-05RC-P01 | ESP SWGR-B PANEL-05RC | EERM-01 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
58 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-05RD-P01 | ESP SWGR-B PANEL-05RD | EERM-02 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
59 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-06RB-P01 | ESP SWGR-B PANEL-06RB | EERM-03 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
60 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-07RB-P01 | ESP SWGR-B PANEL-07RB | EERM-04 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
61 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-07RC-P01 | ESP SWGR-B PANEL-07RC | EERM-05 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
62 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-07RD-P01 | ESP SWGR-B PANEL-07RD | EERM-06 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
63 | 1DB2C | D03C2.5 | 10.5.04 | 1DB2-08RB-P01 | ESP SWGR-B PANEL-08RB | EERM-07 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
64 | 1DB2C | D03C2.5 | 10.5.04 | 1DB1-08RC-P01 | ESP SWGR-A PANEL-08RC | GDRM-01 PASS-C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
65 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AR-C01 | ESP SWGR-B PANEL-01AR | CERM LPBJB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
66 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AR-C02 | ESP SWGR-B PANEL-01AR | CERM LPBJB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
67 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AR-C03 | ESP SWGR-B PANEL-01AR | CERM LPBJB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
68 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AR-C04 | ESP SWGR-B PANEL-01AR | EERM LPBJB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
69 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AR-C05 | ESP SWGR-B PANEL-01AR | EERM LPBJB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
70 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AR-C06 | ESP SWGR-B PANEL-01AR | EERM LPBJB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
71 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-CERM-L01 | CERM LPBJB-01 PASS-C | CERM LPB-01 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
72 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-CERM-L02 | CERM LPBJB-01 PASS-C | CERM LPB-02 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
73 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-CERM-L03 | CERM LPBJB-01 PASS-C | CERM LPB-03 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
74 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-CERM-L04 | CERM LPBJB-01 PASS-C | CERM LPB-04 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
75 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-CERM-L05 | CERM LPBJB-01 PASS-C | CERM LPB-05 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
76 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-CERM-L06 | CERM LPBJB-01 PASS-C | CERM LPB-06 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
77 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-CERM-L07 | CERM LPBJB-01 PASS-C | CERM LPB-07 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
78 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-GDRM-L01 | CERM LPBJB-01 PASS-C | GDRM LPB-01 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
79 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-EERM-L01 | EERM LPBJB-01 PASS-C | EERM LPB-01 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
80 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-EERM-L02 | EERM LPBJB-01 PASS-C | EERM LPB-02 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
81 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-EERM-L03 | EERM LPBJB-01 PASS-C | EERM LPB-03 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
82 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-EERM-L04 | EERM LPBJB-01 PASS-C | EERM LPB-04 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
83 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-EERM-L05 | EERM LPBJB-01 PASS-C | EERM LPB-05 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
84 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-EERM-L06 | EERM LPBJB-01 PASS-C | EERM LPB-06 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
85 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-EERM-L07 | EERM LPBJB-01 PASS-C | EERM LPB-07 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
86 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-04FB-P01 | ESP SWGR-B PANEL-04FB | HH PJB-01 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
87 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB01 C-L01 | HH PJB-01 PASS-C | HOPR2 FLD-1 PASS-C CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
88 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB01 C-L02 | HH PJB-01 PASS-C | HOPR2 FLD-1 PASS-C CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
89 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB01 C-L03 | HH PJB-01 PASS-C | HOPR2 FLD-1 PASS-C CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
90 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-04FC-P01 | ESP SWGR-B PANEL-04FC | HH PJB-02 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
91 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB02 C-L01 | HH PJB-02 PASS-C | HOPR2 FLD-2 PASS-C CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
92 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB02 C-L02 | HH PJB-02 PASS-C | HOPR2 FLD-2 PASS-C CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
93 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB02 C-L03 | HH PJB-02 PASS-C | HOPR2 FLD-2 PASS-C CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
94 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-04FD-P01 | ESP SWGR-B PANEL-04FD | HH PJB-03 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
95 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB03 C-L01 | HH PJB-03 PASS-C | HOPR2 FLD-3 PASS-C CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
96 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB03 C-L02 | HH PJB-03 PASS-C | HOPR2 FLD-3 PASS-C CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
97 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB03 C-L03 | HH PJB-03 PASS-C | HOPR2 FLD-3 PASS-C CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
98 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-04FE-P01 | ESP SWGR-B PANEL-04FE | HH PJB-04 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
99 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB04 C-L01 | HH PJB-04 PASS-C | HOPR2 FLD-4 PASS-C CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
100 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB04 C-L02 | HH PJB-04 PASS-C | HOPR2 FLD-4 PASS-C CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
101 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB04 C-L03 | HH PJB-04 PASS-C | HOPR2 FLD-4 PASS-C CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
102 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-05FD-P01 | ESP SWGR-B PANEL-05FD | HH PJB-05 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
103 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB05 C-L01 | HH PJB-05 PASS-C | HOPR2 FLD-5 PASS-C CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
104 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB05 C-L02 | HH PJB-05 PASS-C | HOPR2 FLD-5 PASS-C CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
105 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB05 C-L03 | HH PJB-05 PASS-C | HOPR2 FLD-5 PASS-C CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
106 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-07FB-P01 | ESP SWGR-B PANEL-07FB | HH PJB-06 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
107 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB06 C-L01 | HH PJB-06 PASS-C | HOPR2 FLD-6 PASS-C CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
108 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB06 C-L02 | HH PJB-06 PASS-C | HOPR2 FLD-6 PASS-C CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
109 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB06 C-L03 | HH PJB-06 PASS-C | HOPR2 FLD-6 PASS-C CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
110 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-07FC-P01 | ESP SWGR-B PANEL-07FC | HH PJB-07 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
111 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB07 C-L01 | HH PJB-07 PASS-C | HOPR2 FLD-7 PASS-C CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
112 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB07 C-L02 | HH PJB-07 PASS-C | HOPR2 FLD-7 PASS-C CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
113 | 1DB2C | D02L2.5 | 10.4.24 | HHPJB07 C-L03 | HH PJB-07 PASS-C | HOPR2 FLD-7 PASS-C CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
114 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AF-C01 | ESP SWGR-B PANEL-01AF | HH TH JB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
115 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AF-C02 | ESP SWGR-B PANEL-01AF | HH TH JB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
116 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-HH-L01 | HH TH JB-01 PASS-C | THERMOSTAT-HH-1 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
117 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-HH-L02 | HH TH JB-01 PASS-C | THERMOSTAT-HH-2 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
118 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-HH-L03 | HH TH JB-01 PASS-C | THERMOSTAT-HH-3 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
119 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-HH-L04 | HH TH JB-01 PASS-C | THERMOSTAT-HH-4 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
120 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-HH-L05 | HH TH JB-01 PASS-C | THERMOSTAT-HH-5 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
121 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-HH-L06 | HH TH JB-01 PASS-C | THERMOSTAT-HH-6 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
122 | 1DB2C | D03C1.5 | 10.5.03 | PASS-C-HH-L07 | HH TH JB-01 PASS-C | THERMOSTAT-HH-7 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
123 | 1DB2C | D03Q035 | 10.4.13 | 1DB2-02FC-P01 | ESP SWGR-A PANEL-14FA | SUPP HTR JB01 VAR-P2 PASS-C | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 100 | [9 empty] | RPT | RPT
124 | 1DB2C | D03Q035 | 10.4.13 | SUPPHTR L02 | SUPP HTR JB01 VAR-P2 PASS-C | SUPP HTR JB02 VAR-P3 PASS-C | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [9 empty] | RPT | RPT
125 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB01 L01 | SUPP HTR JB01 VAR-P2 PASS-C | SUHTR ROW1 PASS-C JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
126 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB01 L02 | SUPP HTR JB01 VAR-P2 PASS-C | SUHTR ROW1 PASS-C JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
127 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB01 L03 | SUPP HTR JB01 VAR-P2 PASS-C | SUHTR ROW1 PASS-C JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
128 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB01 L04 | SUPP HTR JB01 VAR-P2 PASS-C | SUHTR ROW1 PASS-C JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
129 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB01 L05 | SUPP HTR JB01 VAR-P2 PASS-C | SUHTR ROW1 PASS-C JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
130 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB01 L06 | SUPP HTR JB01 VAR-P2 PASS-C | SUHTR ROW1 PASS-C JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
131 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB01 L07 | SUPP HTR JB01 VAR-P2 PASS-C | SUHTR ROW1 PASS-C JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
132 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB02 L01 | SUPP HTR JB02 VAR-P3 PASS-C | SUHTR ROW2 PASS-C JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
133 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB02 L02 | SUPP HTR JB02 VAR-P3 PASS-C | SUHTR ROW2 PASS-C JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
134 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB02 L03 | SUPP HTR JB02 VAR-P3 PASS-C | SUHTR ROW2 PASS-C JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
135 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB02 L04 | SUPP HTR JB02 VAR-P3 PASS-C | SUHTR ROW2 PASS-C JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
136 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB02 L05 | SUPP HTR JB02 VAR-P3 PASS-C | SUHTR ROW2 PASS-C JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
137 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB02 L06 | SUPP HTR JB02 VAR-P3 PASS-C | SUHTR ROW2 PASS-C JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
138 | 1DB2C | D02L2.5 | 10.4.24 | SUHTR-C JB02 L07 | SUPP HTR JB02 VAR-P3 PASS-C | SUHTR ROW2 PASS-C JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
139 | 1DB2C | D03C1.5 | 10.5.03 | 1DB2-01AF-C03 | ESP SWGR-B PANEL-01AF | SUPP HTR TH-P1 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
140 | 1DB2C | D03Q010 | 10.4.11 | 1DB2-02FB-P01 | ESP SWGR-B PANEL-02FB | SHFT HTR VAR-P1 PASS-C | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
141 | 1DB2C | D02L2.5 | 10.4.24 | SHTR-C L01 | SHFT HTR VAR-P1 PASS-C | SHFT HTR PASS-C JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
142 | 1DB2C | D02L2.5 | 10.4.24 | SHTR-C L02 | SHFT HTR VAR-P1 PASS-C | SHFT HTR PASS-C JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
143 | 1DB2C | D02L2.5 | 10.4.24 | SHTR-C L03 | SHFT HTR VAR-P1 PASS-C | SHFT HTR PASS-C JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
144 | 1DB2C | D02L2.5 | 10.4.24 | SHTR-C L04 | SHFT HTR VAR-P1 PASS-C | SHFT HTR PASS-C JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
145 | 1DB2C | D02L2.5 | 10.4.24 | SHTR-C L05 | SHFT HTR VAR-P1 PASS-C | SHFT HTR PASS-C JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
146 | 1DB2C | D02L2.5 | 10.4.24 | SHTR-C L06 | SHFT HTR VAR-P1 PASS-C | SHFT HTR PASS-C JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
147 | 1DB2C | D02L2.5 | 10.4.24 | SHTR-C L07 | SHFT HTR VAR-P1 PASS-C | SHFT HTR PASS-C JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
148 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AF-C04 | ESP SWGR-B PANEL-01AF | ALI LOW JB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
149 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L01 | ALI LOW JB-01 PASS-C | ALI L HOPPER-1 FLD-1 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
150 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L02 | ALI LOW JB-01 PASS-C | ALI L HOPPER-2 FLD-1 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
151 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L03 | ALI LOW JB-01 PASS-C | ALI L HOPPER-1 FLD-2 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
152 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L04 | ALI LOW JB-01 PASS-C | ALI L HOPPER-2 FLD-2 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
153 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L05 | ALI LOW JB-01 PASS-C | ALI L HOPPER-1 FLD-3 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
154 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L06 | ALI LOW JB-01 PASS-C | ALI L HOPPER-2 FLD-3 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
155 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L07 | ALI LOW JB-01 PASS-C | ALI L HOPPER-1 FLD-4 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
156 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L08 | ALI LOW JB-01 PASS-C | ALI L HOPPER-2 FLD-4 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
157 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L09 | ALI LOW JB-01 PASS-C | ALI L HOPPER-1 FLD-5 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
158 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L10 | ALI LOW JB-01 PASS-C | ALI L HOPPER-2 FLD-5 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
159 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L11 | ALI LOW JB-01 PASS-C | ALI L HOPPER-1 FLD-6 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
160 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L12 | ALI LOW JB-01 PASS-C | ALI L HOPPER-2 FLD-6 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
161 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L13 | ALI LOW JB-01 PASS-C | ALI L HOPPER-1 FLD-7 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
162 | 1DB2C | D03C1.5 | 10.5.03 | ALI-L PASS-C L14 | ALI LOW JB-01 PASS-C | ALI L HOPPER-2 FLD-7 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
163 | 1DB2C | D10C1.5 | 10.5.10 | 1DB2-01AR-C07 | ESP SWGR-B PANEL-01AR | ALI HIGH JB-01 PASS-C | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
164 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L01 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-1 FLD-1 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
165 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L02 | ALI HIGH JB-01 PASS-C | ALI L HOPPER-2 FLD-1 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
166 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L03 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-1 FLD-2 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
167 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L04 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-2 FLD-2 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
168 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L05 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-1 FLD-3 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
169 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L06 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-2 FLD-3 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
170 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L07 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-1 FLD-4 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
171 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L08 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-2 FLD-4 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
172 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L09 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-1 FLD-5 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
173 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L10 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-2 FLD-5 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
174 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L11 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-1 FLD-6 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
175 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L12 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-2 FLD-6 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
176 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L13 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-1 FLD-7 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
177 | 1DB2C | D03C1.5 | 10.5.03 | ALI-H PASS-C L14 | ALI HIGH JB-01 PASS-C | ALI H HOPPER-2 FLD-7 PASS-C | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
1 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-10FE-P01 | ESP SWGR-B PANEL-10FE | EC -01 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 49 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
2 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-10FE-P02 | ESP SWGR-B PANEL-10FE | EC -01 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 49 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
3 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11FB-P01 | ESP SWGR-B PANEL-11FB | EC -02 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 49 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
4 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11FB-P02 | ESP SWGR-B PANEL-11FB | EC -02 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 49 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
5 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11FE-P01 | ESP SWGR-B PANEL-11FE | EC -03 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 50 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
6 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11FE-P02 | ESP SWGR-B PANEL-11FE | EC -03 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 50 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
7 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-12FD-P01 | ESP SWGR-B PANEL-12FD | EC -04 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 52 | 20.11.2019 | DR0345_1534 | [6 empty] | RPT | JHS
8 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-12FD-P02 | ESP SWGR-B PANEL-12FD | EC -04 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 52 | 20.11.2019 | DR0345_1535 | [6 empty] | RPT | JHS
9 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-10RB-P01 | ESP SWGR-B PANEL-10RB | EC -05 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 54 | 20.11.2019 | DR0345_1535 | [6 empty] | RPT | JHS
10 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-10RB-P02 | ESP SWGR-B PANEL-10RB | EC -05 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 54 | 20.11.2019 | DR0345_1535 | [6 empty] | RPT | JHS
11 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11RB-P01 | ESP SWGR-B PANEL-11RB | EC -06 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 54 | 20.11.2019 | DR0345_1535 | [6 empty] | RPT | JHS
12 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11RB-P02 | ESP SWGR-B PANEL-11RB | EC -06 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 54 | 20.11.2019 | DR0345_1535 | [6 empty] | RPT | JHS
13 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11RE-P01 | ESP SWGR-B PANEL-11RE | EC -07 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 55 | 20.11.2019 | DR0345_1535 | [6 empty] | RPT | JHS
14 | 1DB2D | D02G120 | 10.4.10 | LTMCC2-11RE-P02 | ESP SWGR-B PANEL-11RE | EC -07 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) |  | 55 | 20.11.2019 | DR0345_1535 | [6 empty] | RPT | JHS
15 | 1DB2D | D02G120 | 10.4.10 | ECTP-D01-P01 | EC -01 PASS-D | HV TXR RECT TRF-01 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
16 | 1DB2D | D02G120 | 10.4.10 | ECTP-D01-P02 | EC -01 PASS-D | HV TXR RECT TRF-01 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
17 | 1DB2D | D10C1.5 | 10.5.10 | ECTP-D01-C01 | EC -01 PASS-D | HV TXR RECT TRF-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
18 | 1DB2D | D03C1.5 | 10.5.03 | ECTP-D01-C02 | EC -01 PASS-D | HV TXR RECT TRF-01 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
19 | 1DB2D | D02W1.5 | 10.4.27 | ECTP-D01-C03 | EC -01 PASS-D | HV TXR RECT TRF-01 PASS-D | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
20 | 1DB2D | D02G120 | 10.4.10 | ECTP-D02-P01 | EC -02 PASS-D | HV TXR RECT TRF-02 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
21 | 1DB2D | D02G120 | 10.4.10 | ECTP-D02-P02 | EC -02 PASS-D | HV TXR RECT TRF-02 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
22 | 1DB2D | D10C1.5 | 10.5.10 | ECTP-D02-C01 | EC -02 PASS-D | HV TXR RECT TRF-02 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
23 | 1DB2D | D03C1.5 | 10.5.03 | ECTP-D02-C02 | EC -02 PASS-D | HV TXR RECT TRF-02 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
24 | 1DB2D | D02W1.5 | 10.4.27 | ECTP-D02-C03 | EC -02 PASS-D | HV TXR RECT TRF-02 PASS-D | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
25 | 1DB2D | D02G120 | 10.4.10 | ECTP-D03-P01 | EC -03 PASS-D | HV TXR RECT TRF-03 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
26 | 1DB2D | D02G120 | 10.4.10 | ECTP-D03-P02 | EC -03 PASS-D | HV TXR RECT TRF-03 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
27 | 1DB2D | D10C1.5 | 10.5.10 | ECTP-D03-C01 | EC -03 PASS-D | HV TXR RECT TRF-03 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
28 | 1DB2D | D03C1.5 | 10.5.03 | ECTP-D03-C02 | EC -03 PASS-D | HV TXR RECT TRF-03 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
29 | 1DB2D | D02W1.5 | 10.4.27 | ECTP-D03-C03 | EC -03 PASS-D | HV TXR RECT TRF-03 PASS-D | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
30 | 1DB2D | D02G120 | 10.4.10 | ECTP-D04-P01 | EC -04 PASS-D | HV TXR RECT TRF-04 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
31 | 1DB2D | D02G120 | 10.4.10 | ECTP-D04-P02 | EC -04 PASS-D | HV TXR RECT TRF-04 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
32 | 1DB2D | D10C1.5 | 10.5.10 | ECTP-D04-C01 | EC -04 PASS-D | HV TXR RECT TRF-04 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
33 | 1DB2D | D03C1.5 | 10.5.03 | ECTP-D04-C02 | EC -04 PASS-D | HV TXR RECT TRF-04 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
34 | 1DB2D | D02W1.5 | 10.4.27 | ECTP-D04-C03 | EC -04 PASS-D | HV TXR RECT TRF-04 PASS-D | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
35 | 1DB2D | D02G120 | 10.4.10 | ECTP-D05-P01 | EC -05 PASS-D | HV TXR RECT TRF-05 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
36 | 1DB2D | D02G120 | 10.4.10 | ECTP-D05-P02 | EC -05 PASS-D | HV TXR RECT TRF-05 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
37 | 1DB2D | D10C1.5 | 10.5.10 | ECTP-D05-C01 | EC -05 PASS-D | HV TXR RECT TRF-05 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
38 | 1DB2D | D03C1.5 | 10.5.03 | ECTP-D05-C02 | EC -05 PASS-D | HV TXR RECT TRF-05 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
39 | 1DB2D | D02W1.5 | 10.4.27 | ECTP-D05-C03 | EC -05 PASS-D | HV TXR RECT TRF-05 PASS-D | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
40 | 1DB2D | D02G120 | 10.4.10 | ECTP-D06-P01 | EC -06 PASS-D | HV TXR RECT TRF-06 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
41 | 1DB2D | D02G120 | 10.4.10 | ECTP-D06-P02 | EC -06 PASS-D | HV TXR RECT TRF-06 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
42 | 1DB2D | D10C1.5 | 10.5.10 | ECTP-D06-C01 | EC -06 PASS-D | HV TXR RECT TRF-06 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
43 | 1DB2D | D03C1.5 | 10.5.03 | ECTP-D06-C02 | EC -06 PASS-D | HV TXR RECT TRF-06 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
44 | 1DB2D | D02W1.5 | 10.4.27 | ECTP-D06-C03 | EC -06 PASS-D | HV TXR RECT TRF-06 PASS-D | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
45 | 1DB2D | D02G120 | 10.4.10 | ECTP-D07-P01 | EC -07 PASS-D | HV TXR RECT TRF-07 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
46 | 1DB2D | D02G120 | 10.4.10 | ECTP-D07-P02 | EC -07 PASS-D | HV TXR RECT TRF-07 PASS-D | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | [10 empty] | JHS | JHS
47 | 1DB2D | D10C1.5 | 10.5.10 | ECTP-D07-C01 | EC -07 PASS-D | HV TXR RECT TRF-07 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
48 | 1DB2D | D03C1.5 | 10.5.03 | ECTP-D07-C02 | EC -07 PASS-D | HV TXR RECT TRF-07 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | JHS | JHS
49 | 1DB2D | D02W1.5 | 10.4.27 | ECTP-D07-C03 | EC -07 PASS-D | HV TXR RECT TRF-07 PASS-D | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [10 empty] | JHS | JHS
50 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-10RC-P01 | ESP SWGR-B PANEL-10RC | CERM-01 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
51 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-10RD-P01 | ESP SWGR-B PANEL-10RD | CERM-02 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
52 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-11RC-P01 | ESP SWGR-B PANEL-11RC | CERM-03 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
53 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-11RD-P01 | ESP SWGR-B PANEL-11RD | CERM-04 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
54 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-12RB-P01 | ESP SWGR-B PANEL-12RB | CERM-05 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
55 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-12RC-P01 | ESP SWGR-B PANEL-12RC | CERM-06 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
56 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-12RD-P01 | ESP SWGR-B PANEL-12RD | CERM-07 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
57 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-12RE-P01 | ESP SWGR-B PANEL-12RE | EERM-01 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
58 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-12RF-P01 | ESP SWGR-B PANEL-12RF | EERM-02 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
59 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-13RB-P01 | ESP SWGR-B PANEL-13RB | EERM-03 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
60 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-13RC-P01 | ESP SWGR-B PANEL-13RC | EERM-04 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
61 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-13RD-P01 | ESP SWGR-B PANEL-13RD | EERM-05 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
62 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-13RE-P01 | ESP SWGR-B PANEL-13RE | EERM-06 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
63 | 1DB2D | D03C2.5 | 10.5.04 | 1DB2-13RF-P01 | ESP SWGR-B PANEL-13RF | EERM-07 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
64 | 1DB2D | D03C2.5 | 10.5.04 | 1DB1-14RC-P01 | ESP SWGR-B PANEL-14RC | GDRM-01 PASS-D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
65 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AR-C01 | ESP SWGR-B PANEL-09AR | CERM LPBJB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
66 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AR-C02 | ESP SWGR-B PANEL-09AR | CERM LPBJB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
67 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AR-C03 | ESP SWGR-B PANEL-09AR | CERM LPBJB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
68 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AR-C04 | ESP SWGR-B PANEL-09AR | EERM LPBJB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
69 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AR-C05 | ESP SWGR-B PANEL-09AR | EERM LPBJB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
70 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AR-C06 | ESP SWGR-B PANEL-09AR | EERM LPBJB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
71 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-CERM-L01 | CERM LPBJB-01 PASS-D | CERM LPB-01 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
72 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-CERM-L02 | CERM LPBJB-01 PASS-D | CERM LPB-02 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
73 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-CERM-L03 | CERM LPBJB-01 PASS-D | CERM LPB-03 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
74 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-CERM-L04 | CERM LPBJB-01 PASS-D | CERM LPB-04 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
75 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-CERM-L05 | CERM LPBJB-01 PASS-D | CERM LPB-05 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
76 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-CERM-L06 | CERM LPBJB-01 PASS-D | CERM LPB-06 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
77 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-CERM-L07 | CERM LPBJB-01 PASS-D | CERM LPB-07 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
78 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-GDRM-L01 | CERM LPBJB-01 PASS-D | GDRM LPB-01 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
79 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-EERM-L01 | EERM LPBJB-01 PASS-D | EERM LPB-01 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
80 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-EERM-L02 | EERM LPBJB-01 PASS-D | EERM LPB-02 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
81 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-EERM-L03 | EERM LPBJB-01 PASS-D | EERM LPB-03 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
82 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-EERM-L04 | EERM LPBJB-01 PASS-D | EERM LPB-04 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
83 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-EERM-L05 | EERM LPBJB-01 PASS-D | EERM LPB-05 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
84 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-EERM-L06 | EERM LPBJB-01 PASS-D | EERM LPB-06 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
85 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-EERM-L07 | EERM LPBJB-01 PASS-D | EERM LPB-07 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
86 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-10FB-P01 | ESP SWGR-B PANEL-10FB | HH PJB-01 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
87 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB01 D-L01 | HH PJB-01 PASS-D | HOPR2 FLD-1 PASS-D CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
88 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB01 D-L02 | HH PJB-01 PASS-D | HOPR2 FLD-1 PASS-D CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
89 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB01 D-L03 | HH PJB-01 PASS-D | HOPR2 FLD-1 PASS-D CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
90 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-10FC-P01 | ESP SWGR-B PANEL-10FC | HH PJB-02 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
91 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB02 D-L01 | HH PJB-02 PASS-D | HOPR2 FLD-2 PASS-D CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
92 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB02 D-L02 | HH PJB-02 PASS-D | HOPR2 FLD-2 PASS-D CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
93 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB02 D-L03 | HH PJB-02 PASS-D | HOPR2 FLD-2 PASS-D CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
94 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-10FD-P01 | ESP SWGR-B PANEL-10FD | HH PJB-03 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
95 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB03 D-L01 | HH PJB-03 PASS-D | HOPR2 FLD-3 PASS-D CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
96 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB03 D-L02 | HH PJB-03 PASS-D | HOPR2 FLD-3 PASS-D CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
97 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB03 D-L03 | HH PJB-03 PASS-D | HOPR2 FLD-3 PASS-D CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
98 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-11FC-P01 | ESP SWGR-B PANEL-11FC | HH PJB-04 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
99 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB04 D-L01 | HH PJB-04 PASS-D | HOPR2 FLD-4 PASS-D CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
100 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB04 D-L02 | HH PJB-04 PASS-D | HOPR2 FLD-4 PASS-D CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
101 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB04 D-L03 | HH PJB-04 PASS-D | HOPR2 FLD-4 PASS-D CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
102 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-11FD-P01 | ESP SWGR-B PANEL-11FD | HH PJB-05 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
103 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB05 D-L01 | HH PJB-05 PASS-D | HOPR2 FLD-5 PASS-D CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
104 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB05 D-L02 | HH PJB-05 PASS-D | HOPR2 FLD-5 PASS-D CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
105 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB05 D-L03 | HH PJB-05 PASS-D | HOPR2 FLD-5 PASS-D CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
106 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-12FB-P01 | ESP SWGR-B PANEL-12FB | HH PJB-06 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
107 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB06 D-L01 | HH PJB-06 PASS-D | HOPR2 FLD-6 PASS-D CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
108 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB06 D-L02 | HH PJB-06 PASS-D | HOPR2 FLD-6 PASS-D CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
109 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB06 D-L03 | HH PJB-06 PASS-D | HOPR2 FLD-6 PASS-D CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
110 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-15FB-P01 | ESP SWGR-B PANEL-15FB | HH PJB-07 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
111 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB07 D-L01 | HH PJB-07 PASS-D | HOPR2 FLD-7 PASS-D CKT-1 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
112 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB07 D-L02 | HH PJB-07 PASS-D | HOPR2 FLD-7 PASS-D CKT-2 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
113 | 1DB2D | D02L2.5 | 10.4.24 | HHPJB07 D-L03 | HH PJB-07 PASS-D | HOPR2 FLD-7 PASS-D CKT-3 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
114 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AF-C01 | ESP SWGR-B PANEL-09AF | HH TH JB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
115 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AF-C02 | ESP SWGR-B PANEL-09AF | HH TH JB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
116 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-HH-L01 | HH TH JB-01 PASS-D | THERMOSTAT-HH-1 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
117 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-HH-L02 | HH TH JB-01 PASS-D | THERMOSTAT-HH-2 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
118 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-HH-L03 | HH TH JB-01 PASS-D | THERMOSTAT-HH-3 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
119 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-HH-L04 | HH TH JB-01 PASS-D | THERMOSTAT-HH-4 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
120 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-HH-L05 | HH TH JB-01 PASS-D | THERMOSTAT-HH-5 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
121 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-HH-L06 | HH TH JB-01 PASS-D | THERMOSTAT-HH-6 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
122 | 1DB2D | D03C1.5 | 10.5.03 | PASS-D-HH-L07 | HH TH JB-01 PASS-D | THERMOSTAT-HH-7 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
123 | 1DB2D | D03Q035 | 10.4.13 | 1DB2-14FA-P01 | ESP SWGR-A PANEL-14FA | SUPP HTR JB01 VAR-P2 PASS-D | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 100 | [9 empty] | RPT | RPT
124 | 1DB2D | D03Q035 | 10.4.13 | SUPPHTR L02 | SUPP HTR JB01 VAR-P2 PASS-D | SUPP HTR JB02 VAR-P3 PASS-D | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [9 empty] | RPT | RPT
125 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB01 L01 | SUPP HTR JB01 VAR-P2 PASS-D | SUHTR ROW1 PASS-D JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
126 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB01 L02 | SUPP HTR JB01 VAR-P2 PASS-D | SUHTR ROW1 PASS-D JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
127 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB01 L03 | SUPP HTR JB01 VAR-P2 PASS-D | SUHTR ROW1 PASS-D JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
128 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB01 L04 | SUPP HTR JB01 VAR-P2 PASS-D | SUHTR ROW1 PASS-D JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
129 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB01 L05 | SUPP HTR JB01 VAR-P2 PASS-D | SUHTR ROW1 PASS-D JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
130 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB01 L06 | SUPP HTR JB01 VAR-P2 PASS-D | SUHTR ROW1 PASS-D JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
131 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB01 L07 | SUPP HTR JB01 VAR-P2 PASS-D | SUHTR ROW1 PASS-D JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
132 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB02 L01 | SUPP HTR JB02 VAR-P3 PASS-D | SUHTR ROW2 PASS-D JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
133 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB02 L02 | SUPP HTR JB02 VAR-P3 PASS-D | SUHTR ROW2 PASS-D JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
134 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB02 L03 | SUPP HTR JB02 VAR-P3 PASS-D | SUHTR ROW2 PASS-D JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
135 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB02 L04 | SUPP HTR JB02 VAR-P3 PASS-D | SUHTR ROW2 PASS-D JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
136 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB02 L05 | SUPP HTR JB02 VAR-P3 PASS-D | SUHTR ROW2 PASS-D JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
137 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB02 L06 | SUPP HTR JB02 VAR-P3 PASS-D | SUHTR ROW2 PASS-D JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
138 | 1DB2D | D02L2.5 | 10.4.24 | SUHTR-D JB02 L07 | SUPP HTR JB02 VAR-P3 PASS-D | SUHTR ROW2 PASS-D JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
139 | 1DB2D | D03C1.5 | 10.5.03 | 1DB2-09AF-C03 | ESP SWGR-B PANEL-09AF | SUPP HTR TH-P1 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
140 | 1DB2D | D03Q010 | 10.4.11 | 1DB2-14FB-P01 | ESP SWGR-B PANEL-14FB | SHFT HTR VAR-P1 PASS-D | 03C X 010 XLPE-Al FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
141 | 1DB2D | D02L2.5 | 10.4.24 | SHTR-D L01 | SHFT HTR VAR-P1 PASS-D | SHFT HTR PASS-D JB01 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
142 | 1DB2D | D02L2.5 | 10.4.24 | SHTR-D L02 | SHFT HTR VAR-P1 PASS-D | SHFT HTR PASS-D JB02 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
143 | 1DB2D | D02L2.5 | 10.4.24 | SHTR-D L03 | SHFT HTR VAR-P1 PASS-D | SHFT HTR PASS-D JB03 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
144 | 1DB2D | D02L2.5 | 10.4.24 | SHTR-D L04 | SHFT HTR VAR-P1 PASS-D | SHFT HTR PASS-D JB04 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
145 | 1DB2D | D02L2.5 | 10.4.24 | SHTR-D L05 | SHFT HTR VAR-P1 PASS-D | SHFT HTR PASS-D JB05 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
146 | 1DB2D | D02L2.5 | 10.4.24 | SHTR-D L06 | SHFT HTR VAR-P1 PASS-D | SHFT HTR PASS-D JB06 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
147 | 1DB2D | D02L2.5 | 10.4.24 | SHTR-D L07 | SHFT HTR VAR-P1 PASS-D | SHFT HTR PASS-D JB07 | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
148 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AF-C04 | ESP SWGR-B PANEL-09AF | ALI LOW JB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
149 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L01 | ALI LOW JB-01 PASS-D | ALI L HOPPER-1 FLD-1 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
150 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L02 | ALI LOW JB-01 PASS-D | ALI L HOPPER-2 FLD-1 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
151 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L03 | ALI LOW JB-01 PASS-D | ALI L HOPPER-1 FLD-2 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
152 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L04 | ALI LOW JB-01 PASS-D | ALI L HOPPER-2 FLD-2 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
153 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L05 | ALI LOW JB-01 PASS-D | ALI L HOPPER-1 FLD-3 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
154 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L06 | ALI LOW JB-01 PASS-D | ALI L HOPPER-2 FLD-3 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
155 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L07 | ALI LOW JB-01 PASS-D | ALI L HOPPER-1 FLD-4 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
156 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L08 | ALI LOW JB-01 PASS-D | ALI L HOPPER-2 FLD-4 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
157 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L09 | ALI LOW JB-01 PASS-D | ALI L HOPPER-1 FLD-5 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
158 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L10 | ALI LOW JB-01 PASS-D | ALI L HOPPER-2 FLD-5 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
159 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L11 | ALI LOW JB-01 PASS-D | ALI L HOPPER-1 FLD-6 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
160 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L12 | ALI LOW JB-01 PASS-D | ALI L HOPPER-2 FLD-6 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
161 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L13 | ALI LOW JB-01 PASS-D | ALI L HOPPER-1 FLD-7 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
162 | 1DB2D | D03C1.5 | 10.5.03 | ALI-L PASS-D L14 | ALI LOW JB-01 PASS-D | ALI L HOPPER-2 FLD-7 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
163 | 1DB2D | D10C1.5 | 10.5.10 | 1DB2-09AR-C07 | ESP SWGR-B PANEL-09AR | ALI HIGH JB-01 PASS-D | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
164 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L01 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-1 FLD-1 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
165 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L02 | ALI HIGH JB-01 PASS-D | ALI L HOPPER-2 FLD-1 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
166 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L03 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-1 FLD-2 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
167 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L04 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-2 FLD-2 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
168 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L05 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-1 FLD-3 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
169 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L06 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-2 FLD-3 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
170 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L07 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-1 FLD-4 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
171 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L08 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-2 FLD-4 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
172 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L09 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-1 FLD-5 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
173 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L10 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-2 FLD-5 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
174 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L11 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-1 FLD-6 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
175 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L12 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-2 FLD-6 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
176 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L13 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-1 FLD-7 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
177 | 1DB2D | D03C1.5 | 10.5.03 | ALI-H PASS-D L14 | ALI HIGH JB-01 PASS-D | ALI H HOPPER-2 FLD-7 PASS-D | 03C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [10 empty] | RPT | RPT
101 | SBLOWR | D05C2.5 | 10.5.07 | SBC-CBL-011 (9ZT09BC02) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 10 (24 WAYS)EL 30400: NEAR S19 | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 155 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
102 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-012 (9ZT09BC03) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 10 (24 WAYS)EL 30400: NEAR S19 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 155 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
103 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB10 -1 (9ZT09BC04) | SBC- JB- 10 (24 WAYS)EL 30400: NEAR S19 | LRB DRAIN HEAD SOLENOID VALVEEL 31000 ; NEAR S19 | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
104 | SBLOWR | E02W0.5 | 10.8.01 | SBC- CBL- JB10 -2 (9ZT09BC05) | SBC- JB- 10 (24 WAYS)EL 30400: NEAR S19 | LRB DRAIN HEAD SOLENOID VALVEEL 31000 ; NEAR S19 | 02P X 0.5 Paired Screened(I) ( 225 V ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
105 | SBLOWR | D05C2.5 | 10.5.07 | SBC-CBL-013 (9ZT09BC06) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 11 (24 WAYS)EL 7000: NEAR S3L | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
106 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-014 (9ZT09BC07) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 11 (24 WAYS)EL 7000: NEAR S3L | 04P X 0.5 Paired Screened(O) ( 225 V ) | 140 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
107 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB11 -1 (9ZT09BC08) | SBC- JB- 11 (24 WAYS)EL 7000: NEAR S3L | WB DRAIN HEAD SOLENOID VALVEEL 7500 ; NEAR S3R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
108 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB11 -2 (9ZT09BC09) | SBC- JB- 11 (24 WAYS)EL 7000: NEAR S3L | WB DRAIN HEAD SOLENOID VALVEEL 7000 ; NEAR S3L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
109 | SBLOWR | E02W0.5 | 10.8.01 | SBC- CBL- JB11 -3 (9ZT09BC10) | SBC- JB- 11 (24 WAYS)EL 7000: NEAR S3L | WB DRAIN HEAD SOLENOID VALVEEL 7500 ; NEAR S3R | 02P X 0.5 Paired Screened(I) ( 225 V ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
110 | SBLOWR | E02W0.5 | 10.8.01 | SBC- CBL- JB11 -4 (9ZT09BC11) | SBC- JB- 11 (24 WAYS) EL 7000: NEAR S3L | WB DRAIN HEAD SOLENOID VALVEEL 7000 ; NEAR S3L | 02P X 0.5 Paired Screened(I) ( 225 V ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
111 | SBLOWR | D05C2.5 | 10.5.07 | SBC-CBL-015 (9ZT09BC12) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 12 (24 WAYS)EL 7000: NEAR S21 | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
112 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-016 (9ZT09BC13) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 12 (24 WAYS)EL 7000: NEAR S21 | 04P X 0.5 Paired Screened(O) ( 225 V ) | 140 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
113 | SBLOWR | D05C2.5 | 10.5.07 | SBC-CBL-017 (9ZT09BC14) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 13 (24 WAYS)EL 12300: NEAR S22 | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
114 | SBLOWR | D05C2.5 | 10.5.07 | SBC-CBL-018 (9ZT09BC15) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 13 (24 WAYS)EL 12300: NEAR S22 | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
115 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB12 -1 (9ZT09BC16) | SBC- JB- 12 (24 WAYS)EL 7000: NEAR S21 | AH DRAIN HEADER SOLENOID VALVEEL 7300 ; NEAR S21 | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
116 | SBLOWR | E02W0.5 | 10.8.01 | SBC- CBL- JB12 -2 (9ZT09BC17) | SBC- JB- 12 (24 WAYS)EL 7000: NEAR S21 | AH DRAIN HEADER SOLENOID VALVEEL 7300 ; NEAR S21 | 02P X 0.5 Paired Screened(I) ( 225 V ) | 10 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
117 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB13 -1 (9ZT09BC18) | SBC- JB- 13 (24 WAYS)EL 12300: NEAR S22 | RAPH-A (HOT END) DP HEAD VALVEEL 20600 ; NEAR S21 | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
118 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB13 -2 (9ZT09BC19) | SBC- JB- 13 (24 WAYS)EL 12300: NEAR S22 | RAPH-A (COLD END) DP HEAD VALVEEL 10500 ; NEAR S21 | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
119 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB13 -3 (9ZT09BC20) | SBC- JB- 13 (24 WAYS)EL 12300: NEAR S22 | RAPH-B (HOT END) DP HEAD VALVEEL 20300 ; NEAR S14R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
120 | SBLOWR | D03C2.5 | 10.5.04 | SBC- CBL- JB13 -4 (9ZT09BC21) | SBC- JB- 13 (24 WAYS)EL 12300: NEAR S22 | RAPH-B (COLD END) DP HEAD VALVEEL 10500 ; NEAR S14R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | TRY
121 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-019 (9ZT09BC22) | SB CPCONTROL EQUIPMENT ROOM (CER) | LIEEL 56850 ; NEAR S11R | 04P X 0.5 Paired Screened(I) ( 225 V ) | 173 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, ZZ99- |  | TRY | EDN
122 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-020 (9ZT09BC23) | SB CPCONTROL EQUIPMENT ROOM (CER) | LIEEL 56850 ; NEAR S11R | 04P X 0.5 Paired Screened(I) ( 225 V ) | 173 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, ZZ99- |  | TRY | EDN
123 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-021 (9ZT09BC24) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 14 (36 WAYS)EL 56850: NEAR S12R | 04P X 0.5 Paired Screened(I) ( 225 V ) | 150 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
124 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-022 (9ZT09BC25) | SB CPCONTROL EQUIPMENT ROOM (CER) | SBC- JB- 14 (36 WAYS)EL 56850: NEAR S12R | 04P X 0.5 Paired Screened(I) ( 225 V ) | 150 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | SITE ROUTING |  | TRY | EDN
129 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-023 (9ZT09BC30) | SB CPCONTROL EQUIPMENT ROOM (CER) | JUNCTION BOX FOR DIN RAIL MOUNTED TEMP. TRANSMITTERSEL 26300 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 164 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, ZZ99- |  | TRY | EDN
130 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-024 (9ZT09BC31) | SB CPCONTROL EQUIPMENT ROOM (CER) | JUNCTION BOX FOR DIN RAIL MOUNTED TEMP. TRANSMITTERSEL 26300 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 164 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, ZZ99- |  | TRY | EDN
131 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-025 (9ZT09BC32) | SB CPCONTROL EQUIPMENT ROOM (CER) | JUNCTION BOX FOR DIN RAIL MOUNTED TEMP. TRANSMITTERSEL 7000 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 172 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, BR02-02, BR01-03, ZZ99- |  | TRY | EDN
139 | SBLOWR | E04W0.5 | 10.8.02 | SBC-CBL-026 (9ZT09BC40) | SB CPCONTROL EQUIPMENT ROOM (CER) | JUNCTION BOX FOR DIN RAIL MOUNTED TEMP. TRANSMITTERSEL 7000 | 04P X 0.5 Paired Screened(I) ( 225 V ) | 172 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, BR02-02, BR01-03, ZZ99- |  | TRY | EDN
142 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-027 (9ZT09BC43) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-1 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
143 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-028 (9ZT09BC44) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-2 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
144 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-029 (9ZT09BC45) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-3 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
145 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-030 (9ZT09BC46) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-4 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
146 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-031 (9ZT09BC47) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-5 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
147 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-032 (9ZT09BC48) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-6 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
148 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-033 (9ZT09BC49) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-7 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
149 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-034 (9ZT09BC50) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-8 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
150 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-035 (9ZT09BC51) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-9 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV81-R4, LV26-L3, LV25-L3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
151 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-036 (9ZT09BC52) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-10 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
152 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-037 (9ZT09BC53) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-11 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
153 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-038 (9ZT09BC54) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-12 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
154 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-039 (9ZT09BC55) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-13 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
155 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-040 (9ZT09BC56) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-14 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
156 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-041 (9ZT09BC57) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-15 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
157 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-042 (9ZT09BC58) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-16 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
158 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-043 (9ZT09BC59) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-17 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
159 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-044 (9ZT09BC60) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-18 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
160 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-045 (9ZT09BC61) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-19 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
161 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-046 (9ZT09BC62) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-20 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-02, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
162 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-047 (9ZT09BC63) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-21 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
163 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-048 (9ZT09BC64) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-22 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
164 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-049 (9ZT09BC65) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-23 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
165 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-050 (9ZT09BC66) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-24 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
166 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-051 (9ZT09BC67) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-25 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
167 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-052 (9ZT09BC68) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-26 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
168 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-053 (9ZT09BC69) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-27 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
169 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-054 (9ZT09BC70) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-28 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
170 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-055 (9ZT09BC71) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-29 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
171 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-056 (9ZT09BC72) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-30 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
172 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-057 (9ZT09BC73) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-31 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
173 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-058 (9ZT09BC74) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-32 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
174 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-059 (9ZT09BC75) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-33 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
175 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-060 (9ZT09BC76) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-34 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
176 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-061 (9ZT09BC77) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-35 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
177 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-062 (9ZT09BC78) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-36 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
178 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-063 (9ZT09BC79) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-37 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
179 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-064 (9ZT09BC80) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-38 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
180 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-065 (9ZT09BC81) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-39 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
181 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-066 (9ZT09BC82) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-40 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
182 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-067 (9ZT09BC83) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-41 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
183 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-068 (9ZT09BC84) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-42 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
184 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-069 (9ZT09BC85) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-43 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-04, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
185 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-070 (9ZT09BC86) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-44 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-04, LR06-02, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
186 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-071 (9ZT09BC87) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-45 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 93 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
187 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-072 (9ZT09BC88) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-46 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
188 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-073 (9ZT09BC89) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-47 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
189 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-074 (9ZT09BC90) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-48 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
190 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-075 (9ZT09BC91) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-49 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
191 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-076 (9ZT09BC92) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-50 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
192 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-077 (9ZT09BC93) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-51 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
193 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-078 (9ZT09BC94) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-52 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
194 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-079 (9ZT09BC95) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-53 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
195 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-080 (9ZT09BC96) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-54 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
196 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-081 (9ZT09BC97) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-55 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
197 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-082 (9ZT09BC98) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER WB-56 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-04, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
198 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-083 (9ZT09BC99) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-57 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
199 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-084 (9ZT09CC01) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-58 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
200 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-085 (9ZT09CC02) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-59 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
201 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-086 (9ZT09CC03) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-60 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
202 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-087 (9ZT09CC04) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-61 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
203 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-088 (9ZT09CC05) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-62 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
204 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-089 (9ZT09CC06) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-63 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
205 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-090 (9ZT09CC07) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-64 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
206 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-091 (9ZT09CC08) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-65 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
207 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-092 (9ZT09CC09) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-66 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-02, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
208 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-093 (9ZT09CC10) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-67 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-04, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
209 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-094 (9ZT09CC11) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-68 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-04, LR06-02, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
210 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-095 (9ZT09CC12) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-69 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 92 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-04, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
211 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-096 (9ZT09CC13) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-70 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
212 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-097 (9ZT09CC14) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-71 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
213 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-098 (9ZT09CC15) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-72 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
214 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-099 (9ZT09CC16) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-73 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
215 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-100 (9ZT09CC17) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER LRB-74 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
216 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-101 (9ZT09CC18) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER AHB1 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
217 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-102 (9ZT09CC19) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER AHB2 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
218 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-103 (9ZT09CC20) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER AHB3 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
219 | SBLOWR | E04V0.5 | 10.7.02 | SBC-CBL-104 (9ZT09CC21) | SB CPCONTROL EQUIPMENT ROOM (CER) | SB MCC FEEDER AHB4 LTMCC ROOM | 04P X 0.5 Paired Screened(O) ( 225 V ) | 94 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , CC01-04, CC73-04, CC75-04, CC77-04, CC79-04, CC81-02, CC82-03, CC91-04, LR06-04, LV77-05, LR10-L5, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ23-03, ZZ99- |  | TRY | EDN
220 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-001 (9ZT09CC22) | SBMCC (WB-1) POWER LTMCC ROOM | WB-1 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
221 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-002 (9ZT09CC23) | SBMCC (WB-1) POWER LTMCC ROOM | WB-1 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
222 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-003 (9ZT09CC24) | SBMCC (WB-02) POWER LTMCC ROOM | WB-02 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
223 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-004 (9ZT09CC25) | SBMCC (WB-02) POWER LTMCC ROOM | WB-02 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
224 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-005 (9ZT09CC26) | SBMCC (WB-03) POWER LTMCC ROOM | WB-03 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
225 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-006 (9ZT09CC27) | SBMCC (WB-03) POWER LTMCC ROOM | WB-03 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
226 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-007 (9ZT09CC28) | SBMCC (WB-04) POWER LTMCC ROOM | WB-04 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
227 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-008 (9ZT09CC29) | SBMCC (WB-04) POWER LTMCC ROOM | WB-04 TERMINAL BOXEL 38670: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BR55-02, BI24-02, ZZ99- |  | TRY | TRY
228 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-009 (9ZT09CC30) | SBMCC (WB-05) POWER LTMCC ROOM | WB-05 TERMINAL BOXEL 38670: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, ZZ99- |  | TRY | TRY
229 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-010 (9ZT09CC31) | SBMCC (WB-05) POWER LTMCC ROOM | WB-05 TERMINAL BOXEL 38670: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, ZZ99- |  | TRY | TRY
230 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-011 (9ZT09CC32) | SBMCC (WB-06) POWER LTMCC ROOM | WB-06 TERMINAL BOXEL 38670: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, ZZ99- |  | TRY | TRY
231 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-012 (9ZT09CC33) | SBMCC (WB-06) POWER LTMCC ROOM | WB-06 TERMINAL BOXEL 38670: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, ZZ99- |  | TRY | TRY
232 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-013 (9ZT09CC34) | SBMCC (WB-07) POWER LTMCC ROOM | WB-07 TERMINAL BOXEL 38670: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 98 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, ZZ99- |  | TRY | TRY
233 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-014 (9ZT09CC35) | SBMCC (WB-07) POWER LTMCC ROOM | WB-07 TERMINAL BOXEL 38670: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 98 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, ZZ99- |  | TRY | TRY
234 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-015 (9ZT09CC36) | SBMCC (WB-08) POWER LTMCC ROOM | WB-08 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
235 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-016 (9ZT09CC37) | SBMCC (WB-08) POWER LTMCC ROOM | WB-08 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
236 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-017 (9ZT09CC38) | SBMCC (WB-09) POWER LTMCC ROOM | WB-09 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
237 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-018 (9ZT09CC39) | SBMCC (WB-09) POWER LTMCC ROOM | WB-09 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
238 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-019 (9ZT09CC40) | SBMCC (WB-10) POWER LTMCC ROOM | WB-10 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
239 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-020 (9ZT09CC41) | SBMCC (WB-10) POWER LTMCC ROOM | WB-10 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
240 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-021 (9ZT09CC42) | SBMCC (WB-11) POWER LTMCC ROOM | WB-11 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
241 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-022 (9ZT09CC43) | SBMCC (WB-11) POWER LTMCC ROOM | WB-11 TERMINAL BOXEL 38670: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
242 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-023 (9ZT09CC44) | SBMCC (WB-12) POWER LTMCC ROOM | WB-12 TERMINAL BOXEL 38670: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BI01-02, BI02-02, ZZ99- |  | TRY | TRY
243 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-024 (9ZT09CC45) | SBMCC (WB-12) POWER LTMCC ROOM | WB-12 TERMINAL BOXEL 38670: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BI01-02, BI02-02, ZZ99- |  | TRY | TRY
244 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-025 (9ZT09CC46) | SBMCC (WB-13) POWER LTMCC ROOM | WB-13 TERMINAL BOXEL 38670: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BI01-02, ZZ99- |  | TRY | TRY
245 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-026 (9ZT09CC47) | SBMCC (WB-13) POWER LTMCC ROOM | WB-13 TERMINAL BOXEL 38670: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BI01-02, ZZ99- |  | TRY | TRY
246 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-027 (9ZT09CC48) | SBMCC (WB-14) POWER LTMCC ROOM | WB-14 TERMINAL BOXEL 38670: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BI01-02, ZZ99- |  | TRY | TRY
247 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-028 (9ZT09CC49) | SBMCC (WB-14) POWER LTMCC ROOM | WB-14 TERMINAL BOXEL 38670: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BI01-02, ZZ99- |  | TRY | TRY
248 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-029 (9ZT09CC50) | SBMCC (WB-15) POWER LTMCC ROOM | WB-15 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 73 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
249 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-030 (9ZT09CC51) | SBMCC (WB-15) POWER LTMCC ROOM | WB-15 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
250 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-031 (9ZT09CC52) | SBMCC (WB-16) POWER LTMCC ROOM | WB-16 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
251 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-032 (9ZT09CC53) | SBMCC (WB-16) POWER LTMCC ROOM | WB-16 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
252 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-033 (9ZT09CC54) | SBMCC (WB-17) POWER LTMCC ROOM | WB-17 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
253 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-034 (9ZT09CC55) | SBMCC (WB-17) POWER LTMCC ROOM | WB-17 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
254 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-035 (9ZT09CC56) | SBMCC (WB-18) POWER LTMCC ROOM | WB-18 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
255 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-036 (9ZT09CC57) | SBMCC (WB-18) POWER LTMCC ROOM | WB-18 TERMINAL BOXEL 34920: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BR53-02, BH15-02, ZZ99- |  | TRY | TRY
256 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-037 (9ZT09CC58) | SBMCC (WB-19) POWER LTMCC ROOM | WB-19 TERMINAL BOXEL 34920: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 102 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, BH08-02, ZZ99- |  | TRY | TRY
257 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-038 (9ZT09CC59) | SBMCC (WB-19) POWER LTMCC ROOM | WB-19 TERMINAL BOXEL 34920: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 102 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, BH08-02, ZZ99- |  | TRY | TRY
258 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-039 (9ZT09CC60) | SBMCC (WB-20) POWER LTMCC ROOM | WB-20 TERMINAL BOXEL 34920: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 102 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, BH08-02, ZZ99- |  | TRY | TRY
259 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-040 (9ZT09CC61) | SBMCC (WB-20) POWER LTMCC ROOM | WB-20 TERMINAL BOXEL 34920: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 102 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, BH08-02, ZZ99- |  | TRY | TRY
260 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-041 (9ZT09CC62) | SBMCC (WB-21) POWER LTMCC ROOM | WB-21 TERMINAL BOXEL 34920: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, ZZ99- |  | TRY | TRY
261 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-042 (9ZT09CC63) | SBMCC (WB-21) POWER LTMCC ROOM | WB-21 TERMINAL BOXEL 34920: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 95 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, ZZ99- |  | TRY | TRY
262 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-043 (9ZT09CC64) | SBMCC (WB-22) POWER LTMCC ROOM | WB-22 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
263 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-044 (9ZT09CC65) | SBMCC (WB-22) POWER LTMCC ROOM | WB-22 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
264 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-045 (9ZT09CC66) | SBMCC (WB-23) POWER LTMCC ROOM | WB-23 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
265 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-046 (9ZT09CC67) | SBMCC (WB-23) POWER LTMCC ROOM | WB-23 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
266 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-047 (9ZT09CC68) | SBMCC (WB-24) POWER LTMCC ROOM | WB-24 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
267 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-048 (9ZT09CC69) | SBMCC (WB-24) POWER LTMCC ROOM | WB-24 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
268 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-049 (9ZT09CC70) | SBMCC (WB-25) POWER LTMCC ROOM | WB-25 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
269 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-050 (9ZT09CC71) | SBMCC (WB-25) POWER LTMCC ROOM | WB-25 TERMINAL BOXEL 34920: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
270 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-051 (9ZT09CC72) | SBMCC (WB-26) POWER LTMCC ROOM | WB-26 TERMINAL BOXEL 34920: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-04, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
271 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-052 (9ZT09CC73) | SBMCC (WB-26) POWER LTMCC ROOM | WB-26 TERMINAL BOXEL 34920: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-04, BR06-04, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
272 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-053 (9ZT09CC74) | SBMCC (WB-27) POWER LTMCC ROOM | WB-27 TERMINAL BOXEL 34920: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-04, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
273 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-054 (9ZT09CC75) | SBMCC (WB-27) POWER LTMCC ROOM | WB-27 TERMINAL BOXEL 34920: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
274 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-055 (9ZT09CC76) | SBMCC (WB-28) POWER LTMCC ROOM | WB-28 TERMINAL BOXEL 34920: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
275 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-056 (9ZT09CC77) | SBMCC (WB-28) POWER LTMCC ROOM | WB-28 TERMINAL BOXEL 34920: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 128 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
276 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-057 (9ZT09CC78) | SBMCC (WB-29) POWER LTMCC ROOM | WB-29 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
277 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-058 (9ZT09CC79) | SBMCC (WB-29) POWER LTMCC ROOM | WB-29 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
278 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-059 (9ZT09CC80) | SBMCC (WB-30) POWER LTMCC ROOM | WB-30 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
279 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-060 (9ZT09CC81) | SBMCC (WB-30) POWER LTMCC ROOM | WB-30 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
280 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-061 (9ZT09CC82) | SBMCC (WB-31) POWER LTMCC ROOM | WB-31 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
281 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-062 (9ZT09CC83) | SBMCC (WB-31) POWER LTMCC ROOM | WB-31 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
282 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-063 (9ZT09CC84) | SBMCC (WB-32) POWER LTMCC ROOM | WB-32 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
283 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-064 (9ZT09CC85) | SBMCC (WB-32) POWER LTMCC ROOM | WB-32 TERMINAL BOXEL 31520: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 79 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, ZZ99- |  | TRY | TRY
284 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-065 (9ZT09CC86) | SBMCC (WB-33) POWER LTMCC ROOM | WB-33 TERMINAL BOXEL 31520: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, ZZ99- |  | TRY | TRY
285 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-066 (9ZT09CC87) | SBMCC (WB-33) POWER LTMCC ROOM | WB-33 TERMINAL BOXEL 31520: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, ZZ99- |  | TRY | TRY
286 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-067 (9ZT09CC88) | SBMCC (WB-34) POWER LTMCC ROOM | WB-34 TERMINAL BOXEL 31520: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, ZZ99- |  | TRY | TRY
287 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-068 (9ZT09CC89) | SBMCC (WB-34) POWER LTMCC ROOM | WB-34 TERMINAL BOXEL 31520: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 76 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, ZZ99- |  | TRY | TRY
288 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-069 (9ZT09CC90) | SBMCC (WB-35) POWER LTMCC ROOM | WB-35 TERMINAL BOXEL 31520: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 81 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, ZZ99- |  | TRY | TRY
289 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-070 (9ZT09CC91) | SBMCC (WB-35) POWER LTMCC ROOM | WB-35 TERMINAL BOXEL 31520: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 81 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, ZZ99- |  | TRY | TRY
290 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-071 (9ZT09CC92) | SBMCC (WB-36) POWER LTMCC ROOM | WB-36 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
291 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-072 (9ZT09CC93) | SBMCC (WB-36) POWER LTMCC ROOM | WB-36 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
292 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-073 (9ZT09CC94) | SBMCC (WB-37) POWER LTMCC ROOM | WB-37 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
293 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-074 (9ZT09CC95) | SBMCC (WB-37) POWER LTMCC ROOM | WB-37 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
294 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-075 (9ZT09CC96) | SBMCC (WB-38) POWER LTMCC ROOM | WB-38 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
295 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-076 (9ZT09CC97) | SBMCC (WB-38) POWER LTMCC ROOM | WB-38 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 110 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BI22-02, BI21-02, BI20-02, BI19-02, BI18-02, ZZ99- |  | TRY | TRY
296 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-077 (9ZT09CC98) | SBMCC (WB-39) POWER LTMCC ROOM | WB-39 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
297 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-078 (9ZT09CC99) | SBMCC (WB-39) POWER LTMCC ROOM | WB-39 TERMINAL BOXEL 31520: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BG15-02, BG20-02, BG21-02, BR51-02, ZZ99- |  | TRY | TRY
298 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-079 (9ZT09DC01) | SBMCC (WB-40) POWER LTMCC ROOM | WB-40 TERMINAL BOXEL 31520: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, ZZ99- |  | TRY | TRY
299 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-080 (9ZT09DC02) | SBMCC (WB-40) POWER LTMCC ROOM | WB-40 TERMINAL BOXEL 31520: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, ZZ99- |  | TRY | TRY
300 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-081 (9ZT09DC03) | SBMCC (WB-41) POWER LTMCC ROOM | WB-41 TERMINAL BOXEL 31520: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 98 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, ZZ99- |  | TRY | TRY
301 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-082 (9ZT09DC04) | SBMCC (WB-41) POWER LTMCC ROOM | WB-41 TERMINAL BOXEL 31520: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, ZZ99- |  | TRY | TRY
302 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-083 (9ZT09DC05) | SBMCC (WB-42) POWER LTMCC ROOM | WB-42 TERMINAL BOXEL 31520: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, ZZ99- |  | TRY | TRY
303 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-084 (9ZT09DC06) | SBMCC (WB-42) POWER LTMCC ROOM | WB-42 TERMINAL BOXEL 31520: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, ZZ99- |  | TRY | TRY
304 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-085 (9ZT09DC07) | SBMCC (WB-43) POWER LTMCC ROOM | WB-43 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BD15-02, BR40-02, ZZ99- |  | TRY | TRY
305 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-086 (9ZT09DC08) | SBMCC (WB-43) POWER LTMCC ROOM | WB-43 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BD15-02, BR40-02, ZZ99- |  | TRY | TRY
306 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-087 (9ZT09DC09) | SBMCC (WB-44) POWER LTMCC ROOM | WB-44 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BD15-02, BR40-02, ZZ99- |  | TRY | TRY
307 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-088 (9ZT09DC10) | SBMCC (WB-44) POWER LTMCC ROOM | WB-44 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BD15-02, BR40-02, ZZ99- |  | TRY | TRY
308 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-089 (9ZT09DC11) | SBMCC (WB-45) POWER LTMCC ROOM | WB-45 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 78 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BD15-02, BR40-02, ZZ99- |  | TRY | TRY
309 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-090 (9ZT09DC12) | SBMCC (WB-45) POWER LTMCC ROOM | WB-45 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BR41-02, ZZ99- |  | TRY | TRY
310 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-091 (9ZT09DC13) | SBMCC (WB-46) POWER LTMCC ROOM | WB-46 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BR41-02, ZZ99- |  | TRY | TRY
311 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-092 (9ZT09DC14) | SBMCC (WB-46) POWER LTMCC ROOM | WB-46 TERMINAL BOXEL 18170: NEAR S17 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 74 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ09-02, BQ10-02, BQ25-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BD13-02, BD14-02, BR41-02, ZZ99- |  | TRY | TRY
312 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-093 (9ZT09DC15) | SBMCC (WB-47) POWER LTMCC ROOM | WB-47 TERMINAL BOXEL 18170: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 70 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, ZZ99- |  | TRY | TRY
313 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-094 (9ZT09DC16) | SBMCC (WB-47) POWER LTMCC ROOM | WB-47 TERMINAL BOXEL 18170: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 70 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, ZZ99- |  | TRY | TRY
314 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-095 (9ZT09DC17) | SBMCC (WB-48) POWER LTMCC ROOM | WB-48 TERMINAL BOXEL 18170: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 70 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, ZZ99- |  | TRY | TRY
315 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-096 (9ZT09DC18) | SBMCC (WB-48) POWER LTMCC ROOM | WB-48 TERMINAL BOXEL 18170: NEAR S10R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 70 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, ZZ99- |  | TRY | TRY
316 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-097 (9ZT09DC19) | SBMCC (WB-49) POWER LTMCC ROOM | WB-49 TERMINAL BOXEL 18170: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 82 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, ZZ99- |  | TRY | TRY
317 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-098 (9ZT09DC20) | SBMCC (WB-49) POWER LTMCC ROOM | WB-49 TERMINAL BOXEL 18170: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 82 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, ZZ99- |  | TRY | TRY
318 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-099 (9ZT09DC21) | SBMCC (WB-50) POWER LTMCC ROOM | WB-50 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, BC04-02, ZZ99- |  | TRY | TRY
319 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-100 (9ZT09DC22) | SBMCC (WB-50) POWER LTMCC ROOM | WB-50 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, BC04-02, ZZ99- |  | TRY | TRY
320 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-101 (9ZT09DC23) | SBMCC (WB-51) POWER LTMCC ROOM | WB-51 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, BC04-02, ZZ99- |  | TRY | TRY
321 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-102 (9ZT09DC24) | SBMCC (WB-51) POWER LTMCC ROOM | WB-51 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, BC04-02, ZZ99- |  | TRY | TRY
322 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-103 (9ZT09DC25) | SBMCC (WB-52) POWER LTMCC ROOM | WB-52 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 99 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, ZZ99- |  | TRY | TRY
323 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-104 (9ZT09DC26) | SBMCC (WB-52) POWER LTMCC ROOM | WB-52 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 99 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, ZZ99- |  | TRY | TRY
324 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-105 (9ZT09DC27) | SBMCC (WB-53) POWER LTMCC ROOM | WB-53 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 99 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-L2, BQ02-L2, QR01-03, BQ01-03, BR44-03, BD09-03, BD08-03, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, ZZ99- |  | TRY | TRY
325 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-106 (9ZT09DC28) | SBMCC (WB-53) POWER LTMCC ROOM | WB-53 TERMINAL BOXEL 18170: NEAR S18 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC05-02, ZZ99- |  | TRY | TRY
326 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-107 (9ZT09DC29) | SBMCC (WB-54) POWER LTMCC ROOM | WB-54 TERMINAL BOXEL 18170: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BD13-02, BD14-02, BD15-02, BD16-02, BD17-02, BR18-03, BC01-02, BC02-02, ZZ99- |  | TRY | TRY
327 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-108 (9ZT09DC30) | SBMCC (WB-54) POWER LTMCC ROOM | WB-54 TERMINAL BOXEL 18170: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BD13-02, BD14-02, BD15-02, BD16-02, BD17-02, BR18-03, BC01-02, BC02-02, ZZ99- |  | TRY | TRY
328 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-109 (9ZT09DC31) | SBMCC (WB-55) POWER LTMCC ROOM | WB-55 TERMINAL BOXEL 18170: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BD13-02, BD14-02, BD15-02, BD16-02, BD17-02, BR18-03, BC01-02, BC02-02, ZZ99- |  | TRY | TRY
329 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-110 (9ZT09DC32) | SBMCC (WB-55) POWER LTMCC ROOM | WB-55 TERMINAL BOXEL 18170: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BD13-02, BD14-02, BD15-02, BD16-02, BD17-02, BR18-03, BC01-02, BC02-02, ZZ99- |  | TRY | TRY
330 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-111 (9ZT09DC33) | SBMCC (WB-56) POWER LTMCC ROOM | WB-56 TERMINAL BOXEL 18170: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BD13-02, BD14-02, BD15-02, BD16-02, BD17-02, BR18-03, BC01-02, BC02-02, ZZ99- |  | TRY | TRY
331 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-112 (9ZT09DC34) | SBMCC (WB-56) POWER LTMCC ROOM | WB-56 TERMINAL BOXEL 18170: NEAR S10L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BD13-02, BD14-02, BD15-02, BD16-02, BD17-02, BR18-03, BC01-02, BC02-02, ZZ99- |  | TRY | TRY
332 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-113 (9ZT09DC35) | SBMCC (LRB-57) POWER LTMCC ROOM | LRB-57 TERMINAL BOXEL 41700: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BJ01-02, BJ02-02, BJ03-02, ZZ99- |  | TRY | TRY
333 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-114 (9ZT09DC36) | SBMCC (LRB-57) POWER LTMCC ROOM | LRB-57 TERMINAL BOXEL 41700: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 106 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BJ01-02, BJ02-02, BJ03-02, ZZ99- |  | TRY | TRY
334 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-115 (9ZT09DC37) | SBMCC (LRB-58) POWER LTMCC ROOM | LRB-58 TERMINAL BOXEL 41700: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, ZZ99- |  | TRY | TRY
335 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-116 (9ZT09DC38) | SBMCC (LRB-58) POWER LTMCC ROOM | LRB-58 TERMINAL BOXEL 41700: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, ZZ99- |  | TRY | TRY
336 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-117 (9ZT09DC39) | SBMCC (LRB-59) POWER LTMCC ROOM | LRB-59 TERMINAL BOXEL 51020: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, ZZ99- |  | TRY | TRY
337 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-118 (9ZT09DC40) | SBMCC (LRB-59) POWER LTMCC ROOM | LRB-59 TERMINAL BOXEL 51020: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, ZZ99- |  | TRY | TRY
338 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-119 (9ZT09DC41) | SBMCC (LRB-60) POWER LTMCC ROOM | LRB-60 TERMINAL BOXEL 51020: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 135 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, ZZ99- |  | TRY | TRY
339 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-120 (9ZT09DC42) | SBMCC (LRB-60) POWER LTMCC ROOM | LRB-60 TERMINAL BOXEL 51020: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 135 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, ZZ99- |  | TRY | TRY
340 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-121 (9ZT09DC43) | SBMCC (LRB-61) POWER LTMCC ROOM | LRB-61 TERMINAL BOXEL 48020: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 118 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, BM06-02, ZZ99- |  | TRY | TRY
341 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-122 (9ZT09DC44) | SBMCC (LRB-61) POWER LTMCC ROOM | LRB-61 TERMINAL BOXEL 48020: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 118 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, BM06-02, ZZ99- |  | TRY | TRY
342 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-123 (9ZT09DC45) | SBMCC (LRB-62) POWER LTMCC ROOM | LRB-62 TERMINAL BOXEL 48020: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, BM03-02, ZZ99- |  | TRY | TRY
343 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-124 (9ZT09DC46) | SBMCC (LRB-62) POWER LTMCC ROOM | LRB-62 TERMINAL BOXEL 48020: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 142 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, BM03-02, ZZ99- |  | TRY | TRY
344 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-125 (9ZT09DC47) | SBMCC (LRB-63) POWER LTMCC ROOM | LRB-63 TERMINAL BOXEL 51520: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, ZZ99- |  | TRY | TRY
345 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-126 (9ZT09DC48) | SBMCC (LRB-63) POWER LTMCC ROOM | LRB-63 TERMINAL BOXEL 51520: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, ZZ99- |  | TRY | TRY
346 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-127 (9ZT09DC49) | SBMCC (LRB-64) POWER LTMCC ROOM | LRB-64 TERMINAL BOXEL 51520: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, ZZ99- |  | TRY | TRY
347 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-128 (9ZT09DC50) | SBMCC (LRB-64) POWER LTMCC ROOM | LRB-64 TERMINAL BOXEL 51520: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, ZZ99- |  | TRY | TRY
348 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-129 (9ZT09DC51) | SBMCC (LRB-65) POWER LTMCC ROOM | LRB-65 TERMINAL BOXEL 48720: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 118 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, BM06-02, ZZ99- |  | TRY | TRY
349 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-130 (9ZT09DC52) | SBMCC (LRB-65) POWER LTMCC ROOM | LRB-65 TERMINAL BOXEL 48720: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 118 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BM04-02, BM05-02, BM06-02, ZZ99- |  | TRY | TRY
350 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-131 (9ZT09DC53) | SBMCC (LRB-66) POWER LTMCC ROOM | LRB-66 TERMINAL BOXEL 48720: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, BM03-02, ZZ99- |  | TRY | TRY
351 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-132 (9ZT09DC54) | SBMCC (LRB-66) POWER LTMCC ROOM | LRB-66 TERMINAL BOXEL 48720: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BM01-02, BM02-02, BM03-02, ZZ99- |  | TRY | TRY
352 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-133 (9ZT09DC55) | SBMCC (LRB-67) POWER LTMCC ROOM | LRB-67 TERMINAL BOXEL 47820: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BR62-02, ZZ99- |  | TRY | TRY
353 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-134 (9ZT09DC56) | SBMCC (LRB-67) POWER LTMCC ROOM | LRB-67 TERMINAL BOXEL 47820: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BR62-02, ZZ99- |  | TRY | TRY
354 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-135 (9ZT09DC57) | SBMCC (LRB-68) POWER LTMCC ROOM | LRB-68 TERMINAL BOXEL 47820: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, BR74-02, BR63-02, ZZ99- |  | TRY | TRY
355 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-136 (9ZT09DC58) | SBMCC (LRB-68) POWER LTMCC ROOM | LRB-68 TERMINAL BOXEL 47820: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, BR74-02, BR63-02, ZZ99- |  | TRY | TRY
356 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-137 (9ZT09DC59) | SBMCC (LRB-69) POWER LTMCC ROOM | LRB-69 TERMINAL BOXEL 46220: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BR62-02, ZZ99- |  | TRY | TRY
357 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-138 (9ZT09DC60) | SBMCC (LRB-69) POWER LTMCC ROOM | LRB-69 TERMINAL BOXEL 46220: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 113 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BR62-02, ZZ99- |  | TRY | TRY
358 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-139 (9ZT09DC61) | SBMCC (LRB-70) POWER LTMCC ROOM | LRB-70 TERMINAL BOXEL 46220: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, BR74-02, BR63-02, ZZ99- |  | TRY | TRY
359 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-140 (9ZT09DC62) | SBMCC (LRB-70) POWER LTMCC ROOM | LRB-70 TERMINAL BOXEL 46220: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 133 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, BR74-02, BR63-02, ZZ99- |  | TRY | TRY
360 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-141 (9ZT09DC63) | SBMCC (LRB-71) POWER LTMCC ROOM | LRB-71 TERMINAL BOXEL 41670: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BJ01-02, BJ02-02, ZZ99- |  | TRY | TRY
361 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-142 (9ZT09DC64) | SBMCC (LRB-71) POWER LTMCC ROOM | LRB-71 TERMINAL BOXEL 41670: NEAR S11R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BJ01-02, BJ02-02, ZZ99- |  | TRY | TRY
362 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-143 (9ZT09DC65) | SBMCC (LRB-72) POWER LTMCC ROOM | LRB-72 TERMINAL BOXEL 41670: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 127 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, ZZ99- |  | TRY | TRY
363 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-144 (9ZT09DC66) | SBMCC (LRB-72) POWER LTMCC ROOM | LRB-72 TERMINAL BOXEL 41670: NEAR S11L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 127 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BR22-04, BR23-04, BR24-04, BJ05-02, BJ06-02, ZZ99- |  | TRY | TRY
364 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-145 (9ZT09DC67) | SBMCC (LRB-73) POWER LTMCC ROOM | LRB-73 TERMINAL BOXEL 34500: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, ZZ99- |  | TRY | TRY
365 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-146 (9ZT09DC68) | SBMCC (LRB-73) POWER LTMCC ROOM | LRB-73 TERMINAL BOXEL 34500: NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 105 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG19-02, BG18-02, BG17-02, BG16-02, BR50-02, BH09-02, ZZ99- |  | TRY | TRY
366 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-147 (9ZT09DC69) | SBMCC (LRB-74) POWER LTMCC ROOM | LRB-74 TERMINAL BOXEL 34500: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
367 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-148 (9ZT09DC70) | SBMCC (LRB-74) POWER LTMCC ROOM | LRB-74 TERMINAL BOXEL 34500: NEAR S12L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 137 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BG23-02, BG24-02, BG22-02, BG01-02, BG02-02, BG03-02, BR49-02, BH01-02, ZZ99- |  | TRY | TRY
368 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-149 (9ZT09DC71) | SBMCC (AHB-1) POWER LTMCC ROOM | AHB-1 TERMINAL BOXEL 19160 ; NEAR S21 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 134 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, BD27-02, ZZ99- |  | TRY | TRY
369 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-150 (9ZT09DC72) | SBMCC (AHB-2) POWER LTMCC ROOM | AHB-2 TERMINAL BOXEL 19160 ; NEAR S14R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 115 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, ZZ99- |  | TRY | TRY
370 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-151 (9ZT09DC73) | SBMCC (AHB-3) POWER LTMCC ROOM | AHB-3 TERMINAL BOXEL 13368 ; NEAR S21 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 136 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BR02-03, BB11-02, BB10-02, BB09-02, BB08-02, BB07-02, BB06-02, ZZ99- |  | TRY | TRY
371 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-152 (9ZT09DC74) | SBMCC (AHB-4) POWER LTMCC ROOM | AHB-4 TERMINAL BOXEL 13368 ; NEAR S14R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 138 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ23-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BR02-03, BR01-02, BA25-02, BA26-02, BA27-02, BA28-02, BA29-02, BA19-02, BA18-02, BA17-02, BR38-02, ZZ99- |  | TRY | TRY
372 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-153 (9ZT09DC75) | STEAM ISO VALVE SB MCC POWER LTMCC ROOM | MOTOR STARTER TERMINAL BOXEL 57530 ; NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, ZZ99- |  | TRY | TRY
373 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-154 (9ZT09DC76) | STEAM ISO VALVE SB MCC POWER LTMCC ROOM | MOTOR STARTER TERMINAL BOXEL 57530 ; NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, ZZ99- |  | TRY | TRY
374 | SBLOWR | D03L2.5 | 10.4.26 | SBMCC-CBL-155 (9ZT09DC77) | STEAM ISO VALVE SB MCC POWER LTMCC ROOM | MOTOR STARTER TERMINAL BOXEL 57530 ; NEAR S12R | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | INTERCONNECTION DIAGRAM FOR SOOT BLOWER SYSTEM | TRICHY SCOPE CABLE | ZZ99- , BQ08-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, ZZ99- |  | TRY | TRY
1 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C001 (9ZI05AC01) | 1HNC10GX111, IDF-A VFD VCB(Q1), VFD BKR PNL, ESP CONTROL ROO | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 274 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES10-03, ES11-03, ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
2 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C002 (9ZI05AC02) | 1HNC10GX112, IDF-A VFD VCB(Q2), VFD BKR PNL, ESP CONTROL ROO | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 274 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES10-03, ES11-03, ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
3 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C003 (9ZI05AC03) | 1HNC10GX115, IDF-A VFD VCB(Q3), VFD BKR PNL, ESP CONTROL ROO | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 263 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
4 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C004 (9ZI05AC04) | 1HNC10GX104, IDF-A VFD REMOTE, VFD PNL, ESP CONTROL ROOM | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 263 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
5 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C005 (9ZI05AC05) | 1HNC10GX107, IDF-A VFD CMD, VFD PNL, ESP CONTROL ROOM | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 263 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
6 | VFD | E04W0.5 | 10.8.02 | CVP01-VFD-C006 (9ZI05AC06) | 1HNC10CE101, IDF-A VFD CURRENT, VFD PNL, ESP CONTROL ROOM | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 263 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
7 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C007 (9ZI05AC07) | 1HNC01AN001, ID FAN-A VFD VCB (Q3), VFD BKR PNL, ESP CONTRO | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 263 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
8 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C008 (9ZI05AC08) | 1HNC01AN01A, ID FAN-A SOURCE BREAKER, HT SWGR ROOM | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 49 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC82-03, CC31-03, ZZ99- |  | BPL | EDN
9 | VFD | E04W0.5 | 10.8.02 | CVP01-VFD-C009 (9ZI05AC09) | 1HNC01AN01A, ID FAN-A SOURCE BREAKER, HT SWGR ROOM | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 49 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC82-03, CC31-03, ZZ99- |  | BPL | EDN
10 | VFD | E04V0.5 | 10.7.02 | CVP01-VFD-C010 (9ZI05AC10) | 1HNC01AN002, ID FAN-A BYPASS MODE, VFD BKR PNL, ESP CONTROL | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 263 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
11 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C001 (9ZI05AC11) | 1HNC20GX109, IDF-B VFD VCB(Q1), VFD BKR PNL, ESP CONTROL ROO | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 269 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES11-03, ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
12 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C002 (9ZI05AC12) | 1HNC20GX114, IDF-B VFD VCB(Q2), VFD BKR PNL, ESP CONTROL ROO | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 269 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES11-03, ES12-03, ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
13 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C003 (9ZI05AC13) | 1HNC20GX115, IDF-B VFD VCB(Q3), VFD BKR PNL, ESP CONTROL ROO | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 256 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
14 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C004 (9ZI05AC14) | 1HNC20GX105, IDF-B VFD RUNNING, VFD PNL, ESP CONTROL ROOM | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 256 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
15 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C005 (9ZI05AC15) | 1HNC20GX106, IDF-B VFD CMD, VFD PNL, ESP CONTROL ROOM | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 256 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
16 | VFD | E04W0.5 | 10.8.02 | CVP02-VFD-C006 (9ZI05AC16) | 1HNC15CE101, IDF-B VFD CURRENT, VFD PNL, ESP CONTROL ROOM | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 256 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
17 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C007 (9ZI05AC17) | 1HNC02AN001, ID FAN-B VFD VCB (Q3), VFD BKR PNL, ESP CONTROL | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 256 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
18 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C008 (9ZI05AC18) | 1HNC02AN01A, ID FAN-B SOURCE BREAKER, HT SWGR ROOM | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 52 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV68-06, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC82-03, CC31-03, ZZ99- |  | BPL | EDN
19 | VFD | E04W0.5 | 10.8.02 | CVP02-VFD-C009 (9ZI05AC19) | 1HNC02AN01A, ID FAN-B SOURCE BREAKER, HT SWGR ROOM | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 52 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV68-06, MV09-03, MV26-R2, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC82-03, CC31-03, ZZ99- |  | BPL | EDN
20 | VFD | E04V0.5 | 10.7.02 | CVP02-VFD-C010 (9ZI05AC20) | 1HNC02AN002, ID FAN-B BYPASS MODE, VFD BKR PNL, ESP CONTROL | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 256 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , ES13-03, ES14-03, ES15-03, ES16-03, ES96-03, ES01-R3, IR25-R3, IM63-R3, IM62-R3, IM61-R3, IM60-R3, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99- |  | BPL | EDN
21 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C001 (9ZI05AC21) | 1LCB10GX110, CEP-A VFD VCB(Q1), VFD BKR PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , LV29-R4, LV28-R4, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
22 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C002 (9ZI05AC22) | 1LCB10GX112, CEP-A VFD VCB(Q2), VFD BKR PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , LV29-R4, LV28-R4, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
23 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C003 (9ZI05AC23) | 1LCB10GX117, CEP-A VFD VCB(Q3), VFD BKR PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC12-03, AC11-03, AC10-03, DR06-03, AC09-04, AC04-04, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
24 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C004 (9ZI05AC24) | 1LCB10GX103, CEP-A VFD FAULT, VFD PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC12-03, AC11-03, AC10-03, DR06-03, AC09-04, AC04-04, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
25 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C005 (9ZI05AC25) | 1LCB10GX107, CEP-A VFD CMD, VFD PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC12-03, AC11-03, AC10-03, DR06-03, AC09-04, AC04-04, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
26 | VFD | E04W0.5 | 10.8.02 | CVP11-VFD-C006 (9ZI05AC26) | 1LCA10CE101, CEP-A VFD CURRENT, VFD PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 79 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC12-03, AC11-03, AC10-03, DR06-03, AC09-04, AC04-04, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
27 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C007 (9ZI05AC27) | 1LCB10AP01A, CEP-A VFD VCB (Q3), VFD BKR PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC12-03, AC11-03, AC10-03, DR06-03, AC09-04, AC04-04, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
28 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C008 (9ZI05AC28) | 1LCB10AP001, CEP-A SOURCE BREAKER, HT SWGR ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 67 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV13-03, MV12-03, MV86-03, MV06-R2, MV07-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99- |  | BPL | EDN
29 | VFD | E04W0.5 | 10.8.02 | CVP11-VFD-C009 (9ZI05AC29) | 1LCB10AP001, CEP-A SOURCE BREAKER, HT SWGR ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 67 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV13-03, MV12-03, MV86-03, MV06-R2, MV07-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99- |  | BPL | EDN
30 | VFD | E04V0.5 | 10.7.02 | CVP11-VFD-C010 (9ZI05AC30) | 1LCB10AP001, CEP-A BYPASS MODE, VFD BKR PNL, CEP VFD ROOM | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 79 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC12-03, AC11-03, AC10-03, DR06-03, AC09-04, AC04-04, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
31 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C001 (9ZI05AC31) | 1LCB20GX109, CEP-B VFD VCB(Q1), VFD BKR PNL, CEP VFD ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , LV29-R4, LV28-R4, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
32 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C002 (9ZI05AC32) | 1LCB20GX112, CEP-B VFD VCB(Q2), VFD BKR PNL, CEP VFD ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 64 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , LV29-R4, LV28-R4, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
33 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C003 (9ZI05AC33) | 1LCB20GX117, CEP-B VFD VCB(Q3), VFD BKR PNL, CEP VFD ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC03-03, AC02-03, DR04-03, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
34 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C004 (9ZI05AC34) | 1LCB20GX104, CEP-B VFD REMOTE, VFD PNL, CEP VFD ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC03-03, AC02-03, DR04-03, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
35 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C005 (9ZI05AC35) | 1LCB20GX107, CEP-B VFD CMD, VFD PNL, CEP VFD ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC03-03, AC02-03, DR04-03, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
36 | VFD | E04W0.5 | 10.8.02 | CVP12-VFD-C006 (9ZI05AC36) | 1LCA20CE101, CEP-B VFD CURRENT, VFD PNL, CEP VFD ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC03-03, AC02-03, DR04-03, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
37 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C007 (9ZI05AC37) | 1LCB20AP01A, CEP-B VFD VCB (Q3), HT SWGR ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
38 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C008 (9ZI05AC38) | 1LCB20AP001, CEP-B SOURCE BREAKER, HT SWGR ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
39 | VFD | E04W0.5 | 10.8.02 | CVP12-VFD-C009 (9ZI05AC39) | 1LCB20AP001, CEP-B SOURCE BREAKER, HT SWGR ROOM | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | HTUD | ZZ99- , MV21-03, MV22-03, MV23-03, MV24-03, MV25-03, MV27-R2, MA06-04, MR09-04, LR06-04, CC91-04, CC83-04, CC93-03, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
40 | VFD | E04V0.5 | 10.7.02 | CVP12-VFD-C010 (9ZI05AC40) | 1LCB20AP001, CEP-B BYPASS MODE, VFD BKR PNL | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 70 | [5 empty] | CONTROL AND MONITORING | VFD | ZZ99- , AC03-03, AC02-03, DR04-03, AC01-04, DR03-04, DC11-04, DC10-04, DC09-04, DC08-04, DC07-04, LR07-04, CC90-04, CC81-04, CC33-04, CC42-04, CC41-03, ZZ99- |  | BPL | EDN
1 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CRE0 1-01 (9ZB02AP01) | RISER | CRE01-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | EARTHING |  | ZZ99- , CC92-01, CC88-01, CC86-02, CC84-01, CC83-01 |  | EDN | EDN
2 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP01-CRE0 3-02 (9ZB02AP02) | CVP01-PE | CRE03-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
3 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP02-CRE0 5-03 (9ZB02AP03) | CVP02-PE | CRE05-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
4 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP03-CRE0 7-04 (9ZB02AP04) | CVP03-PE | CRE07-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
5 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP04-CRE0 9-05 (9ZB02AP05) | CVP04-PE | CRE09-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
6 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP05-RISE R-06 (9ZB02AP06) | CVP05-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
7 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CRE1 1-07 (9ZB02AP07) | RISER | CRE11-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | EARTHING |  | ZZ99- , CC01-01, CC73-01, CC75-01, CC77-01, CC79-01, CC81-01, CC33-02, CC93-01, CC84-01, CC86-02, CC87-01 |  | EDN | EDN
8 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP06-CRE1 3-08 (9ZB02AP08) | CVP06-PE | CRE13-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
9 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP07-CRE1 5-09 (9ZB02AP09) | CVP07-PE | CRE15-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
10 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP08-CRE1 7-10 (9ZB02AP10) | CVP08-PE | CRE17-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
11 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP09-CRE1 9-11 (9ZB02AP11) | CVP09-PE | CRE19-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
12 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP10-CTE0 1-12 (9ZB02AP12) | CVP10-PE | CTE01-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
13 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CTE01-RISE R-13 (9ZB02AP13) | CTE01-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
14 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CRE2 1-14 (9ZB02AP14) | RISER | CRE21-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 49 | [5 empty] | EARTHING |  | ZZ99- , CC05-01, CC04-01, CC62-01, CC63-01, CC64-01, CC65-01, CC66-01, CC67-01, CC34-01, CC93-01, CC84-01, CC85-01 |  | EDN | EDN
15 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP11-CRE2 3-15 (9ZB02AP15) | CVP11-PE | CRE23-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
16 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP12-CRE2 5-16 (9ZB02AP16) | CVP12-PE | CRE25-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 16 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
17 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP13-CRE2 7-17 (9ZB02AP17) | CVP13-PE | CRE27-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 17 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
18 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP14-CRE2 9-18 (9ZB02AP18) | CVP14-PE | CRE29-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 18 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
19 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP15-CTE0 2-19 (9ZB02AP19) | CVP15-PE | CTE02-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 19 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
20 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CTE02-RISE R-20 (9ZB02AP20) | CTE02-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 20 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
21 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CRE6 1-21 (9ZB02AP21) | RISER | CRE61-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 26 | [5 empty] | EARTHING |  | ZZ99- , CC48-01, CC49-01 |  | EDN | EDN
22 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP31-CWB0 1-22 (9ZB02AP22) | CVP31-PE | CWB01-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
23 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CWB01-CWB0 2-23 (9ZB02AP23) | CWB01-PE | CWB02-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
24 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CWB02-RISE R-24 (9ZB02AP24) | CWB02-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
25 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CRE6 3-25 (9ZB02AP25) | RISER | CRE63-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 45 | [5 empty] | EARTHING |  | ZZ99- , CC08-01, CC17-01, CC18-01, CC27-01, CC28-01, CC37-01, CC38-01, CC47-01, CC48-01, CC49-01 |  | EDN | EDN
26 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CVP32-CTE0 3-26 (9ZB02AP26) | CTE03-PE | CTE03-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
27 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CTE03-RISE R-27 (9ZB02AP27) | CTE03-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 15 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
28 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CRE6 5-28 (9ZB02AP28) | RISER | CRE65-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 41 | [5 empty] | EARTHING |  | ZZ99- , CC29-01, CC37-01, CC38-01, CC47-01, CC48-01, CC49-01 |  | EDN | EDN
29 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CJJ0 1-29 (9ZB02AP29) | RISER | CJJ01-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 40 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
30 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJJ02-CJJ0 3-30 (9ZB02AP30) | CJJ02-PE | CJJ03-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
31 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJJ53-CJJ0 5-31 (9ZB02AP31) | CJJ53-PE | CJJ05-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 6 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
32 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJJ56-CJJ0 8-32 (9ZB02AP32) | CJJ56-PE | CJJ08-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 7 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
33 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJJ08-CJJ1 1-33 (9ZB02AP33) | CJJ08-PE | CJJ11-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 8 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
34 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJJ61-CCA0 1-34 (9ZB02AP34) | CJJ61-PE | CCA01-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 9 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
35 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CCA51-RISE R-35 (9ZB02AP35) | CCA51-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
36 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CCA0 3-36 (9ZB02AP36) | RISER | CCA03-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
37 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CCA53-CCA0 5-37 (9ZB02AP37) | CCA53-PE | CCA05-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
38 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CCA10-CCA0 6-39 (9ZB02AP38) | CCA10-PE | CCA06-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 3 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
39 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CCA56-CJJ4 1-40 (9ZB02AP39) | CCA56-PE | CJJ41-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 3 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
40 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJJ91-CJF2 1-41 (9ZB02AP40) | CJJ91-PE | CJF21-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 3 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
41 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF24-RISE R-42 (9ZB02AP41) | CJF24-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 3 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
42 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CJF0 1-43 (9ZB02AP42) | RISER | CJF01-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 25 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
43 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF05-CJF1 1-44 (9ZB02AP43) | CJF05-PE | CJF11-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 3 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
44 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF14-CJF1 6-45 (9ZB02AP44) | CJF14-PE | CJF16-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 3 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
45 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF19-CJJ0 8-46 (9ZB02AP45) | CJF19-PE | CJJ08-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 3 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
46 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJJ08-RISE R-47 (9ZB02AP46) | CJJ08-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
47 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CJF4 1-48 (9ZB02AP47) | RISER | CJF41-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
48 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF42-CJF4 9-49 (9ZB02AP48) | CJF42-PE | CJF49-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
49 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF50-CJF5 1-50 (9ZB02AP49) | CJF50-PE | CJF51-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
50 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF53-CJF6 1-51 (9ZB02AP50) | CJF53-PE | CJF61-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
51 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF64-CJF7 1-52 (9ZB02AP51) | CJF64-PE | CJF71-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
52 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF73-CJF8 1-53 (9ZB02AP52) | CJF73-PE | CJF81-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
53 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF82-RISE R-54 (9ZB02AP53) | CJF82-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 20 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
54 | EFCON JK | D01Q035 | 10.4.01 | 1PE-RISER-CJF8 6-55 (9ZB02AP54) | RISER | CJF86-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 20 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
55 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF87-CJF9 8-56 (9ZB02AP55) | CJF87-PE | CJF98-PE | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 5 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
56 | EFCON JK | D01Q035 | 10.4.01 | 1PE-CJF99-RISE R-57 (9ZB02AP56) | CJF99-PE | RISER | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 20 | [5 empty] | EARTHING |  | SITE ROUTING |  | EDN | EDN
1 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-01-DCDB1-01 | CRE01-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 41 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC31-02, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
2 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-01-DCDB2-02 | CRE01-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 40 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC31-02, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
3 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-03-DCDB1-03 | CRE03-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 42 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC31-02, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
4 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-03-DCDB2-04 | CRE03-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 41 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC31-02, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
5 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-05-DCDB1-05 | CRE05-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 40 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC31-02, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
6 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-05-DCDB2-06 | CRE05-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 39 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC31-02, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
7 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-07-DCDB1-07 | CRE07-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | 37 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC30-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
8 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-07-DCDB2-08 | CRE07-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC30-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
9 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-09-DCDB1-09 | CRE09-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | 35 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC30-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
10 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-09-DCDB2-10 | CRE09-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 30 | 34 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC30-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
11 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-11-DCDB1-11 | CRE11-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 42 | 42 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC44-02, CC69-01, CC68-01, CC67-01, CC66-01, CC25-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
12 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-11-DCDB2-12 | CRE11-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 42 | 42 | 11.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC44-02, CC69-01, CC68-01, CC67-01, CC66-01, CC25-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
13 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-13-DCDB1-13 | CRE13-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 42 | 40 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC44-02, CC69-01, CC68-01, CC67-01, CC66-01, CC25-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
14 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-13-DCDB2-14 | CRE13-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 42 | 41 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC44-02, CC69-01, CC68-01, CC67-01, CC66-01, CC25-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
15 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-15-DCDB1-15 | CRE15-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 38 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC45-02, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
16 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-15-DCDB2-16 | CRE15-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 38 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC45-02, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
17 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-17-DCDB1-17 | CRE17-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 35 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC45-02, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
18 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-17-DCDB2-18 | CRE17-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 36 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC45-02, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
19 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-19-DCDB1-19 | CRE19-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 34 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC45-02, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
20 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-19-DCDB2-20 | CRE19-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 33 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC45-02, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
21 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-21-DCDB1-21 | CRE21-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 40 | 40 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC85-01, CC84-01, CC93-01, CC34-01, CC67-01, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
22 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-21-DCDB2-22 | CRE21-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 40 | 40 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC85-01, CC84-01, CC93-01, CC34-01, CC67-01, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
23 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-23-DCDB1-23 | CRE23-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 40 | 39 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC85-01, CC84-01, CC93-01, CC34-01, CC67-01, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
24 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-23-DCDB2-24 | CRE23-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 40 | 39 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC85-01, CC84-01, CC93-01, CC34-01, CC67-01, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
25 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-25-DCDB1-25 | CRE25-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 40 | 36 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC85-01, CC84-01, CC93-01, CC34-01, CC67-01, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
26 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-25-DCDB2-26 | CRE25-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 40 | 36 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC85-01, CC84-01, CC93-01, CC34-01, CC67-01, CC66-01, CC65-01, CC20-01, CC19-01, ZZ99- |  | EDN | EDN
27 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-27-DCDB1-27 | CRE27-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 34 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC40-02, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
28 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-27-DCDB2-28 | CRE27-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 34 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC40-02, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
29 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-29-DCDB1-29 | CRE29-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 31 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC40-02, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
30 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-29-DCDB2-30 | CRE29-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 31 | 12.12.2019 | DR0816_0001 |  |  | EARTHING |  | ZZ99- , CC40-02, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
31 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-61-DCDB1-31 | CRE61-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 41 | 40 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC49-01, CC48-01, CC47-01, CC38-01, CC37-01, CC28-01, CC27-01, CC19-01, ZZ99- |  | EDN | EDN
32 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-61-DCDB2-32 | CRE61-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 41 | 40 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC49-01, CC48-01, CC47-01, CC38-01, CC37-01, CC28-01, CC27-01, CC19-01, ZZ99- |  | EDN | EDN
33 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-63-DCDB1-33 | CRE63-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 37 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC46-01, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
34 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-63-DCDB2-34 | CRE63-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 38 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC46-01, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-01, ZZ99- |  | EDN | EDN
35 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-65-DCDB1-35 | CRE65-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 34 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC39-01, CC38-01, CC37-01, CC28-01, CC27-01, CC19-01, ZZ99- |  | EDN | EDN
36 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRE-65-DCDB2-36 | CRE65-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 36 | 35 | 13.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC39-01, CC38-01, CC37-01, CC28-01, CC27-01, CC19-02, ZZ99- |  | EDN | EDN
37 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CTE-01-DCDB1-37 | CTE01-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 37 | 34 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC61-01, CC60-01, CC59-01, CC58-01, CC57-01, CC56-01, CC19-02, ZZ99- |  | EDN | EDN
38 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CTE-01-DCDB2-38 | CTE01-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 37 | 35 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC61-01, CC60-01, CC59-01, CC58-01, CC57-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
39 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CTE-02-DCDB1-39 | CTE02-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 32 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC60-01, CC59-01, CC58-01, CC57-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
40 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CTE-02-DCDB2-40 | CTE02-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 32 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC60-01, CC59-01, CC58-01, CC57-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
41 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CTE-03-DCDB1-41 | CTE03-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 37 | 31 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC48-01, CC47-01, CC38-01, CC37-01, CC28-01, CC27-01, CC19-02, ZZ99- |  | EDN | EDN
42 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CTE-03-DCDB2-42 | CTE03-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 37 | 31 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC48-01, CC47-01, CC38-01, CC37-01, CC28-01, CC27-01, CC19-02, ZZ99- |  | EDN | EDN
43 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-01-DCDB1-43 | CJJ01-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 36 | 36 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC80-01, CC24-01, CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
44 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-01-DCDB2-44 | CJJ01-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 36 | 36 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC80-01, CC24-01, CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
45 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-03-DCDB1-45 | CJJ03-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 31 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC24-01, CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
46 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-03-DCDB2-46 | CJJ03-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 32 | 14.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC24-01, CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
47 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-05-DCDB1-47 | CJJ05-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 31 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC24-01, CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
48 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-05-DCDB2-48 | CJJ05-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 30 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC24-01, CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
49 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-08-DCDB1-49 | CJJ08-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 33 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
50 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-08-DCDB2-50 | CJJ08-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 32 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
51 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-11-DCDB1-51 | CJJ11-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 27 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
52 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-11-DCDB2-52 | CJJ11-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 26 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
53 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-01-DCDB1-53 | CCA01-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 26 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
54 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-01-DCDB2-54 | CCA01-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 26 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC25-01, CC56-02, CC19-02, ZZ99- |  | EDN | EDN
55 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-03-DCDB1-55 | CCA03-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 34 | 39 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC78-01, CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
56 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-06-DCDB2-60 | CCA03-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 34 | 34 | 15.12.2019 | DR0816_0002 |  |  | EARTHING |  | ZZ99- , CC78-01, CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
57 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-03-DCDB2-56 | CCA05-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 32 | 36 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
58 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-05-DCDB1-57 | CCA05-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 32 | 39 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
59 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-05-DCDB2-58 | CCA06-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 32 | 38 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
60 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CCA-03-DCDB1-59 | CCA06-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 32 | 36 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
61 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-41-DCDB1-61 | CJJ41-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 29 | 37 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC20-01, CC19-02, ZZ99- |  | EDN | EDN
62 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJJ-41-DCDB2-62 | CJJ41-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 29 | 37 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC20-01, CC19-02, ZZ99- |  | EDN | EDN
63 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF01-DCDB1-63 | CJF01-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 36 | 43 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC76-01, CC14-01, CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
64 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF01-DCDB2-64 | CJF01-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 36 | 43 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC76-01, CC14-01, CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
65 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF11-DCDB1-65 | CJF11-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 39 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC14-01, CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
66 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF11-DCDB2-66 | CJF11-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 40 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC14-01, CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
67 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF16-DCDB1-67 | CJF16-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 39 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
68 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF16-DCDB2-68 | CJF16-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 31 | 39 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC15-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
69 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF21-DCDB1-69 | CJF21-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 29 | 22 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC20-01, CC19-02, ZZ99- |  | EDN | EDN
70 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF21-DCDB2-70 | CJF21-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 29 | 22 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC20-01, CC19-02, ZZ99- |  | EDN | EDN
71 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF41-DCDB1-71 | CJF41-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 38 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC74-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
72 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF41-DCDB2-72 | CJF41-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 38 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC74-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
73 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF49-DCDB1-73 | CJF49-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 36 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC74-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
74 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF49-DCDB2-74 | CJF49-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 38 | 36 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC74-01, CC13-01, CC22-01, CC21-01, CC20-01, CC19-02, ZZ99- |  | EDN | EDN
75 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF51-DCDB1-75 | CJF51-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 37 | 33 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC11-01, CC10-01, CC54-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
76 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF51-DCDB2-76 | CJF51-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 37 | 33 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC11-01, CC10-01, CC54-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
77 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF61-DCDB1-77 | CJF61-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 37 | 31 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC11-01, CC10-01, CC54-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
78 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF61-DCDB2-78 | CJF61-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 36 | 31 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC11-01, CC10-01, CC54-01, CC55-01, CC19-01, ZZ99- |  | EDN | EDN
79 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF71-DCDB1-79 | CJF71-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 32 | 27 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC10-01, CC54-01, CC55-01, CC19-01, ZZ99- |  | EDN | EDN
80 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF71-DCDB2-80 | CJF71-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 32 | 27 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC10-01, CC54-01, CC55-01, CC19-01, ZZ99- |  | EDN | EDN
81 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF86-DCDB1-83 | CJF81-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 28 | 24 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC53-01, CC54-01, CC55-01, CC19-01, ZZ99- |  | EDN | EDN
82 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF86-DCDB2-84 | CJF81-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 29 | 24 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC53-01, CC54-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
83 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF98-DCDB1-85 | CJF86-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC04-01, CC53-01, CC54-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
84 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CJF98-DCDB2-86 | CJF86-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC04-01, CC53-01, CC54-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
85 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRC01-DCDB1-87 | CJF98-A | BOP DCDB-1 (A1) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 30 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC04-01, CC53-01, CC54-01, CC55-01, CC19-02, ZZ99- |  | EDN | EDN
86 | EFCON AZ | D01Q035 | 10.4.01 | 1A-CRC01-DCDB2-88 | CJF98-A | BOP DCDB-2 (A2) | 01C X 035 XLPE-Al FRLS ( 1.1 kV ) | 35 | 30 | 17.12.2019 | DR0816_0006 |  |  | EARTHING |  | ZZ99- , CC04-01, CC53-01, CC54-01, CC55-01, CC19-01, ZZ99- |  | EDN | EDN
C1 | DCDB1 | D01Q630 | 10.4.05 | 24V ELTEK-M1 P01 | MAIN PLANT 24V BATTERY CHARGR1 +VE | MAIN PLANT 24V BATTERY BANK1 +VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 60 | 23.09.2019 | DR1050_0014
C2 | DCDB1 | D01Q630 | 10.4.05 | 24V ELTEK-M1 P02 | MAIN PLANT 24V BATTERY CHARGR1 +VE | MAIN PLANT 24V BATTERY BANK1 +VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 60 | 23.09.2019 | DR1050_0014
C3 | DCDB1 | D01Q630 | 10.4.05 | 24V ELTEK-M1 P03 | MAIN PLANT 24V BATTERY CHARGR1 -VE | MAIN PLANT 24V BATTERY BANK1 -VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 60 | 23.09.2019 | DR1050_0014
C4 | DCDB1 | D01Q630 | 10.4.05 | 24V ELTEK-M1 P04 | MAIN PLANT 24V BATTERY CHARGR1 -VE | MAIN PLANT 24V BATTERY BANK1 -VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 60 | 23.09.2019 | DR1050_0014
1 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF01-001 | 1-DCDB1- FDR01:T1 | MAIN PLANT 24V BATTERY BANK1 +VE | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 35 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC23-01, CC22-01, CC76-01, ZZ99- |  | EDN | EDN
1 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF01-01A | 1-DCDB1- FDR01:T1 | CJF01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 35 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC23-01, CC22-01, CC76-01, ZZ99- |  | EDN | EDN
2 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF01-002 | 1-DCDB1- FDR02:T3 | CJF01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 35 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC20-01, CC64-01, CC14-01, ZZ99- |  | EDN | EDN
2 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF01-02A | 1-DCDB1- FDR02:T3 | CJF01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 35 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC20-01, CC64-01, CC14-01, ZZ99- |  | EDN | EDN
3 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF04-003 | 1-DCDB1- FDR03:T5 | CJF04-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 36 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC55-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
3 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF04-03A | 1-DCDB1- FDR03:T5 | CJF04-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 36 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC20-01, CC64-01, CC14-01, ZZ99- |  | EDN | EDN
4 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF05-004 | 1-DCDB1- FDR04:T7 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC55-03, ZZ99- |  | EDN | EDN
4 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF05-04A | 1-DCDB1- FDR04:T7 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC65-02, CC20-01, CC55-03, ZZ99- |  | EDN | EDN
5 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF05-005 | 1-DCDB1- FDR05:T9 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-01, CC65-02, CC20-01, CC55-03, ZZ99- |  | EDN | EDN
5 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF05-05A | 1-DCDB1- FDR05:T9 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-01, CC65-02, CC20-01, CC55-03, ZZ99- |  | EDN | EDN
6 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF12-006 | 1-DCDB1- FDR06:T11 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 38 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-01, CC65-02, CC64-01, CC15-01, CC55-03, ZZ99- |  | EDN | EDN
6 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF12-06A | 1-DCDB1- FDR06:T11 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 38 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC55-01, ZZ99- |  | EDN | EDN
7 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF12-007 | 1-DCDB1- FDR07:T13 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 36 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC55-02, ZZ99- |  | EDN | EDN
7 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF12-07A | 1-DCDB1- FDR07:T13 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 36 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC19-01, ZZ99- |  | EDN | EDN
8 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF13-008 | 1-DCDB1- FDR08:T15 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 48 | 37 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC19-01, ZZ99- |  | EDN | EDN
8 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF13-08A | 1-DCDB1- FDR08:T15 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 48 | 37 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC19-02, ZZ99- |  | EDN | EDN
9 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF13-009 | 1-DCDB1- FDR09:T17 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | 37 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-01, CC19-02, ZZ99- |  | EDN | EDN
9 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF13-09A | 1-DCDB1- FDR09:T17 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | 37 | 20.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-01, CC36-01, CC38-02, CC47-01, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
10 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF17-010 | 1-DCDB1- FDR10:T19 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | 41 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-02, CC36-01, CC38-02, CC47-02, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
10 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF17-10A | 1-DCDB1- FDR10:T19 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | 41 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
11 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF17-011 | 1-DCDB1- FDR11:T21 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 41 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
11 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF17-11A | 1-DCDB1- FDR11:T21 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 41 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
12 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF18-012 | 1-DCDB1- FDR12:T23 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 42 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
12 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF18-12A | 1-DCDB1- FDR12:T23 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 42 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
13 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF18-013 | 1-DCDB1- FDR13:T25 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 42 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
13 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF18-13A | 1-DCDB1- FDR13:T25 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 42 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
14 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF22-014 | 1-DCDB1- FDR14:T27 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 20 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
14 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF22-14A | 1-DCDB1- FDR14:T27 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 20 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
15 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF22-015 | 1-DCDB1- FDR15:T29 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 20 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
15 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF22-15A | 1-DCDB1- FDR15:T29 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 20 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
16 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF23-016 | 1-DCDB1- FDR16:T31 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 29 | 20 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
16 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF23-16A | 1-DCDB1- FDR16:T31 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 29 | 20 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, ZZ99- |  | EDN | EDN
17 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF23-017 | 1-DCDB1- FDR17:T33 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 29 | 20 | 21.09.2019 | DR0816_0005 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC23-01, CC78-01, ZZ99- |  | EDN | EDN
17 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF23-17A | 1-DCDB1- FDR17:T33 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 29 | 20 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-02, CC35-01, CC34-01, CC33-02, CC32-02, CC23-01, CC21-01, ZZ99- |  | EDN | EDN
18 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF41-018 | 1-DCDB1- FDR18:T35 | CJF41-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 63 | 35 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC65-02, CC21-01, ZZ99- |  | EDN | EDN
18 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF41-18A | 1-DCDB1- FDR18:T35 | CJF41-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 63 | 35 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-02, CC65-02, CC21-01, ZZ99- |  | EDN | EDN
19 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF51-019 | 1-DCDB1- FDR19:T37 | CJF51-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 63 | 38 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC32-01, CC31-02, ZZ99- |  | EDN | EDN
19 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF51-19A | 1-DCDB1- FDR19:T37 | CJF51-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 63 | 38 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC28-02, CC29-01, CC58-02, CC35-01, CC67-01, CC31-02, ZZ99- |  | EDN | EDN
20 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF61-020 | 1-DCDB1- FDR20:T39 | CJF61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 39 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC32-02, CC31-02, ZZ99- |  | EDN | EDN
20 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF61-20A | 1-DCDB1- FDR20:T39 | CJF61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 39 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-02, CC66-01, CC30-01, ZZ99- |  | EDN | EDN
21 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF71-021 | 1-DCDB1- FDR21:T41 | CJF71-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 46 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-01, CC35-01, CC67-01, CC30-01, ZZ99- |  | EDN | EDN
21 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF71-21A | 1-DCDB1- FDR21:T41 | CJF71-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 46 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
22 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF86-022 | 1-DCDB1- FDR22:T43 | CJF86-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 45 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
22 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF86-22A | 1-DCDB1- FDR22:T43 | CJF86-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 45 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-03, CC58-02, CC59-02, CC60-01, CC45-02, CC44-02, ZZ99- |  | EDN | EDN
23 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF98-023 | 1-DCDB1- FDR23:T45 | CJF98-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 46 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-03, CC58-02, CC59-02, CC60-01, CC45-02, ZZ99- |  | EDN | EDN
23 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJF98-23A | 1-DCDB1- FDR23:T45 | CJF98-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 46 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-03, CC59-02, CC60-01, CC45-02, ZZ99- |  | EDN | EDN
24 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ01-024 | 1-DCDB1- FDR24:T47 | CJJ01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 31 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC36-01, CC38-02, CC47-01, CC46-01, CC45-02, ZZ99- |  | EDN | EDN
24 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ01-24A | 1-DCDB1- FDR24:T47 | CJJ01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 31 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC59-02, CC40-02, CC41-01, ZZ99- |  | EDN | EDN
25 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ02-025 | 1-DCDB1- FDR25:T49 | CJJ02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 32 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-03, CC59-02, CC40-02, CC41-01, ZZ99- |  | EDN | EDN
25 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ02-25A | 1-DCDB1- FDR25:T49 | CJJ02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 32 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC36-01, CC38-02, CC39-01, CC40-02, ZZ99- |  | EDN | EDN
26 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ03-026 | 1-DCDB1- FDR26:T51 | CJJ03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 33 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-03, CC59-02, CC40-02, ZZ99- |  | EDN | EDN
26 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ03-26A | 1-DCDB1- FDR26:T51 | CJJ03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 33 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-03, CC59-02, CC60-01, CC61-01, CC49-01, ZZ99- |  | EDN | EDN
27 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ05-027 | 1-DCDB1- FDR27:T53 | CJJ05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 35 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-03, CC59-02, CC60-02, CC46-01, ZZ99- |  | EDN | EDN
27 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ05-27A | 1-DCDB1- FDR27:T53 | CJJ05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 35 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-01, CC59-02, CC39-01, ZZ99- |  | EDN | EDN
28 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ06-028 | 1-DCDB1- FDR28:T55 | CJJ06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
28 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ06-28A | 1-DCDB1- FDR28:T55 | CJJ06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 21.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
29 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ08-029 | 1-DCDB1- FDR29:T57 | CJJ08-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 55 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
29 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ08-29A | 1-DCDB1- FDR29:T57 | CJJ08-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 55 | 0 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, ZZ99- |  | EDN | EDN
30 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ11-030 | 1-DCDB1- FDR30:T59 | CJJ11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 42 | 24.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, ZZ99- |  | EDN | EDN
30 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ11-30A | 1-DCDB1- FDR30:T59 | CJJ11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 42 | 24.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, CC34-01, ZZ99- |  | EDN | EDN
31 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ61-031 | 1-DCDB1- FDR31:T61 | CJJ61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 40 | 24.09.2019 | DR0816_0007 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-01, CC58-01, CC35-01, CC34-01, ZZ99- |  | EDN | EDN
31 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CJJ61-31A | 1-DCDB1- FDR31:T61 | CJJ61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 40 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | CC26-01, CC25-02, CC66-01, CC67-01, CC34-01, CC42-02, CC85-01, CC86-02, CC88-01, CC92-01, ZZ99- |  | EDN | EDN
32 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA01-032 | 1-DCDB1- FDR32:T63 | CCA01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 41 | 24.09.2019 | DR0816_0004 |  |  | EARTHING |  | Site Route |  | EDN | EDN
32 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA01-32A | 1-DCDB1- FDR32:T63 | CCA01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 41 | 24.09.2019 | DR0816_0004 |  |  | EARTHING |  | Site Route |  | EDN | EDN
33 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA03-033 | 1-DCDB1- FDR33:T65 | CCA03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 30 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC23-01, CC22-01, CC76-01, ZZ99- |  | EDN | EDN
33 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA03-33A | 1-DCDB1- FDR33:T65 | CCA03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 30 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC23-01, CC22-01, CC76-01, ZZ99- |  | EDN | EDN
34 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA05-034 | 1-DCDB1- FDR34:T67 | CCA05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 52 | 29 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC20-01, CC64-01, CC14-01, ZZ99- |  | EDN | EDN
34 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA05-34A | 1-DCDB1- FDR34:T67 | CCA05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 52 | 29 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC20-01, CC64-01, CC14-01, ZZ99- |  | EDN | EDN
35 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA06-035 | 1-DCDB1- FDR35:T69 | CCA06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 25 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC55-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
35 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA06-35A | 1-DCDB1- FDR35:T69 | CCA06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 25 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC20-01, CC64-01, CC14-01, ZZ99- |  | EDN | EDN
36 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA10-036 | 1-DCDB1- FDR36:T71 | CCA10-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 27 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC56-02, CC55-03, ZZ99- |  | EDN | EDN
36 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CCA10-36A | 1-DCDB1- FDR36:T71 | CCA10-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 27 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC65-02, CC20-01, CC55-03, ZZ99- |  | EDN | EDN
37 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE01-037 | 1-DCDB1- FDR37:T73 | CRE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 40 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-01, CC65-02, CC20-01, CC55-03, ZZ99- |  | EDN | EDN
37 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE01-37A | 1-DCDB1- FDR37:T73 | CRE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 40 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-01, CC65-02, CC20-01, CC55-03, ZZ99- |  | EDN | EDN
38 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE03-038 | 1-DCDB1- FDR38:T75 | CRE03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 42 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-01, CC65-02, CC64-01, CC15-01, CC55-03, ZZ99- |  | EDN | EDN
38 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE03-38A | 1-DCDB1- FDR38:T75 | CRE03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 42 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC55-01, ZZ99- |  | EDN | EDN
39 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE05-039 | 1-DCDB1- FDR39:T77 | CRE05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 46 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC55-02, ZZ99- |  | EDN | EDN
39 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE05-39A | 1-DCDB1- FDR39:T77 | CRE05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 46 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC19-01, ZZ99- |  | EDN | EDN
40 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE07-040 | 1-DCDB1- FDR40:T79 | CRE07-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 40 | 47 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC19-01, ZZ99- |  | EDN | EDN
40 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE07-40A | 1-DCDB1- FDR40:T79 | CRE07-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 40 | 47 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-03, CC19-02, ZZ99- |  | EDN | EDN
41 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE09-041 | 1-DCDB1- FDR41:T81 | CRE09-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 45 | 50 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC56-01, CC19-02, ZZ99- |  | EDN | EDN
41 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE09-41A | 1-DCDB1- FDR41:T81 | CRE09-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 45 | 50 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-01, CC36-01, CC38-02, CC47-01, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
42 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE11-042 | 1-DCDB1- FDR42:T83 | CRE11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 38 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-02, CC36-01, CC38-02, CC47-02, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
42 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE11-42A | 1-DCDB1- FDR42:T83 | CRE11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 38 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
43 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE13-043 | 1-DCDB1- FDR43:T85 | CRE13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 38 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
43 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE13-43A | 1-DCDB1- FDR43:T85 | CRE13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 38 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
44 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE15-044 | 1-DCDB1- FDR44:T87 | CRE15-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | 42 | 24.09.2019 | DR0816_0004 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
44 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE15-44A | 1-DCDB1- FDR44:T87 | CRE15-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | 42 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
45 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE17-045 | 1-DCDB1- FDR45:T89 | CRE17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 44 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
45 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE17-45A | 1-DCDB1- FDR45:T89 | CRE17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 44 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
46 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE19-046 | 1-DCDB1- FDR46:T91 | CRE19-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 44 | 46 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
46 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE19-46A | 1-DCDB1- FDR46:T91 | CRE19-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 44 | 46 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
47 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE21-047 | 1-DCDB1- FDR47:T93 | CRE21-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 58 | 35 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
47 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE21-47A | 1-DCDB1- FDR47:T93 | CRE21-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 58 | 35 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
48 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE23-048 | 1-DCDB1- FDR48:T95 | CRE23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 42 | 37 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
48 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE23-48A | 1-DCDB1- FDR48:T95 | CRE23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 42 | 37 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, ZZ99- |  | EDN | EDN
49 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE25-049 | 1-DCDB1- FDR49:T97 | CRE25-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 40 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC23-01, CC78-01, ZZ99- |  | EDN | EDN
49 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE25-49A | 1-DCDB1- FDR49:T97 | CRE25-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 40 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-02, CC35-01, CC34-01, CC33-02, CC32-02, CC23-01, CC21-01, ZZ99- |  | EDN | EDN
50 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE27-050 | 1-DCDB1- FDR50:T99 | CRE27-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 55 | 43 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC65-02, CC21-01, ZZ99- |  | EDN | EDN
50 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE27-50A | 1-DCDB1- FDR50:T99 | CRE27-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 55 | 43 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-02, CC65-02, CC21-01, ZZ99- |  | EDN | EDN
51 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE29-051 | 1-DCDB1- FDR51:T101 | CRE29-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 40 | 47 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC32-01, CC31-02, ZZ99- |  | EDN | EDN
51 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE29-51A | 1-DCDB1- FDR51:T101 | CRE29-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 40 | 47 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC28-02, CC29-01, CC58-02, CC35-01, CC67-01, CC31-02, ZZ99- |  | EDN | EDN
52 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE61-052 | 1-DCDB1- FDR52:T103 | CRE61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 58 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC25-01, CC24-01, CC32-02, CC31-02, ZZ99- |  | EDN | EDN
52 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE61-52A | 1-DCDB1- FDR52:T103 | CRE61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 58 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC25-02, CC66-01, CC30-01, ZZ99- |  | EDN | EDN
53 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE63-053 | 1-DCDB1- FDR53:T105 | CRE63-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 55 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-01, CC35-01, CC67-01, CC30-01, ZZ99- |  | EDN | EDN
53 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE63-53A | 1-DCDB1- FDR53:T105 | CRE63-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 55 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
54 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE65-054 | 1-DCDB1- FDR54:T107 | CRE65-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 52 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
54 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRE65-54A | 1-DCDB1- FDR54:T107 | CRE65-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 52 | 24.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-03, CC58-02, CC59-02, CC60-01, CC45-02, CC44-02, ZZ99- |  | EDN | EDN
55 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CTE01-055 | 1-DCDB1- FDR55:T109 | CTE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 51 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-03, CC58-02, CC59-02, CC60-01, CC45-02, ZZ99- |  | EDN | EDN
55 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CTE01-55A | 1-DCDB1- FDR55:T109 | CTE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 51 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-03, CC59-02, CC60-01, CC45-02, ZZ99- |  | EDN | EDN
56 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRC01-056 | 1-DCDB1- FDR56:T111 | CRC01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 51 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC36-01, CC38-02, CC47-01, CC46-01, CC45-02, ZZ99- |  | EDN | EDN
56 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRC01-56A | 1-DCDB1- FDR56:T111 | CRC01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 51 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC59-02, CC40-02, CC41-01, ZZ99- |  | EDN | EDN
57 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRC03-057 | 1-DCDB1- FDR57:T113 | CRC03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 51 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-03, CC59-02, CC40-02, CC41-01, ZZ99- |  | EDN | EDN
57 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1CRC03-57A | 1-DCDB1- FDR57:T113 | CRC03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 51 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC36-01, CC38-02, CC39-01, CC40-02, ZZ99- |  | EDN | EDN
58 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1VMS-058 | 1-DCDB1- FDR58:T115 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 31 | 38 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-03, CC59-02, CC40-02, ZZ99- |  | EDN | EDN
58 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1VMS-58A | 1-DCDB1- FDR58:T115 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 31 | 38 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-03, CC59-02, CC60-01, CC61-01, CC49-01, ZZ99- |  | EDN | EDN
59 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1VMS-059 | 1-DCDB1- FDR59:T117 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 31 | 38 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-02, CC58-03, CC59-02, CC60-02, CC46-01, ZZ99- |  | EDN | EDN
59 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1VMS-59A | 1-DCDB1- FDR59:T117 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 31 | 38 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-02, CC57-01, CC58-01, CC59-02, CC39-01, ZZ99- |  | EDN | EDN
60 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1NWPD-0106 | 1-DCDB1- FDR60:T119 | NWPD01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 39 | 36 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
60 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1NWPD-106A | 1-DCDB1- FDR60:T119 | NWPD01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 39 | 36 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
61 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1NWPD-0206 | 1-DCDB1- FDR61:T121 | NWPD02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 35 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
61 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1NWPD-206A | 1-DCDB1- FDR61:T121 | NWPD02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 37 | 35 | 25.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, ZZ99- |  | EDN | EDN
62 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1UCD-062 | 1-DCDB1- FDR62:T123 | UCD-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 61 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, ZZ99- |  | EDN | EDN
62 | DCDB1 | D01Q070 | 10.4.02 | 1DCDB1UCD-62A | 1-DCDB1- FDR62:T123 | UCD-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 61 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-02, CC58-02, CC35-01, CC34-01, ZZ99- |  | EDN | EDN
63 | DCDB1 | D02G120 | 10.4.10 | 1EARTH1(C&I)-DCDB1-01 | 1-DCDB1- EARTHBUS | ELECTRONIC EARTHPIT CD-BAY | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 55 | 50 | 20.11.2019 | DR0345_1535 |  |  | POWER SUPPLY |  | ZZ99- , CC26-01, CC57-01, CC58-01, CC35-01, CC34-01, ZZ99- |  | EDN | EDN
64 | DCDB1 | D02G120 | 10.4.10 | 1EARTH1(C&I)-DCDB1-02 | 1-DCDB1- EARTHBUS | ELECTRONIC EARTHPIT CD-BAY | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 55 | 50 | 20.11.2019 | DR0345_1535 |  |  | POWER SUPPLY |  | CC26-01, CC25-02, CC66-01, CC67-01, CC34-01, CC42-02, CC85-01, CC86-02, CC88-01, CC92-01, ZZ99- |  | EDN | EDN
C1 | DCDB2 | D01Q630 | 10.4.05 | 24V ELTEK-M2 P01 | MAIN PLANT 24V BATTERY CHARGR2 +VE | MAIN PLANT 24V BATTERY BANK2 +VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 63 | 23.09.2019 | DR1050_0014
C2 | DCDB2 | D01Q630 | 10.4.05 | 24V ELTEK-M2 P02 | MAIN PLANT 24V BATTERY CHARGR2 +VE | MAIN PLANT 24V BATTERY BANK2 +VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 63 | 23.09.2019 | DR1050_0014
C3 | DCDB2 | D01Q630 | 10.4.05 | 24V ELTEK-M2 P03 | MAIN PLANT 24V BATTERY CHARGR2 -VE | MAIN PLANT 24V BATTERY BANK2 -VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 63 | 26.09.2019 | DR1050_0011
C4 | DCDB2 | D01Q630 | 10.4.05 | 24V ELTEK-M2 P04 | MAIN PLANT 24V BATTERY CHARGR2 -VE | MAIN PLANT 24V BATTERY BANK2 -VE | 01C X 630 XLPE-Al FRLS ( 1.1 kV ) | 60 | 63 | 26.09.2019 | DR1050_0011
1 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF01-001 | 1-DCDB2- FDR02:T3 | CJF01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 30 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, CC76-01, ZZ99- |  | EDN | EDN
1 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF01-01A | 1-DCDB2- FDR03:T5 | CJF01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 30 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, CC76-01, ZZ99- |  | EDN | EDN
2 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF01-002 | 1-DCDB2- FDR04:T7 | CJF01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 30 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
2 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF01-02A | 1-DCDB2- FDR05:T9 | CJF01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 30 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
3 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF04-003 | 1-DCDB2- FDR06:T11 | CJF04-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
3 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF04-03A | 1-DCDB2- FDR07:T13 | CJF04-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
4 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF05-004 | 1-DCDB2- FDR08:T15 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
4 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF05-04A | 1-DCDB2- FDR09:T17 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
5 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF05-005 | 1-DCDB2- FDR10:T19 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
5 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF05-05A | 1-DCDB2- FDR11:T21 | CJF05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 27 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
6 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF12-006 | 1-DCDB2- FDR12:T23 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 26 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
6 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF12-06A | 1-DCDB2- FDR13:T25 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 26 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
7 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF12-007 | 1-DCDB2- FDR14:T27 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 26 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
7 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF12-07A | 1-DCDB2- FDR15:T29 | CJF12-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 26 | 26.09.2019 | DR0816_0006 |  |  | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, CC19-01, ZZ99- |  | EDN | EDN
8 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF13-008 | 1-DCDB2- FDR16:T31 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 25 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, CC19-01, ZZ99- |  | EDN | EDN
8 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF13-08A | 1-DCDB2- FDR17:T33 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 25 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, CC19-02, ZZ99- |  | EDN | EDN
9 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF13-009 | 1-DCDB2- FDR18:T35 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 25 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC55-02, CC19-02, ZZ99- |  | EDN | EDN
9 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF13-09A | 1-DCDB2- FDR19:T37 | CJF13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 25 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC28-02, CC37-02, CC38-01, CC47-01, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
10 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF17-010 | 1-DCDB2- FDR20:T39 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 21 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC38-01, CC47-01, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
10 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF17-10A | 1-DCDB2- FDR21:T41 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 21 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
11 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF17-011 | 1-DCDB2- FDR22:T43 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 22 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
11 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF17-11A | 1-DCDB2- FDR23:T45 | CJF17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 22 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
12 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF18-012 | 1-DCDB2- FDR24:T47 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 23 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
12 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF18-12A | 1-DCDB2- FDR25:T49 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 23 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
13 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF18-013 | 1-DCDB2- FDR26:T51 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 23 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
13 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF18-13A | 1-DCDB2- FDR27:T53 | CJF18-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 23 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
14 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF22-014 | 1-DCDB2- FDR28:T55 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 41 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
14 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF22-14A | 1-DCDB2- FDR29:T57 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 41 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
15 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF22-015 | 1-DCDB2- FDR30:T59 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 41 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
15 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF22-15A | 1-DCDB2- FDR31:T61 | CJF22-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 33 | 41 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
16 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF23-016 | 1-DCDB2- FDR32:T63 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 32 | 42 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
16 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF23-16A | 1-DCDB2- FDR33:T65 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 32 | 42 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC26-01, CC25-01, ZZ99- |  | EDN | EDN
17 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF23-017 | 1-DCDB2- FDR34:T67 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 31 | 42 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC21-01, CC78-01, ZZ99- |  | EDN | EDN
17 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF23-17A | 1-DCDB2- FDR35:T69 | CJF23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 31 | 42 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC21-01, ZZ99- |  | EDN | EDN
18 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF41-018 | 1-DCDB2- FDR36:T71 | CJF41-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 52 | 31 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC21-01, ZZ99- |  | EDN | EDN
18 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF41-18A | 1-DCDB2- FDR37:T73 | CJF41-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 52 | 31 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC64-01, CC21-01, ZZ99- |  | EDN | EDN
19 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF51-019 | 1-DCDB2- FDR38:T75 | CJF51-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 33 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC26-01, CC25-01, CC66-01, CC31-02, ZZ99- |  | EDN | EDN
19 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF51-19A | 1-DCDB2- FDR39:T77 | CJF51-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 33 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC26-01, CC25-01, CC24-01, CC32-01, CC31-02, ZZ99- |  | EDN | EDN
20 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF61-020 | 1-DCDB2- FDR40:T79 | CJF61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC26-01, CC25-01, CC66-01, CC31-02, ZZ99- |  | EDN | EDN
20 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF61-20A | 1-DCDB2- FDR41:T81 | CJF61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 36 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, CC67-01, CC30-01, ZZ99- |  | EDN | EDN
21 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF71-021 | 1-DCDB2- FDR42:T83 | CJF71-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 40 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC28-01, CC37-01, CC36-01, CC35-01, CC67-01, CC30-01, ZZ99- |  | EDN | EDN
21 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF71-21A | 1-DCDB2- FDR43:T85 | CJF71-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 40 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC28-01, CC37-01, CC36-01, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
22 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF86-022 | 1-DCDB2- FDR44:T87 | CJF86-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 43 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC28-01, CC37-01, CC36-01, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
22 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF86-22A | 1-DCDB2- FDR45:T89 | CJF86-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 43 | 26.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
23 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF98-023 | 1-DCDB2- FDR46:T91 | CJF98-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 5 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC28-02, CC37-02, CC38-01, CC47-01, CC46-01, CC45-02, ZZ99- |  | EDN | EDN
23 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJF98-23A | 1-DCDB2- FDR47:T93 | CJF98-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 85 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, CC56-02, CC57-02, CC58-01, CC35-01, CC68-01, CC69-01, CC45-02, ZZ99- |  | EDN | EDN
24 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ01-024 | 1-DCDB2- FDR48:T95 | CJJ01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 34 | 27.09.2019 | DR0816_0009 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-01, CC37-01, CC36-01, CC59-01, CC60-01, CC45-02, ZZ99- |  | EDN | EDN
24 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ01-24A | 1-DCDB2- FDR49:T97 | CJJ01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 34 | 27.09.2019 | DR0816_0002 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-01, CC37-02, CC36-01, CC35-01, CC68-01, CC41-01, ZZ99- |  | EDN | EDN
25 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ02-025 | 1-DCDB2- FDR50:T99 | CJJ02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 35 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, CC68-01, CC41-01, ZZ99- |  | EDN | EDN
25 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ02-25A | 1-DCDB2- FDR51:T101 | CJJ02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 35 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC59-01, CC40-02, ZZ99- |  | EDN | EDN
26 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ03-026 | 1-DCDB2- FDR52:T103 | CJJ03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 35 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, CC68-01, CC40-02, ZZ99- |  | EDN | EDN
26 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ03-26A | 1-DCDB2- FDR53:T105 | CJJ03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 35 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-03, CC28-02, CC37-02, CC38-01, CC47-01, CC48-01, CC49-01, ZZ99- |  | EDN | EDN
27 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ05-027 | 1-DCDB2- FDR54:T107 | CJJ05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 38 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-03, CC28-02, CC37-02, CC38-01, CC47-01, CC46-01, ZZ99- |  | EDN | EDN
27 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ05-27A | 1-DCDB2- FDR55:T109 | CJJ05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 38 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-03, CC28-02, CC37-02, CC38-01, CC39-01, ZZ99- |  | EDN | EDN
28 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ06-028 | 1-DCDB2- FDR56:T111 | CJJ06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 41 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
28 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ06-28A | 1-DCDB2- FDR57:T113 | CJJ06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 41 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
29 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ08-029 | 1-DCDB2- FDR58:T115 | CJJ08-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 42 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
29 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ08-29A | 1-DCDB2- FDR59:T117 | CJJ08-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 42 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, ZZ99- |  | EDN | EDN
30 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ11-030 | 1-DCDB2- FDR60:T119 | CJJ11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 57 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, ZZ99- |  | EDN | EDN
30 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ11-30A | 1-DCDB2- FDR61:T121 | CJJ11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 57 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, ZZ99- |  | EDN | EDN
31 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ61-031 | 1-DCDB2- FDR62:T123 | CJJ61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 42 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, ZZ99- |  | EDN | EDN
31 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CJJ61-31A | 1-DCDB2- FDR62:T123 | CJJ61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 42 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | CC18-01, CC27-03, CC26-01, CC25-01, CC66-01, CC67-01, CC34-01, CC42-02, CC85-01, CC86-02, CC88-01, CC92-01, ZZ99- |  | EDN | EDN
32 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA01-032 | 1-DCDB2- FDR32:T63 | CCA01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 43 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, CC76-01, ZZ99- |  | EDN | EDN
32 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA01-32A | 1-DCDB2- FDR32:T63 | CCA01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 34 | 43 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, CC76-01, ZZ99- |  | EDN | EDN
33 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA03-033 | 1-DCDB2- FDR33:T65 | CCA03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 40 | 31 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
33 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA03-33A | 1-DCDB2- FDR33:T65 | CCA03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 40 | 31 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
34 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA05-034 | 1-DCDB2- FDR34:T67 | CCA05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 33 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
34 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA05-34A | 1-DCDB2- FDR34:T67 | CCA05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 33 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC14-01, ZZ99- |  | EDN | EDN
35 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA06-035 | 1-DCDB2- FDR35:T69 | CCA06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 35 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
35 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA06-35A | 1-DCDB2- FDR35:T69 | CCA06-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 35 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
36 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA10-036 | 1-DCDB2- FDR36:T71 | CCA10-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 39 | 31 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
36 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CCA10-36A | 1-DCDB2- FDR36:T71 | CCA10-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 39 | 31 | 27.09.2019 | DR0816_0008 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
37 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE01-037 | 1-DCDB2- FDR37:T73 | CRE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
37 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE01-37A | 1-DCDB2- FDR37:T73 | CRE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
38 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE03-038 | 1-DCDB2- FDR38:T75 | CRE03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, ZZ99- |  | EDN | EDN
38 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE03-38A | 1-DCDB2- FDR38:T75 | CRE03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, CC19-01, ZZ99- |  | EDN | EDN
39 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE05-039 | 1-DCDB2- FDR39:T77 | CRE05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, CC19-01, ZZ99- |  | EDN | EDN
39 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE05-39A | 1-DCDB2- FDR39:T77 | CRE05-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-03, CC16-01, CC55-02, CC19-02, ZZ99- |  | EDN | EDN
40 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE07-040 | 1-DCDB2- FDR40:T79 | CRE07-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC55-02, CC19-02, ZZ99- |  | EDN | EDN
40 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE07-40A | 1-DCDB2- FDR40:T79 | CRE07-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC28-02, CC37-02, CC38-01, CC47-01, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
41 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE09-041 | 1-DCDB2- FDR41:T81 | CRE09-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 48 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC38-01, CC47-01, CC48-01, CC49-01, CC50-01, CC51-01, ZZ99- |  | EDN | EDN
41 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE09-41A | 1-DCDB2- FDR41:T81 | CRE09-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 48 | 50 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
42 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE11-042 | 1-DCDB2- FDR42:T83 | CRE11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | 50 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
42 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE11-42A | 1-DCDB2- FDR42:T83 | CRE11-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
43 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE13-043 | 1-DCDB2- FDR43:T85 | CRE13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
43 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE13-43A | 1-DCDB2- FDR43:T85 | CRE13-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
44 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE15-044 | 1-DCDB2- FDR44:T87 | CRE15-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 50 | 42 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
44 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE15-44A | 1-DCDB2- FDR44:T87 | CRE15-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 50 | 42 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
45 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE17-045 | 1-DCDB2- FDR45:T89 | CRE17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | 44 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
45 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE17-45A | 1-DCDB2- FDR45:T89 | CRE17-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | 44 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
46 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE19-046 | 1-DCDB2- FDR46:T91 | CRE19-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 56 | 47 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
46 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE19-46A | 1-DCDB2- FDR46:T91 | CRE19-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 56 | 47 | 0 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
47 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE21-047 | 1-DCDB2- FDR47:T93 | CRE21-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 41 | 01.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
47 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE21-47A | 1-DCDB2- FDR47:T93 | CRE21-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 46 | 41 | 01.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC26-01, CC25-01, ZZ99- |  | EDN | EDN
48 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE23-048 | 1-DCDB2- FDR48:T95 | CRE23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | 43 | 01.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC21-01, CC78-01, ZZ99- |  | EDN | EDN
48 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE23-48A | 1-DCDB2- FDR48:T95 | CRE23-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 47 | 43 | 01.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC21-01, ZZ99- |  | EDN | EDN
49 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE25-049 | 1-DCDB2- FDR49:T97 | CRE25-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 57 | 45 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC21-01, ZZ99- |  | EDN | EDN
49 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE25-49A | 1-DCDB2- FDR49:T97 | CRE25-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 57 | 45 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC64-01, CC21-01, ZZ99- |  | EDN | EDN
50 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE27-050 | 1-DCDB2- FDR50:T99 | CRE27-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 47 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC26-01, CC25-01, CC66-01, CC31-02, ZZ99- |  | EDN | EDN
50 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE27-50A | 1-DCDB2- FDR50:T99 | CRE27-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 47 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC26-01, CC25-01, CC24-01, CC32-01, CC31-02, ZZ99- |  | EDN | EDN
51 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE29-051 | 1-DCDB2- FDR51:T101 | CRE29-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 61 | 49 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC26-01, CC25-01, CC66-01, CC31-02, ZZ99- |  | EDN | EDN
51 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE29-51A | 1-DCDB2- FDR51:T101 | CRE29-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 61 | 49 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, CC67-01, CC30-01, ZZ99- |  | EDN | EDN
52 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE61-052 | 1-DCDB2- FDR52:T103 | CRE61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 63 | 16.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC28-01, CC37-01, CC36-01, CC35-01, CC67-01, CC30-01, ZZ99- |  | EDN | EDN
52 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE61-52A | 1-DCDB2- FDR52:T103 | CRE61-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 43 | 63 | 16.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-01, CC28-01, CC37-01, CC36-01, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
53 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE63-053 | 1-DCDB2- FDR53:T105 | CRE63-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 60 | 16.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC28-01, CC37-01, CC36-01, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
53 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE63-53A | 1-DCDB2- FDR53:T105 | CRE63-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 41 | 60 | 16.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, CC68-01, CC69-01, CC44-02, ZZ99- |  | EDN | EDN
54 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE65-054 | 1-DCDB2- FDR54:T107 | CRE65-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 58 | 16.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-02, CC28-02, CC37-02, CC38-01, CC47-01, CC46-01, CC45-02, ZZ99- |  | EDN | EDN
54 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRE65-54A | 1-DCDB2- FDR54:T107 | CRE65-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 38 | 58 | 16.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC55-02, CC56-02, CC57-02, CC58-01, CC35-01, CC68-01, CC69-01, CC45-02, ZZ99- |  | EDN | EDN
55 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CTE01-055 | 1-DCDB2- FDR55:T109 | CTE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 56 | 16.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-01, CC37-01, CC36-01, CC59-01, CC60-01, CC45-02, ZZ99- |  | EDN | EDN
55 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CTE01-55A | 1-DCDB2- FDR55:T109 | CTE01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 56 | 16.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-01, CC37-02, CC36-01, CC35-01, CC68-01, CC41-01, ZZ99- |  | EDN | EDN
56 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRC01-056 | 1-DCDB2- FDR56:T111 | CRC01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 55 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, CC68-01, CC41-01, ZZ99- |  | EDN | EDN
56 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRC01-56A | 1-DCDB2- FDR56:T111 | CRC01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 55 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC59-01, CC40-02, ZZ99- |  | EDN | EDN
57 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRC03-057 | 1-DCDB2- FDR57:T113 | CRC03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 57 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, CC68-01, CC40-02, ZZ99- |  | EDN | EDN
57 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2CRC03-57A | 1-DCDB2- FDR57:T113 | CRC03-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 30 | 57 | 15.11.2019 | DR0816_0001 |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-03, CC28-02, CC37-02, CC38-01, CC47-01, CC48-01, CC49-01, ZZ99- |  | EDN | EDN
58 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2VMS-058 | 1-DCDB2- FDR58:T115 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 44 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC27-03, CC28-02, CC37-02, CC38-01, CC47-01, CC46-01, ZZ99- |  | EDN | EDN
58 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2VMS-58A | 1-DCDB2- FDR58:T115 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 44 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-03, CC28-02, CC37-02, CC38-01, CC39-01, ZZ99- |  | EDN | EDN
59 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2VMS-059 | 1-DCDB2- FDR59:T117 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 43 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
59 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2VMS-59A | 1-DCDB2- FDR59:T117 | VMS-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 35 | 43 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
60 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2NWPD-0106 | 1-DCDB2- FDR60:T119 | NWPD01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 42 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | SITE ROUTING |  | EDN | EDN
60 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2NWPD-106A | 1-DCDB2- FDR60:T119 | NWPD01-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 42 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, ZZ99- |  | EDN | EDN
61 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2NWPD-0206 | 1-DCDB2- FDR61:T121 | NWPD02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 41 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-02, CC27-02, CC28-02, CC37-02, CC36-01, CC35-01, ZZ99- |  | EDN | EDN
61 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2NWPD-206A | 1-DCDB2- FDR61:T121 | NWPD02-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 51 | 41 | 18.11.2019 | NA |  |  | POWER SUPPLY |  | ZZ99- , CC18-01, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, ZZ99- |  | EDN | EDN
62 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2UCD-062 | 1-DCDB2- FDR62:T123 | UCD-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 68 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC18-02, CC16-01, CC15-01, CC64-01, CC65-01, CC24-01, CC32-01, CC33-02, CC34-01, ZZ99- |  | EDN | EDN
62 | DCDB2 | D01Q070 | 10.4.02 | 1DCDB2UCD-62A | 1-DCDB2- FDR62:T123 | UCD-X01:P | 01C X 070 XLPE-Al FRLS ( 1.1 kV ) | 68 | [5 empty] | POWER SUPPLY |  | CC18-01, CC27-03, CC26-01, CC25-01, CC66-01, CC67-01, CC34-01, CC42-02, CC85-01, CC86-02, CC88-01, CC92-01, ZZ99- |  | EDN | EDN
63 | DCDB2 | D02G120 | 10.4.10 | 1EARTH2(C&I)-DCDB2-01 | 1-DCDB2- EARTHBUS | ELECTRONIC EARTHPIT CD-BAY | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 150 | 42 | 20.11.2019 | DR0345_1535 |  |  | EARTHING |  | Site Route |  | EDN | EDN
64 | DCDB2 | D02G120 | 10.4.10 | 1EARTH2(C&I)-DCDB2-02 | 1-DCDB2- EARTHBUS | ELECTRONIC EARTHPIT CD-BAY | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 150 | 42 | 20.11.2019 | DR0345_1535 |  |  | EARTHING |  | Site Route |  | EDN | EDN
1 | LDB | D03Q050 | 10.4.14 | 1UA-103n-P01 | 1UA FDR-01 | 103n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall EL. 9.0M, Col1 & Row B |  |  |  | PEM | PEM
2 | LDB | D03Q050 | 10.4.14 | 1UA-107n-P02 | 1UA FDR-02 | 107n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall EL. 15.5M, Col1 & Row B |  |  |  | PEM | PEM
3 | LDB | D03Q050 | 10.4.14 | 1UA-144n-P03 | 1UA FDR-03 | 144n.LP-A (6) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall EL. 15.5M, Col1 & Row B |  |  |  | PEM | PEM
4 | LDB | D03Q050 | 10.4.14 | 1UA-101n-P04 | 1UA FDR-04 | 101n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall Gr. Floor Col 2 & Row B |  |  |  | PEM | PEM
5 | LDB | D03Q050 | 10.4.14 | 1UA-102n-P05 | 1UA FDR-05 | 102n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall Gr. Floor Col 1 & Row B |  |  |  | PEM | PEM
6 | LDB | D03Q050 | 10.4.14 | 1UA-141n-P06 | 1UA FDR-06 | 141n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM CL 6 & ROW A, Trf Yard |  |  |  | PEM | PEM
7 | LDB | D03Q050 | 10.4.14 | 1UA-110n-P07 | 1UA FDR-07 | 110n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Compressor Building CL 6 & ROW B |  |  |  | PEM | PEM
8 | LDB | D03Q050 | 10.4.14 | 1UA-145n-P08 | 1UA FDR-08 | 145n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM AC Plant Area, CL 8 & ROW E |  |  |  | PEM | PEM
9 | LDB | D03Q050 | 10.4.14 | 1UA-145n-P09 | 1UA FDR-09 | 145n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Boiler, CL S 17 EL 56.85M |  |  |  | PEM | PEM
10 | LDB | D3HQ025 | 10.4.18 | 1UF-101e-P01 | 1UF FDR-01 | 101e.LP-A (12) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM TG Hall Gr. Floor Col 8 & Row B |  |  |  | PEM | PEM
11 | LDB | D3HQ025 | 10.4.18 | 1UF-102e-P02 | 1UF FDR-02 | 102e.LP-A (12) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM TG Hall EL. 9.0M, Col8 & Row B |  |  |  | PEM | PEM
12 | LDB | D03Q050 | 10.4.14 | 1UF-103e-P03 | 1UF FDR-03 | 103e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM TG Hall EL. 15.5M, Col1 & Row B |  |  |  | PEM | PEM
13 | LDB | D03Q050 | 10.4.14 | 1UF-111e-P04 | 1UF FDR-04 | 111e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Bioler, Col S14R EL 10.0M |  |  |  | PEM | PEM
14 | LDB | D03Q050 | 10.4.14 | 1UF-112e-P05 | 1UF FDR-05 | 112e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, Col S10 EL 23.3M |  |  |  | PEM | PEM
15 | LDB | D03Q050 | 10.4.14 | 1UF-113e-P06 | 1UF FDR-06 | 113e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, Col S19 EL 34.0M |  |  |  | PEM | PEM
16 | LDB | D3HQ025 | 10.4.18 | 1UH-101d-P01 | 1UH FDR-01 | 101d.LP-D (6) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall Gr. Floor, Col 8 & Row B |  |  |  | PEM | PEM
17 | LDB | D3HQ025 | 10.4.18 | 1UH-102d-P02 | 1UH FDR-02 | 102d.LP-D (6) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall EL. 9.0M, Col 8 & Row B |  |  |  | PEM | PEM
18 | LDB | D03Q050 | 10.4.14 | 1UH-103d-P03 | 1UH FDR-03 | 103d.LP-D (6) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM TG Hall EL. 15.5M, Col1 & Row B |  |  |  | PEM | PEM
19 | LDB | D03Q050 | 10.4.14 | 1UH-114d-P04 | 1UH FDR-04 | 114d.LP-D (6) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Boiler, CL S 17 EL 44.75M |  |  |  | PEM | PEM
20 | LDB | D03Q050 | 10.4.14 | 1UH-115d-P05 | 1UH FDR-05 | 115d.LP-D (6) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Boiler, CL S 17 EL 53.5M |  |  |  | PEM | PEM
21 | LDB | D3HQ025 | 10.4.18 | 1UC-105n-P01 | 1UC FDR-01 | 105n.LP-A (18) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM LV Swgr Room, Col 8 & Row B |  |  |  | PEM | PEM
22 | LDB | D03Q050 | 10.4.14 | 1UC-129n-P02 | 1UC FDR-02 | 129n.LP-A (12 | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Col 9 & Row C (CCR/EER Room) |  |  |  | PEM | PEM
23 | LDB | D03Q050 | 10.4.14 | 1UC-117n-P03 | 1UC FDR-03 | 117n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 17 EL 37.35M |  |  |  | PEM | PEM
24 | LDB | D03Q050 | 10.4.14 | 1UC-118n-P04 | 1UC FDR-04 | 118n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 17 EL 44.75M |  |  |  | PEM | PEM
25 | LDB | D03Q050 | 10.4.14 | 1UC-119n-P05 | 1UC FDR-05 | 119n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 17 EL 47.3M |  |  |  | PEM | PEM
26 | LDB | D03Q050 | 10.4.14 | 1UC-120n-P06 | 1UC FDR-06 | 120n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 17 EL 53.5M |  |  |  | PEM | PEM
27 | LDB | D3HN050 | 10.3.02 | 1UC-High-P07 | 1UC FDR-07 | High Mast | 3.5C X 050 XLPE-Al FRLS A ( 1.1 kV ) | 250 | [5 empty] | TGB LV SWGR ROOM N - 177 & E-1474 |  |  |  | PEM | PEM
28 | LDB | D03Q050 | 10.4.14 | 0UA-133n-P01 | 0UA FDR-01 | 133n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | CT SWGR ROOM Col 4 & Row B in CWPH |  |  |  | PEM | PEM
29 | LDB | D3HQ050 | 10.4.19 | 0UA-135n-P02 | 0UA FDR-02 | 135n.SLP-S (6) | 3.5C X 050 XLPE-Al FRLS A ( 1.1 kV ) | [6 empty] | CT SWGR ROOM Near CWPH |  |  |  | PEM | PEM
30 | LDB | D3HQ025 | 10.4.18 | 0UA-109n-P03 | 0UA FDR-03 | 109n.LP-A (12) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | CT SWGR ROOM CT SwGR Room Col 1 & Row A |  |  |  | PEM | PEM
31 | LDB | D03Q050 | 10.4.14 | 0UA-142n-P04 | 0UA FDR-04 | 142n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | CT SWGR ROOM Chlorination Building Col 4 & Row C |  |  |  | PEM | PEM
32 | LDB | D3HN050 | 10.3.02 | 0UA-High-P05 | 0UA FDR-05 | High Mast | 3.5C X 050 XLPE-Al FRLS A ( 1.1 kV ) | 250 | [5 empty] | CT SWGR ROOM N - 231 & E-1318 |  |  |  | PEM | PEM
33 | LDB | D03Q050 | 10.4.14 | 0UB-134n-P01 | 0UB FDR-01 | 134n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ETP SWGR Room ETP SWGR Room Col 2 & Row A |  |  |  | PEM | PEM
34 | LDB | D3HQ025 | 10.4.18 | 1UD-130n-P01 | 1UD FDR-01 | 130n.LP-A (12) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Col 10 & Row C (CCR/EER Room) |  |  |  | PEM | PEM
35 | LDB | D03Q050 | 10.4.14 | 1UD-111n-P02 | 1UD FDR-02 | 111n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S14L EL 7M |  |  |  | PEM | PEM
36 | LDB | D03Q050 | 10.4.14 | 1UD-112n-P03 | 1UD FDR-03 | 112n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S14L EL 10M |  |  |  | PEM | PEM
37 | LDB | D03Q050 | 10.4.14 | 1UD-113n-P04 | 1UD FDR-04 | 113n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S18 EL 16.6M |  |  |  | PEM | PEM
38 | LDB | D03Q050 | 10.4.14 | 1UD-108n-P05 | 1UD FDR-05 | 108n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM TG Hall EL. 21.0m, Col5 & Row B |  |  |  | PEM | PEM
39 | LDB | D03Q050 | 10.4.14 | 1UD-106n-P06 | 1UD FDR-06 | 106n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM TG Hall EL. 15.5M, Col1 & Row B |  |  |  | PEM | PEM
40 | LDB | D3HQ025 | 10.4.18 | 1UE-125n-P01 | 1UE FDR-01 | 125n.LP-A (18) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM ESP SWGR Room, Col 1 & Row B (EL 3.7M) |  |  |  | PEM | PEM
41 | LDB | D03Q050 | 10.4.14 | 1UE-126n-P02 | 1UE FDR-02 | 126n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM CL ESP D EL 3.5M |  |  |  | PEM | PEM
42 | LDB | D03Q050 | 10.4.14 | 1UE-127n-P03 | 1UE FDR-03 | 127n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM CL ESP A-B EL 26.05M |  |  |  | PEM | PEM
43 | LDB | D03Q050 | 10.4.14 | 1UE-128n-P04 | 1UE FDR-04 | 128n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM CL ESP A-B EL 26.05M |  |  |  | PEM | PEM
44 | LDB | D3HQ050 | 10.4.19 | 1UE-136n-P05 | 1UE FDR-05 | 136n.SLP-S (6) | 3.5C X 050 XLPE-Al FRLS A ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM Near ESP Control Room |  |  |  | PEM | PEM
45 | LDB | D3HN050 | 10.3.02 | 1UE-High-P06 | 1UE FDR-06 | High Mast | 3.5C X 050 XLPE-Al FRLS A ( 1.1 kV ) | 250 | [5 empty] | ESP CONTROL ROOM N - 28 & E-1338 |  |  |  | PEM | PEM
46 | LDB | D3HQ025 | 10.4.18 | 1UG-104e-P01 | 1UG FDR-01 | 104e.LP-A (6) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM ESP SWGR Room Col 1 & Row B (EL 3.7M) |  |  |  | PEM | PEM
47 | LDB | D03Q050 | 10.4.14 | 1UG-105e-P02 | 1UG FDR-02 | 105e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM CL ESP D EL 3.5M |  |  |  | PEM | PEM
48 | LDB | D03Q050 | 10.4.14 | 1UG-110e-P03 | 1UG FDR-03 | 110e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM Boiler, CL SL16R at EL 0.0M |  |  |  | PEM | PEM
49 | LDB | D03Q050 | 10.4.14 | 1UG-114e-P04 | 1UG FDR-04 | 114e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM Boiler, Col S17 EL 44.75M |  |  |  | PEM | PEM
50 | LDB | D03Q050 | 10.4.14 | 1UG-115e-P05 | 1UG FDR-05 | 115e.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ESP CONTROL ROOM Boiler, Col S17 EL 53.5M |  |  |  | PEM | PEM
51 | LDB | D02Q025 | 10.4.07 | 1UJ-105d-P01 | 1UJ FDR-01 | 105d.LP-D (6) | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM ESP B EL 3.5M |  |  |  | PEM | PEM
52 | LDB | D02Q025 | 10.4.07 | 1UJ-110d-P02 | 1UJ FDR-02 | 110d.LP-D (6) | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 25 EL 0.0M |  |  |  | PEM | PEM
53 | LDB | D02Q025 | 10.4.07 | 1UJ-111d-P03 | 1UJ FDR-03 | 111d.LP-D (6) | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 22 EL 10.0M |  |  |  | PEM | PEM
54 | LDB | D02Q025 | 10.4.07 | 1UJ-112d-P04 | 1UJ FDR-04 | 112d.LP-D (6) | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 17 EL 23.3M |  |  |  | PEM | PEM
55 | LDB | D02Q025 | 10.4.07 | 1UJ-113d-P05 | 1UJ FDR-05 | 113d.LP-D (6) | 02C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | TGB LV SWGR ROOM Boiler, CL S 19 EL 34M |  |  |  | PEM | PEM
56 | LDB | D03Q050 | 10.4.14 | 1UB-114n-P01 | 1UB FDR-01 | 114n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Boiler, CL S 19 EL 20.3M |  |  |  | PEM | PEM
57 | LDB | D03Q050 | 10.4.14 | 1UB-115n-P02 | 1UB FDR-02 | 115n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Boiler, CL S 10L EL 23.3M |  |  |  | PEM | PEM
58 | LDB | D03Q050 | 10.4.14 | 1UB-116n-P03 | 1UB FDR-03 | 116n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Boiler, CL S 19 EL 30.4M |  |  |  | PEM | PEM
59 | LDB | D03Q050 | 10.4.14 | 1UB-137n-P04 | 1UB FDR-04 | 137n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM Boiler, CL SL16 at EL 0.0M |  |  |  | PEM | PEM
60 | LDB | D03Q050 | 10.4.14 | 1UB-143n-P05 | 1UB FDR-05 | 143n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | TGB MV SWGR ROOM ID & PA Fan Area, NEAR CL U15 |  |  |  | PEM | PEM
61 | LDB | D3HQ050 | 10.4.19 | 0UC-137n-P01 | 0UC FDR-01 | 137n.SLP-S (6) | 3.5C X 050 XLPE-Al FRLS A ( 1.1 kV ) | [6 empty] | PTP MCC ROOM NEAR FIRE WATER P/H |  |  |  | PEM | PEM
62 | LDB | D03Q050 | 10.4.14 | 0UC-138n-P02 | 0UC FDR-02 | 138n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | PTP MCC ROOM Fire Water PH Col 4 & Row A |  |  |  | PEM | PEM
63 | LDB | D3HQ025 | 10.4.18 | 0UC-140n-P03 | 0UC FDR-03 | 140n.LP-A (12) | 3.5C X 025 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | PTP MCC ROOM PTP MCC Room Col 4 & Row A |  |  |  | PEM | PEM
64 | LDB | D03Q050 | 10.4.14 | 0UC-139n-P04 | 0UC FDR-04 | 139n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | PTP MCC ROOM Chemical Bldg Col 2 & Row A |  |  |  | PEM | PEM
65 | LDB | D3HN050 | 10.3.02 | 0UC-High-P05 | 0UC FDR-05 | High Mast | 3.5C X 050 XLPE-Al FRLS A ( 1.1 kV ) | 250 | [5 empty] | PTP MCC ROOM N - 197 & E-1073 |  |  |  | PEM | PEM
66 | LDB | D03Q050 | 10.4.14 | 1UD-121n-P01 | 1UD FDR-01 | 121n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ADMIN BUILDING MCC Room Admin Bldg Col 3A & Row-E (G.F.) |  |  |  | PEM | PEM
67 | LDB | D03Q050 | 10.4.14 | 1UD-123n-P02 | 1UD FDR-02 | 123n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ADMIN BUILDING MCC Room Admin Bldg Col 3A & Row-E (F.F.) |  |  |  | PEM | PEM
68 | LDB | D03Q050 | 10.4.14 | 1UD-122n-P03 | 1UD FDR-03 | 122n.LP-A (6) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ADMIN BUILDING MCC Room Admin Bldg Col 3A & Row-E (G.F.) |  |  |  | PEM | PEM
69 | LDB | D03Q050 | 10.4.14 | 1UD-124n-P04 | 1UD FDR-04 | 124n.LP-A (6) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ADMIN BUILDING MCC Room Admin Bldg Col 3A & Row-E (F.F.) |  |  |  | PEM | PEM
70 | LDB | D03Q050 | 10.4.14 | 1UD-131n-P05 | 1UD FDR-05 | 131n.LP-A (18) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ADMIN BUILDING MCC Room Admin Bldg Col 4 & Row F (G.F.) |  |  |  | PEM | PEM
71 | LDB | D03Q050 | 10.4.14 | 1UD-132n-P06 | 1UD FDR-06 | 132n.LP-A (12) | 3.5C X 050 XLPE-Al FRLS UA ( 1.1 kV ) | [6 empty] | ADMIN BUILDING MCC Room Admin Bldg Col 4 & Row F (F.F.) |  |  |  | PEM | PEM
1 | ACDB1 | D02G120 | 10.4.10 | 1EARTH2(C&I)-ACDB1-01 | ACDB-01 | (C&I) EARTHPIT-01 | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 44 | 44 | 20.11.2019 | DR0345_1535 |  |  | NA |  |  |  | EDN | EDN
1 | ACDB2 | D02G120 | 10.4.10 | 1EARTH2(C&I)-ACDB2-01 | ACDB-02 | (C&I) EARTHPIT-02 | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 41 | 41 | 20.11.2019 | DR0345_1535 |  |  | NA |  |  |  | EDN | EDN
1 | ACDB1 | D02G120 | 10.4.10 | 1ACDB01-DRB01-P01 | ACDB-01 | (C&I) DISCHARGE BANK | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 82 | 82 | 04.03.20 | DR0345_1535 |  |  | NA |  |  |  | EDN | EDN
1 | ACDB2 | D02G120 | 10.4.10 | 1ACDB02-DRB01-P02 | ACDB-01 | (C&I) DISCHARGE BANK | 02C X 120 XLPE-Al FRLS RPT ( 1.1 kV ) | 73 | 73 | 09.03.20 | DR0345_1535 |  |  | NA |  |  |  | EDN | EDN
1 | NA | D3HN025 | 10.3.01 | NO SCHEDULE | NA | NA | 3.5C X 25 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | NA | PEM LT ARM CABLE 5DRUM |  |  | 0 | 0
1 | NA | D3HN050 | 10.3.02 | NO SCHEDULE | NA | NA | 3.5C X 50 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | NA | PEM LT ARM CABLE 1DRUM |  |  | 0 | 0
1 | NA | D03J2.5 | 10.3.03 | NO SCHEDULE | NA | NA | 03C X 2.5 XLPE-CU FRLS ( 1.1 kV ) | [6 empty] | NA | PEM LT ARM CABLE 1DRUM |  |  | 0 | 0
1 | NA | D02Q050 | 10.4.08 | NO SCHEDULE | NA | NA | 02C X 50 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | NA | PEM LT CABLE 1DRUM |  |  | 0 | 0
1 | NA | D03C035 | 10.4.13 | NO SCHEDULE | NA | NA | 03C X 035 XLPE-Al FRLS ( 1.1 kV ) | [6 empty] | NA | RPT LT CABLE 1DRUM |  |  | 0 | 0
1 | NA | D02L1.5 | 10.4.23 | NO SCHEDULE | NA | NA | 02C X 1.5 XLPE-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | NO CABLE |  |  | 0 | 0
1 | NA | D03L1.5 | 10.4.25 | NO SCHEDULE | NA | NA | 03C X 1.5 XLPE-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | NO CABLE |  |  | 0 | 0
1 | NA | D03L2.5 | 10.4.26 | NO SCHEDULE | NA | NA | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | PEM LT ARM CABLE 1DRUM |  |  | 0 | 0
1 | NA | D02W1.5 | 10.4.27 | NO SCHEDULE | NA | NA | 04C X 1.5 PVC-Cu TYPE-F ( 1.1 kV ) | [6 empty] | NA | RPT INST CABLE 6DRUM |  |  | 0 | 0
1 | NA | D10L2.5 | 10.4.28 | NO SCHEDULE | NA | NA | 10C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | TRY INST CABLE 1DRUM |  |  | 0 | 0
1 | NA | D10C2.5 | 10.5.11 | NO SCHEDULE | NA | NA | 10C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | TRY INST CABLE 1DRUM |  |  | 0 | 0
1 | NA | D02N2.5 | 10.6.01 | NO SCHEDULE | NA | NA | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | D03N2.5 | 10.6.02 | NO SCHEDULE | NA | NA | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | D05N2.5 | 10.6.03 | NO SCHEDULE | NA | NA | 05C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | D05N006 | 10.6.04 | NO SCHEDULE | NA | NA | 05C X 6.0 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | D07N2.5 | 10.6.05 | NO SCHEDULE | NA | NA | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | D12N2.5 | 10.6.06 | NO SCHEDULE | NA | NA | 12C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | D14N2.5 | 10.6.07 | NO SCHEDULE | NA | NA | 14C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | D16N2.5 | 10.6.08 | NO SCHEDULE | NA | NA | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA | LT ARM CABLE |  |  | 0 | 0
1 | NA | E02V0.5 | 10.7.01 | NO SCHEDULE | NA | NA | 02P X 0.5 Paired Screened(O) ( 225 V ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | E06V0.5 | 10.7.03 | NO SCHEDULE | NA | NA | 06P X 0.5 Paired Screened(O) ( 225 V ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | E12V0.5 | 10.7.05 | NO SCHEDULE | NA | NA | 12P X 0.5 Paired Screened(O) ( 225 V ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | E16V0.5 | 10.7.06 | NO SCHEDULE | NA | NA | 16P X 0.5 Paired Screened(O) ( 225 V ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | E12W0.5 | 10.8.04 | NO SCHEDULE | NA | NA | 12P X 0.5 Paired Screened(I) ( 225 V ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | D02C2.5 | 10.5.02 | NO SCHEDULE | NA | NA | 02C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | D03C16 | 10.5.05 | NO SCHEDULE | NA | NA | 03C X 16 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | D10C1.5 | 10.5.10 | NO SCHEDULE | NA | NA | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | D12C2.5 | 10.5.13 | NO SCHEDULE | NA | NA | 10C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | F04-0.5 | 10.9.01 | NO SCHEDULE | NA | NA | 04P X 0.5 OFC CABLE ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | F12-0.5 | 10.9.02 | NO SCHEDULE | NA | NA | 12P X 0.5 OFC CABLE ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | D16C2.5 | NA | NO SCHEDULE | NA | NA | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | D19C1.5 | NA | NO SCHEDULE | NA | NA | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA | D19C1.5 | NA | NO SCHEDULE | NA | NA | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | [6 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0
1 | NA |  |  | NO SCHEDULE | NA | NA | [7 empty] | NA |  |  |  | 0 | 0

## SummerySheetElec
[7 empty] | CABLE LENGTH RECONCILIATION | [5 empty] | CABLE RUN QUANTITY |  | UNIT WISE GLAND QUANTITY
CABLE CODE | PTX BOQ | CABLE SIZE DESCRIPTION | CABLE DIA | RATED AMPS | GLAND | QTY | SUPPLY | SCHEDULE LENGTH | PTX SCOPE | ACTUAL LENGTH | % COMPLETED | BALANCE STOCK % | TOTAL RUN CABLE | TOTAL RUN LAYED | EPD | PEM | BPL | JHS | RPT | HWR | HYD | TRY | EDN | ISG
B01Q400 | 10.1.01 | 01Cx400Sqmm AL XLPE-FRLS UNARM CABLE HT | 42 mm | 380 A | CBW09 | 120 | 26981 | 22752 | 32000 | 585 | 2.571% | 97.8318 | 60 | 12 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B03Q150 | 10.1.02 | 03Cx150Sqmm AL XLPE-FRLS UNARM CABLE HT | 61 mm | 210 A | CBW012 | 94 | 13928 | 9045 | 13000 | 1194 | 13.2% | 91.4273 | 47 | 16 | 0 | 2 | 76 | 14 | 0 | 0 | 0 | 0 | 2 | 0
B03Q240 | 10.1.03 | 03Cx240Sqmm AL XLPE-FRLS UNARM CABLE HT | 72 mm | 275 A | CBW013 | 44 | 2949 | 2749 | 5000 | 457 | 16.62% | 84.5032 | 22 | 8 | 0 | 0 | 38 | 2 | 0 | 0 | 0 | 0 | 4 | 0
A03Q120 | 10.2.01 | 03Cx120Sqmm AL XLPE-FRLS UNARM CABLE HT | 87 mm | 215 A | CBW015 | 4 | 1448 | 1400 | 1500 | 0 | 0% | 100 | 2 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D3HN025 | 10.3.01 | 3.5Cx025Sqmm AL XLPE-FRLS ARM CABLE | 23 mm | 94 A | CBW04 | 2 | 8867 | 0 | 8000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D3HN050 | 10.3.02 | 3.5Cx050Sqmm AL XLPE-FRLS ARM CABLE | 29 mm | 133 A | CBW06 | 10 | 978 | 1000 | 1000 | 0 | 0% | 100 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03J2.5 | 10.3.03 | 03Cx2.5Sqmm CU XLPE-FRLS ARM P CABLE | 14 mm | 24 A | CBW01S | 2 | 5987 | 0 | 8000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D01Q035 | 10.4.01 | 01Cx035Sqmm AL XLPE-FRLS UNARM CABLE | 13 mm | 114 A | CBW01S | 284 | 5962 | 3969 | 8000 | 2984 | 75.18% | 49.9497 | 142 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0
D01Q070 | 10.4.02 | 01Cx070Sqmm AL XLPE-FRLS UNARM CABLE | 16 mm | 166 A | CBW01S | 496 | 9893 | 9662 | 14000 | 8910 | 92.22% | 9.9363 | 248 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496 | 0
D01Q120 | 10.4.03 | 01Cx120Sqmm AL XLPE-FRLS UNARM CABLE | 19 mm | 225 A | CBW03 | 0 | 2000 | 0 | 2000 | 0 | 0% | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D01Q400 | 10.4.04 | 01Cx400Sqmm AL XLPE-FRLS UNARM CABLE | 33 mm | 431 A | CBW07 | 252 | 9631 | 8564 | 13500 | 7681 | 89.69% | 20.2471 | 126 | 108 | 234 | 14 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0
D01Q630 | 10.4.05 | 01Cx630Sqmm AL XLPE-FRLS UNARM CABLE | 40 mm | 557 A | CBW09 | 168 | 12741 | 10213 | 18000 | 1191 | 11.66% | 90.6522 | 84 | 30 | 92 | 20 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 18
D02Q010 | 10.4.06 | 02Cx010Sqmm AL XLPE-FRLS UNARM CABLE | 16 mm | 59 A | CBW01 | 284 | 8876 | 8028 | 6000 | 1387 | 17.28% | 84.3736 | 142 | 24 | 160 | 91 | 13 | 3 | 0 | 0 | 0 | 0 | 17 | 0
D02Q025 | 10.4.07 | 02Cx025Sqmm AL XLPE-FRLS UNARM CABLE | 17 mm | 74 A | CBW02 | 142 | 7930 | 6523 | 8000 | 414 | 6.347% | 94.7793 | 71 | 8 | 76 | 36 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D02Q050 | 10.4.08 | 02Cx050Sqmm AL XLPE-FRLS UNARM CABLE | 21 mm | 156 A | CBW03 | 2 | 999 | 0 | 1000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D02Q095 | 10.4.09 | 02Cx095Sqmm AL XLPE-FRLS UNARM CABLE | 27 mm | 231 A | CBW05 | 98 | 5916 | 5482 | 6000 | 342 | 6.239% | 94.2191 | 49 | 4 | 80 | 12 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 0
D02G120 | 10.4.10 | 02Cx120Sqmm AL PVC-FRLS UNARM CABLE | 29 mm | 262 A | CBW06 | 240 | 8008 | 3650 | 8000 | 2722 | 74.58% | 66.009 | 120 | 64 | 0 | 0 | 0 | 168 | 56 | 0 | 0 | 0 | 16 | 0
D03Q010 | 10.4.11 | 03Cx010Sqmm AL XLPE-FRLS UNARM CABLE | 17 mm | 57 A | CBW01 | 328 | 25842 | 21030 | 36100 | 2490 | 11.84% | 90.3645 | 164 | 20 | 132 | 98 | 0 | 0 | 71 | 7 | 20 | 0 | 0 | 0
D03Q025 | 10.4.12 | 03Cx025Sqmm AL XLPE-FRLS UNARM CABLE | 20 mm | 94 A | CBW03 | 160 | 16849 | 15121 | 14000 | 585 | 3.869% | 96.528 | 80 | 9 | 80 | 55 | 0 | 0 | 10 | 2 | 13 | 0 | 0 | 0
D03Q035 | 10.4.13 | 03Cx035Sqmm AL XLPE-FRLS UNARM CABLE | 22 mm | 113 A | CBW03 | 16 | 794 | 520 | 800 | 0 | 0% | 100 | 8 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0
D03Q050 | 10.4.14 | 03Cx050Sqmm AL XLPE-FRLS UNARM CABLE | 25 mm | 133 A | CBW05 | 140 | 2974 | 3260 | 2000 | 204 | 6.258% | 93.1406 | 70 | 4 | 19 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0
D03Q095 | 10.4.15 | 03Cx095Sqmm AL XLPE-FRLS UNARM CABLE | 34 mm | 190 A | CBW07 | 66 | 5897 | 3283 | 8000 | 307 | 9.351% | 94.794 | 33 | 3 | 31 | 30 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 2
D03Q150 | 10.4.16 | 03Cx150Sqmm AL XLPE-FRLS UNARM CABLE | 39 mm | 249 A | CBW08 | 8 | 1468 | 1032 | 750 | 0 | 0% | 100 | 4 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03Q240 | 10.4.17 | 03Cx240Sqmm AL XLPE-FRLS UNARM CABLE | 49 mm | 326 A | CBW010 | 68 | 8121 | 5868 | 6750 | 128 | 2.181% | 98.4238 | 34 | 2 | 38 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D3HQ025 | 10.4.18 | 3.5Cx025Sqmm AL XLPE-FRLS UNAR CABLE | 22 mm | 94 A | CBW03 | 380 | 3975 | 16908 | 6000 | 408 | 2.413% | 89.7358 | 190 | 6 | 258 | 94 | 8 | 6 | 0 | 0 | 0 | 3 | 10 | 0
D3HQ050 | 10.4.19 | 3.5Cx050Sqmm AL XLPE-FRLS UNAR CABLE | 28 mm | 133 A | CBW05 | 36 | 7916 | 1747 | 12000 | 0 | 0% | 100 | 18 | 0 | 15 | 19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D3HQ095 | 10.4.20 | 3.5Cx095Sqmm AL XLPE-FRLS UNAR CABLE | 35 mm | 196 A | CBW08 | 16 | 6834 | 1136 | 10000 | 126 | 11.09% | 98.1563 | 8 | 1 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D3HQ185 | 10.4.21 | 3.5Cx185Sqmm AL XLPE-FRLS UNAR CABLE | 47 mm | 282 A | CBW010 | 38 | 2971 | 3557 | 750 | 709 | 19.93% | 76.136 | 19 | 11 | 19 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0
D04Q010 | 10.4.22 | 04Cx010Sqmm AL XLPE-FRLS UNARM CABLE | 19 mm | 57 A | CBW02 | 270 | 13933 | 11968 | 15000 | 0 | 0% | 100 | 135 | 0 | 135 | 98 | 0 | 0 | 8 | 0 | 0 | 10 | 17 | 0
D02L1.5 | 10.4.23 | 02Cx1.5Sqmm CU XLPE-FRLS UNARM CABLE | 12 mm | 13 A | CBW01SS | 2 | 0 | 0 | 140 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D02L2.5 | 10.4.24 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM CABLE | 14 mm | 25 A | CBW01S | 784 | 55130 | 24220 | 68500 | 1710 | 7.06% | 96.8982 | 392 | 20 | 191 | 81 | 81 | 47 | 343 | 6 | 0 | 6 | 24 | 2
D03L1.5 | 10.4.25 | 03Cx1.5Sqmm CU XLPE-FRLS UNARM CABLE | 12 mm | 13 A | CBW01SS | 2 | 0 | 0 | 9200 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03L2.5 | 10.4.26 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM CABLE | 14 mm | 24 A | CBW01S | 1380 | 71192 | 78238 | 95300 | 2501 | 3.197% | 96.487 | 690 | 27 | 528 | 390 | 24 | 0 | 4 | 18 | 99 | 310 | 3 | 2
D02W1.5 | 10.4.27 | 04Cx1.5Sqmm ATC TYPE-F UNARM R CABLE | 15 mm | 13 A | CBW01S | 58 | 5496 | 1400 | 5500 | 0 | 0% | 100 | 29 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0
D10L2.5 | 10.4.28 | 10Cx2.5Sqmm CU XLPE-FRLS UNARM CABLE | 17 mm | 18 A | CBW01 | 2 | 0 | 0 | 8200 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D02C1.5 | 10.5.01 | 02Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 13 mm | 20 A | CBW01S | 798 | 61485 | 55129 | 50000 | 2031 | 3.684% | 96.6968 | 399 | 22 | 658 | 3 | 94 | 2 | 0 | 1 | 0 | 0 | 22 | 4
D02C2.5 | 10.5.02 | 02Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 27 A | CBW01S | 2 | 1482 | 0 | 3000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03C1.5 | 10.5.03 | 03Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 13 mm | 17 A | CBW01S | 504 | 35493 | 6473 | 2500 | 0 | 0% | 100 | 252 | 0 | 0 | 0 | 6 | 56 | 408 | 0 | 0 | 0 | 34 | 0
D03C2.5 | 10.5.04 | 03Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 24 A | CBW01S | 136 | 43391 | 1620 | 18500 | 0 | 0% | 100 | 68 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 16 | 0 | 0
D03C16 | 10.5.05 | 03Cx16Sqmm CU PVC-FRLS UNARM CABLE | 19 mm | 24 A | CBW02 | 2 | 0 | 0 | 1500 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D05C1.5 | 10.5.06 | 05Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 13 mm | 10 A | CBW01S | 200 | 14908 | 18502 | 15000 | 1092 | 5.902% | 92.6751 | 100 | 15 | 47 | 3 | 94 | 26 | 0 | 0 | 0 | 0 | 20 | 4
D05C2.5 | 10.5.07 | 05Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 13 A | CBW01S | 160 | 12607 | 10585 | 7000 | 100 | 0.9447% | 99.2068 | 80 | 1 | 4 | 0 | 74 | 8 | 0 | 0 | 0 | 10 | 27 | 4
D07C1.5 | 10.5.08 | 07Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 10 A | CBW01S | 64 | 11973 | 4788 | 12000 | 0 | 0% | 100 | 32 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D07C2.5 | 10.5.09 | 07Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 16 mm | 13 A | CBW01S | 2 | 2000 | 104 | 1000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0
D10C1.5 | 10.5.10 | 10Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 17 mm | 10 A | CBW01 | 138 | 8070 | 2400 | 8200 | 318 | 13.25% | 96.0595 | 69 | 3 | 0 | 0 | 0 | 56 | 80 | 0 | 0 | 0 | 0 | 0
D10C2.5 | 10.5.11 | 10Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 19 mm | 13 A | CBW02 | 2 | 499 | 0 | 250 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D12C1.5 | 10.5.12 | 12Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 18 mm | 10 A | CBW02 | 12 | 14909 | 592 | 15000 | 0 | 0% | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0
D12C2.5 | 10.5.13 | 12Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 20 mm | 13 A | CBW02 | 2 | 4942 | 0 | 5000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D16C2.5 | 10.5.14 | 16Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 22 mm | 13 A | CBW03 | 2 | 7841 | 0 | 4000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D19C1.5 | 10.5.15 | 19Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 20 mm | 10 A | CBW03 | 4 | 4981 | 0 | 2000 | 0 | 0% | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E02V0.5 | 10.7.01 | 02Px0.5Sqmm ATC TYPE-G UNAR CABLE | 8 mm | 5 A | CBW01SS | 2 | 16297 | 0 | 1000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E04V0.5 | 10.7.02 | 04Px0.5Sqmm ATC TYPE-G UNAR CABLE | 12 mm | 5 A | CBW01SS | 1054 | 171965 | 46324 | 5000 | 14465 | 31.23% | 91.5884 | 527 | 200 | 194 | 9 | 160 | 16 | 0 | 9 | 0 | 81 | 501 | 6
E06V0.5 | 10.7.03 | 06Px0.5Sqmm ATC TYPE-G UNAR CABLE | 13 mm | 6 A | CBW01SS | 2 | 0 | 0 | 10000 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E08V0.5 | 10.7.04 | 08Px0.5Sqmm ATC TYPE-G UNAR CABLE | 15 mm | 7 A | CBW01S | 18 | 45535 | 1034 | 1000 | 0 | 0% | 100 | 9 | 0 | 0 | 1 | 4 | 2 | 0 | 0 | 0 | 0 | 11 | 0
E12V0.5 | 10.7.05 | 12Px0.5Sqmm ATC TYPE-G UNAR CABLE | 19 mm | 8 A | CBW02 | 2 | 17958 | 0 | 15000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E16V0.5 | 10.7.06 | 16Px0.5Sqmm ATC TYPE-G UNAR CABLE | 20 mm | 9 A | CBW02 | 2 | 0 | 0 | 10000 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E02W0.5 | 10.8.01 | 02Px0.5Sqmm ATC TYPE-F UNAR CABLE | 8 mm | 5 A | CBW01SS | 68 | 64768 | 2500 | 6000 | 1003 | 40.12% | 98.4514 | 34 | 16 | 11 | 0 | 16 | 0 | 0 | 3 | 0 | 4 | 34 | 0
E04W0.5 | 10.8.02 | 04Px0.5Sqmm ATC TYPE-F UNAR CABLE | 12 mm | 5 A | CBW01SS | 86 | 110242 | 4702 | 14000 | 0 | 0% | 100 | 43 | 0 | 2 | 2 | 8 | 16 | 0 | 2 | 0 | 8 | 48 | 0
E08W0.5 | 10.8.03 | 08Px0.5Sqmm ATC TYPE-F UNAR CABLE | 15 mm | 5 A | CBW01S | 4 | 40983 | 56 | 10000 | 0 | 0% | 100 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
E12W0.5 | 10.8.04 | 12Px0.5Sqmm ATC TYPE-F UNAR CABLE | 19 mm | 5 A | CBW02 | 2 | 22855 | 0 | 5000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F04-0.5 | 10.9.01 | OFC CABLE WITHOUT HDPE PIPE | 12 mm | 0 A | CBW01SS | 2 | 8674 | 0 | 8000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F12-0.5 | 10.9.02 | OFC CABLE WITH HDPE PIPE | 12 mm | 0 A | CBW01SS | 2 | 41206 | 0 | 3000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D04C2.5 | NA | 04Cx2.5Sqmm CU PVC-FRLS EDN UA CABLE | 17 mm | 18 A | CBW01 | 0 | 2994 | 0 | 0 | 0 | 0% | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03J1.5 | NA | 03Cx1.5Sqmm CU XLPE-FRLS ARM FIRE CABLE | 13 mm | 17 A | CBW01S | 0 | 85473 | 0 | 0 | 0 | 0% | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D01C050 | NA | 01Cx050Sqmm CU XLPE-FRLS UNARM CABLE | 18 mm | 150 A | CBW02 | 4 | 400 | 140 | 0 | 0 | 0% | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
[6 empty] | 9272 |  | 437274 |  | 56044 | 12.82% |  | 4636 | 948
|  |  | GLAND SELECTION |  |  | TOTAL | GLAND QUANTITY | bar: UNIT WISE GLAND QUANTITY EPD
|  |  | MIN-OD | MAX-OD | TYPE | QTY | EPD | PEM | BPL | JHS | RPT | EDN | HWR | TRY | UNIT WISE GLAND QUANTITY EPD: ISG
|  |  | 8 | 13 | CBW01SS | 1220 | 207 | 11 | 184 | 32 | 0 | 583 | 14 | 93 | UNIT WISE GLAND QUANTITY EPD: 6
|  |  | 13.5 | 16 | CBW01S | 4892 | 1494 | 478 | 377 | 197 | 875 | 924 | 26 | 342 | UNIT WISE GLAND QUANTITY EPD: 16
|  |  | 16.5 | 18 | CBW01 | 752 | 292 | 189 | 13 | 59 | 151 | 17 | 7 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 18.5 | 20 | CBW02 | 440 | 211 | 134 | 30 | 0 | 8 | 33 | 0 | 10 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 20.5 | 23 | CBW03 | 564 | 338 | 149 | 8 | 6 | 26 | 10 | 2 | 3 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 23.5 | 26 | CBW04 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 26.5 | 30 | CBW05 | 274 | 114 | 144 | 2 | 0 | 0 | 8 | 3 | 1 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 30.5 | 33 | CBW06 | 250 | 0 | 8 | 0 | 168 | 56 | 16 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 33.5 | 37 | CBW07 | 318 | 265 | 44 | 0 | 0 | 4 | 0 | 3 | 0 | UNIT WISE GLAND QUANTITY EPD: 2
|  |  | 37.5 | 41 | CBW08 | 24 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 41.5 | 46 | CBW09 | 288 | 92 | 20 | 120 | 0 | 6 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 18
|  |  | 46.5 | 52 | CBW010 | 106 | 57 | 43 | 0 | 0 | 0 | 6 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 52.5 | 56 | CBW011S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 56.5 | 60 | CBW011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 60.5 | 66 | CBW012 | 94 | 0 | 2 | 76 | 14 | 0 | 2 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 66.5 | 72 | CBW013A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 72.5 | 78 | CBW013 | 44 | 0 | 0 | 38 | 2 | 0 | 4 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 78.5 | 84 | CBW014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 84.5 | 92 | CBW015 | 4 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 92.5 | 104 | CBW016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
[5 empty] | TOTAL | 9272

## ScheduleCnI
SL |  | CMS | [5 empty] | DRG | LENGTH | LAYING | DRUM | TERMINATION | PLAN | PURPOSE | REMARK | SCHEDULE | ACTUAL
SCH | DOC | CABLE CODE | BOQ | CABLE NO | FROM | TO | CABLE DETAILS | LENGTH | ACTUAL | DATE | NO | STATUS |  |  |  | CABLE ROUTE | CABLE ROUTE | FROM | TO
1 | ACDB1 |  |  | 1A1-CJF11-01 (9ZB05AC01) | ACDB1-FDR01-P1 | CJF11-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
2 | ACDB1 |  |  | 1A1-CJF16-02 (9ZB05AC02) | ACDB1-FDR02-P2 | CJF16-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
3 | ACDB1 |  |  | 1A1-CJF21-03 (9ZB05AC03) | ACDB1-FDR03-P3 | CJF21-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
4 | ACDB1 |  |  | 1A1-CJF49-04 (9ZB05AC04) | ACDB1-FDR04-P4 | CJF49-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
5 | ACDB1 |  |  | 1A1-CJF50-05 (9ZB05AC05) | ACDB1-FDR05-P5 | CJF50-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
6 | ACDB1 |  |  | 1A1-CJJ41-06 (9ZB05AC06) | ACDB1-FDR06-P6 | CJJ41-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
7 | ACDB1 |  |  | 1A1-CTE01-07 (9ZB05AC07) | ACDB1-FDR07-P7 | CTE01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
8 | ACDB1 |  |  | 1A1-CWB01-08 (9ZB05AC08) | ACDB1-FDR08-P8 | CWB01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 37 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC18-03, CC27-03, CC28-03, CC37-03, CC38-03, CC47-03, CC48-03, ZZ99-
9 | ACDB1 |  |  | 1A1-U1PDPH01SW 5-10 (9ZB05AC09) | ACDB1-FDR10-P10 | SW-5 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
10 | ACDB1 |  |  | 1A1-U1PDPH01SW 5-10A (9ZB05AC10) | ACDB1-FDR10-P10 | SW-5 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
11 | ACDB1 |  |  | 1A1-U1PDPH01SW 6-11 (9ZB05AC11) | ACDB1-FDR11-P11 | SW-6 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
12 | ACDB1 |  |  | 1A1-U1PDPH01SW 6-11A (9ZB05AC12) | ACDB1-FDR11-P11 | SW-6 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
13 | ACDB1 |  |  | 1A1-U1PDPH01SW 1-12 (9ZB05AC13) | ACDB1-FDR12-P12 | SW-1 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
14 | ACDB1 |  |  | 1A1-U1PDPH01SW 2-13 (9ZB05AC14) | ACDB1-FDR13-P13 | SW-2 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
15 | ACDB1 |  |  | 1A1-U1PDPH01SW 3-14 (9ZB05AC15) | ACDB1-FDR14-P14 | SW-3 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
16 | ACDB1 |  |  | 1A1-U1PDPH01SW 4-15 (9ZB05AC16) | ACDB1-FDR15-P15 | SW-4 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 47 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, ZZ99-
17 | ACDB1 |  |  | 1A1-OXYGEN-16 (9ZB05AC17) | ACDB1-FDR16-P16 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
18 | ACDB1 |  |  | 1A1-OXYGEN-17 (9ZB05AC18) | ACDB1-FDR17-P17 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
19 | ACDB1 |  |  | 1A1-OXYGEN-18 (9ZB05AC19) | ACDB1-FDR18-P18 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
20 | ACDB1 |  |  | 1A1-OXYGEN-19 (9ZB05AC20) | ACDB1-FDR19-P19 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
21 | ACDB1 |  |  | 1A1-OXYGEN-20 (9ZB05AC21) | ACDB1-FDR20-P20 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
22 | ACDB1 |  |  | 1A1-OXYGEN-21 (9ZB05AC22) | ACDB1-FDR21-P21 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
23 | ACDB1 |  |  | 1A1-OXYGEN-22 (9ZB05AC23) | ACDB1-FDR22-P22 | OXYGEN ANALYZER-HIGH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
24 | ACDB1 |  |  | 1A1-OXYGEN-23 (9ZB05AC24) | ACDB1-FDR23-P23 | OXYGEN ANALYZER-HIGH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
25 | ACDB1 |  |  | 1A1-SWAS-24 (9ZB05AC25) | ACDB1-FDR24-P24 | SWAS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV43-03, LV09-L4, LV08-L4, LV45-03, TR22-03, ZZ99-
26 | ACDB1 |  |  | 1A1-OPAC-25 (9ZB05AC26) | ACDB1-FDR25-P25 | OPACITY MONITOR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
27 | ACDB1 |  |  | 1A1-CONDLS-26 (9ZB05AC27) | ACDB1-FDR26-P26 | CONDUCTIVITY TYPE LEVEL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV43-03, LV09-L4, LV08-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, ZZ99-
28 | ACDB1 |  |  | 1A1-CONDLS-27 (9ZB05AC28) | ACDB1-FDR27-P27 | CONDUCTIVITY TYPE LEVEL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 149 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV43-03, LV09-L4, LV08-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, ZZ99-
29 | ACDB1 |  |  | 1A1-CAPALS-28 (9ZB05AC29) | ACDB1-FDR28-P28 | CAPACITANCE TYPE LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L3, LV46-04, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99-
30 | ACDB1 |  |  | 1A1-CAPALS-29 (9ZB05AC30) | ACDB1-FDR29-P29 | CAPACITANCE TYPE LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L3, LV46-04, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99-
31 | ACDB1 |  |  | 1A1-VFDID-30 (9ZB05AC31) | ACDB1-FDR30-P30 | VFD(ID FAN)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 257 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES96-02, ES16-02, ES15-02, ES14-02, ES13-02, ES12-02, ES45-L3, ZZ99-
32 | ACDB1 |  |  | 1A1-VFDCEP-31 (9ZB05AC32) | ACDB1-FDR31-P31 | VFD(CEP)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 58 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, AC05-02, AC09-03, DR06-02, AC10-02, AC11-02, AC12-02, ZZ99-
33 | ACDB1 |  |  | 1A1-VMS-32 (9ZB05AC33) | ACDB1-FDR32-P32 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, ZZ99-
34 | ACDB1 |  |  | 1A1-VMS-33 (9ZB05AC34) | ACDB1-FDR33-P33 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, ZZ99-
35 | ACDB1 |  |  | 1A1-VMS-34 (9ZB05AC35) | ACDB1-FDR34-P34 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, ZZ99-
36 | ACDB1 |  |  | 1A1-VMS-35 (9ZB05AC36) | ACDB1-FDR35-P35 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 42 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, ZZ99-
37 | ACDB1 |  |  | 1A1-CCTV-36 (9ZB05AC37) | ACDB1-FDR36-P36 | CCTV(UNIT)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
38 | ACDB1 |  |  | 1A1-CCTV-37 (9ZB05AC38) | ACDB1-FDR37-P37 | CCTV(CPA)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
39 | ACDB1 |  |  | 1A1-DAVR-38 (9ZB05AC39) | ACDB1-FDR38-P38 | DAVR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 180 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
40 | ACDB1 |  |  | 1A1-EIS-39 (9ZB05AC40) | ACDB1-FDR39-P39 | EIS(CCR)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
41 | ACDB1 |  |  | 1A1-EMS-40 (9ZB05AC41) | ACDB1-FDR40-P40 | EMS(CCR)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
42 | ACDB1 |  |  | 1A1-GEN-INST-4 1 (9ZB05AC42) | ACDB1-FDR41-P41 | GEN INST CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, ZZ99-
43 | ACDB1 |  |  | 1A1-GEN-WDG-42 (9ZB05AC43) | ACDB1-FDR42-P42 | GEN WDG VIB SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, ZZ99-
44 | ACDB1 |  |  | 1A1-ALK-DOS-43 (9ZB05AC44) | ACDB1-FDR43-P43 | ALK DOS PMP-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, TG08-R2, ZZ99-
45 | ACDB1 |  |  | 1A1-H2-GAS-44 (9ZB05AC45) | ACDB1-FDR44-P44 | H2 GAS ANA-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
46 | ACDB1 |  |  | 1A1-GND-BR-45 (9ZB05AC46) | ACDB1-FDR45-P45 | GND BRUSH MON-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 196 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV76-04, LV07-L4, LV06-L3, LV54-02, TR23-02, TP01-02, TP02-02, TP03-02, TP05-02, TP10-02, TP11-02, TP12-02, TP13-02, TP14-02, TP21-01, TP20-01, TP22-02, TP27-02, TP28-02, TP44-02, TP45-02, TP46-02, ZZ99-
47 | ACDB1 |  |  | 1A1-FLMSCN-46 (9ZB05AC47) | ACDB1-FDR46-P46 | FLAME SCAN AMP-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
48 | ACDB1 |  |  | 1A1-GRAVI-47 (9ZB05AC48) | ACDB1-FDR47-P47 | GRAVI FEEDER REM CTRL CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY |  | CC16-02, CC54-03, CC53-03, CC04-03, CC02-03, ZZ99-
49 | ACDB1 |  |  | 1A1-GRAVI-48 (9ZB05AC49) | ACDB1-FDR48-P48 | GRAVI FEEDER REM CTRL CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY |  | CC16-02, CC54-03, CC53-03, CC04-03, CC02-03, ZZ99-
50 | ACDB1 |  |  | 1A1-GRAVI-49 (9ZB05AC50) | ACDB1-FDR49-P49 | GRAVI FEEDER REM CTRL CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 28 | [5 empty] | POWER SUPPLY |  | CC16-02, CC54-03, CC53-03, CC04-03, CC02-03, ZZ99-
51 | ACDB1 |  |  | 1A1-BLRLIFE-50 (9ZB05AC51) | ACDB1-FDR50-P50 | BLR LIFE ASSES-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
52 | ACDB1 |  |  | 1A1-HEA-51 (9ZB05AC52) | ACDB1-FDR51-P51 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
53 | ACDB1 |  |  | 1A1-HEA-52 (9ZB05AC53) | ACDB1-FDR52-P52 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
54 | ACDB1 |  |  | 1A1-HEA-53 (9ZB05AC54) | ACDB1-FDR53-P53 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
55 | ACDB1 |  |  | 1A1-HEA-54 (9ZB05AC55) | ACDB1-FDR54-P54 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
56 | ACDB1 |  |  | 1A1-HEA-55 (9ZB05AC56) | ACDB1-FDR55-P55 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 200 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
57 | ACDB1 |  |  | 1A1-HEA-56 (9ZB05AC57) | ACDB1-FDR56-P56 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 201 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
58 | ACDB1 |  |  | 1A1-LDO-57 (9ZB05AC58) | ACDB1-FDR57-P57 | LDO FLOW MTR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 447 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, ZZ99-
59 | ACDB1 |  |  | 1A1-AH-SOV-58 (9ZB05AC59) | ACDB1-FDR58-P58 | AH AIR MOTOR SOL VLV-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 199 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, BD25-02, BD26-02, ZZ99-
60 | ACDB1 |  |  | 1A1-AH-SPEED-5 9 (9ZB05AC60) | ACDB1-FDR59-P59 | APH ROTOR SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 214 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC10-02, BC09-02, ZZ99-
61 | ACDB1 |  |  | 1A1-AH-SPEED-6 0 (9ZB05AC61) | ACDB1-FDR60-P60 | APH ROTOR SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 201 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC10-02, ZZ99-
62 | ACDB1 |  |  | 1A1-APHLVL-61 (9ZB05AC62) | ACDB1-FDR61-P61 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 199 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, BD25-02, BD26-02, ZZ99-
63 | ACDB1 |  |  | 1A1-APHLVL-62 (9ZB05AC63) | ACDB1-FDR62-P62 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 199 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, BD25-02, BD26-02, ZZ99-
64 | ACDB1 |  |  | 1A1-APHLVL-63 (9ZB05AC64) | ACDB1-FDR63-P63 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 205 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, BD25-02, BD26-02, BD27-02, ZZ99-
65 | ACDB1 |  |  | 1A1-APHLVL-64 (9ZB05AC65) | ACDB1-FDR64-P64 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 205 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, BD25-02, BD26-02, BD27-02, ZZ99-
66 | ACDB1 |  |  | 1A1-ECOLVL-65 (9ZB05AC66) | ACDB1-FDR65-P65 | ECO HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 222 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BK04-02, BK05-02, BK06-02, BK07-02, ZZ99-
67 | ACDB1 |  |  | 1A1-ECOLVL-66 (9ZB05AC67) | ACDB1-FDR66-P66 | ECO HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 232 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BK04-02, BK05-02, BK06-02, BK07-02, ZZ99-
68 | ACDB1 |  |  | 1A1-DRMLVL-67 (9ZB05AC68) | ACDB1-FDR67-P67 | LOC DRM LVL GAUGE-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 231 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BR69-02, BO08-02, BO09-02, ZZ99-
69 | ACDB1 |  |  | 1A1-HYDSCP-68 (9ZB05AC69) | ACDB1-FDR68-P68 | POS TX OF HYD SCOUP TUBE-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
70 | ACDB1 |  |  | 1A1-HYDSCP-69 (9ZB05AC70) | ACDB1-FDR69-P69 | POS TX OF HYD SCOUP TUBE-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
71 | ACDB1 |  |  | 1A1-MILLREJ-70 (9ZB05AC71) | ACDB1-FDR70-P70 | MILL REJ SEQ-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
72 | ACDB1 |  |  | 1A1-FIREALM-71 (9ZB05AC72) | ACDB1-FDR71-P71 | FIRE ALM SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC25-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, ZZ99-
73 | ACDB1 |  |  | 1A1-PASYS-72 (9ZB05AC73) | ACDB1-FDR72-P72 | PA SYSTEM-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC59-02, CC39-02, ZZ99-
74 | ACDB1 |  |  | 1A1-PC-PRNTR-E LEC-73 (9ZB05AC74) | ACDB1-FDR73-P73 | PC, PRNTR FOR ELEC-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
75 | ACDB1 |  |  | 1A1-COMP-AIR-7 4 (9ZB05AC75) | ACDB1-FDR74-P74 | COMPRESSED AIR SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 244 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV23-L4, LV22-L4, LV21-L4, LV20-L4, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, ZZ99-
76 | ACDB1 |  |  | 1A1-COMP-AIR-7 5 (9ZB05AC76) | ACDB1-FDR75-P75 | COMPRESSED AIR SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 243 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC75-03, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV23-R3, LV22-R3, LV21-R3, LV20-R3, LV19-R3, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, ZZ99-
77 | ACDB1 |  |  | 1A1-IOSPC-DATA -76 (9ZB05AC77) | ACDB1-FDR76-P76 | IOS PC, DATA LOG-PRNTR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
78 | ACDB1 |  |  | 1A1-OPAC-77 (9ZB05AC78) | ACDB1-FDR77-P77 | OPACITY MONITOR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
79 | ACDB1 |  |  | 1A1-OPAC-78 (9ZB05AC79) | ACDB1-FDR78-P78 | OPACITY MONITOR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
80 | ACDB1 |  |  | 1A1-HTMTRSPEED -79 (9ZB05AC80) | ACDB1-FDR79-P79 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
81 | ACDB1 |  |  | 1A1-HTMTRSPEED -80 (9ZB05AC81) | ACDB1-FDR80-P80 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 141 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
82 | ACDB1 |  |  | 1A1-HTMTRSPEED -81 (9ZB05AC82) | ACDB1-FDR81-P81 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 146 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
83 | ACDB1 |  |  | 1A1-HTMTRSPEED -82 (9ZB05AC83) | ACDB1-FDR82-P82 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
84 | ACDB1 |  |  | 1A1-HTMTRSPEED -83 (9ZB05AC84) | ACDB1-FDR83-P83 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
85 | ACDB1 |  |  | 1A1-HTMTRSPEED -84 (9ZB05AC85) | ACDB1-FDR84-P84 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 126 | [5 empty] | POWER SUPPLY |  | CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
86 | ACDB1 |  |  | 1A1-HTMTRSPEED -85 (9ZB05AC86) | ACDB1-FDR85-P85 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99-
87 | ACDB1 |  |  | 1A1-HTMTRSPEED -86 (9ZB05AC87) | ACDB1-FDR86-P86 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99-
88 | ACDB1 |  |  | 1A1-HTMTRSPEED -87 (9ZB05AC88) | ACDB1-FDR87-P87 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 97 | [5 empty] | POWER SUPPLY |  | CC16-02, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99-
89 | ACDB1 |  |  | 1A1-PCOWS-88 (9ZB05AC89) | ACDB1-FDR88-P88 | PC(OWS)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
90 | ACDB1 |  |  | 1A1-BNKR-LVL-8 9 (9ZB05AC90) | ACDB1-FDR89-P89 | COAL BUNKER LVL MON-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
91 | ACDB1 |  |  | 1A1-MERCURY-10 0 (9ZB05AC91) | ACDB1-FDR100-P100 | MERCURY ANALYSER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 399 | [5 empty] | POWER SUPPLY |  | CC16-02, CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
1 | ACDB2 |  |  | 1A2-CJF11-01 (9ZB06AC01) | ACDB2-FDR01-P1 | CJF11-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
2 | ACDB2 |  |  | 1A2-CJF16-02 (9ZB06AC02) | ACDB2-FDR02-P2 | CJF16-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
3 | ACDB2 |  |  | 1A2-CJF21-03 (9ZB06AC03) | ACDB2-FDR03-P3 | CJF21-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
4 | ACDB2 |  |  | 1A2-CJF49-04 (9ZB06AC04) | ACDB2-FDR04-P4 | CJF49-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
5 | ACDB2 |  |  | 1A2-CJF50-05 (9ZB06AC05) | ACDB2-FDR05-P5 | CJF50-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
6 | ACDB2 |  |  | 1A2-CJJ41-06 (9ZB06AC06) | ACDB2-FDR06-P6 | CJJ41-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
7 | ACDB2 |  |  | 1A2-CTE01-07 (9ZB06AC07) | ACDB2-FDR07-P7 | CTE01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
8 | ACDB2 |  |  | 1A2-CWB01-08 (9ZB06AC08) | ACDB2-FDR08-P8 | CWB01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 31 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC38-03, CC47-03, CC48-03, ZZ99-
9 | ACDB2 |  |  | 1A2-U1PDPH01SW 5-10 (9ZB06AC09) | ACDB2-FDR10-P10 | SW-5 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
10 | ACDB2 |  |  | 1A2-U1PDPH01SW 5-10A (9ZB06AC10) | ACDB2-FDR10-N10 | SW-5 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
11 | ACDB2 |  |  | 1A2-U1PDPH01SW 6-11 (9ZB06AC11) | ACDB2-FDR11-P11 | SW-6 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
12 | ACDB2 |  |  | 1A2-U1PDPH01SW 6-11A (9ZB06AC12) | ACDB2-FDR11-N11 | SW-6 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
13 | ACDB2 |  |  | 1A2-U1PDPH01SW 1-12 (9ZB06AC13) | ACDB2-FDR12-P12 | SW-1 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
14 | ACDB2 |  |  | 1A2-U1PDPH01SW 2-13 (9ZB06AC14) | ACDB2-FDR13-P13 | SW-2 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
15 | ACDB2 |  |  | 1A2-U1PDPH01SW 3-14 (9ZB06AC15) | ACDB2-FDR14-P14 | SW-3 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
16 | ACDB2 |  |  | 1A2-U1PDPH01SW 4-15 (9ZB06AC16) | ACDB2-FDR15-P15 | SW-4 OF U1 PDPH01-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 49 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC34-02, CC42-02, ZZ99-
17 | ACDB2 |  |  | 1A2-OXYGEN-16 (9ZB06AC17) | ACDB2-FDR16-P16 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
18 | ACDB2 |  |  | 1A2-OXYGEN-17 (9ZB06AC18) | ACDB2-FDR17-P17 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
19 | ACDB2 |  |  | 1A2-OXYGEN-18 (9ZB06AC19) | ACDB2-FDR18-P18 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
20 | ACDB2 |  |  | 1A2-OXYGEN-19 (9ZB06AC20) | ACDB2-FDR19-P19 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
21 | ACDB2 |  |  | 1A2-OXYGEN-20 (9ZB06AC21) | ACDB2-FDR20-P20 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
22 | ACDB2 |  |  | 1A2-OXYGEN-21 (9ZB06AC22) | ACDB2-FDR21-P21 | OXYGEN ANALYZER-LOW-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
23 | ACDB2 |  |  | 1A2-OXYGEN-22 (9ZB06AC23) | ACDB2-FDR22-P22 | OXYGEN ANALYZER-HIGH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
24 | ACDB2 |  |  | 1A2-OXYGEN-23 (9ZB06AC24) | ACDB2-FDR23-P23 | OXYGEN ANALYZER-HIGH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 403 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
25 | ACDB2 |  |  | 1A2-FG-SOX-NOX -24 (9ZB06AC25) | ACDB2-FDR24-P24 | FG ANA(Sox, Nox)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 393 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
26 | ACDB2 |  |  | 1A2-CONDLS-25 (9ZB06AC26) | ACDB2-FDR25-P25 | CONDUCTIVITY TYPE LEVEL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 152 | [5 empty] | POWER SUPPLY |  | CC17-02, CC09-02, CC10-02, CC11-02, CC74-02, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV43-03, LV09-L4, LV08-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, ZZ99-
27 | ACDB2 |  |  | 1A2-CONDLS-26 (9ZB06AC27) | ACDB2-FDR26-P26 | CONDUCTIVITY TYPE LEVEL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 152 | [5 empty] | POWER SUPPLY |  | CC17-02, CC09-02, CC10-02, CC11-02, CC74-02, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV43-03, LV09-L4, LV08-L4, LV45-03, TR52-03, TG67-03, TG68-03, TR03-03, TG22-03, TR04-03, TG23-03, ZZ99-
28 | ACDB2 |  |  | 1A2-CAPALS-27 (9ZB06AC28) | ACDB2-FDR27-P27 | CAPACITANCE TYPE LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY |  | CC17-03, CC09-02, CC10-02, CC11-02, CC74-02, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L3, LV46-04, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99-
29 | ACDB2 |  |  | 1A2-CAPALS-28 (9ZB06AC29) | ACDB2-FDR28-P28 | CAPACITANCE TYPE LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 103 | [5 empty] | POWER SUPPLY |  | CC17-03, CC09-02, CC10-02, CC11-02, CC74-02, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L3, LV46-04, LV37-L4, LV36-L4, LV35-L4, LV34-L4, LV33-L4, LV65-02, LR09-02, ZZ99-
30 | ACDB2 |  |  | 1A2-VFDID-29 (9ZB06AC30) | ACDB2-FDR29-P29 | VFD(ID FAN)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 246 | [5 empty] | POWER SUPPLY |  | CC17-02, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM60-L3, IM61-L3, IM62-L3, IM63-L3, IR25-L3, ES01-L3, ES02-02, ES03-02, ES04-02, ES42-02, ZZ99-
31 | ACDB2 |  |  | 1A2-VFDCEP-30 (9ZB06AC31) | ACDB2-FDR30-P30 | VFD(CEP)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 36 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, DR05-02, AC08-02, AC07-02, AC06-02, ZZ99-
32 | ACDB2 |  |  | 1A2-VMS-31 (9ZB06AC32) | ACDB2-FDR31-P31 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, ZZ99-
33 | ACDB2 |  |  | 1A2-VMS-32 (9ZB06AC33) | ACDB2-FDR32-P32 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, ZZ99-
34 | ACDB2 |  |  | 1A2-VMS-33 (9ZB06AC34) | ACDB2-FDR33-P33 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, ZZ99-
35 | ACDB2 |  |  | 1A2-VMS-34 (9ZB06AC35) | ACDB2-FDR34-P34 | VMS AT MAIN UNIT EER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, ZZ99-
36 | ACDB2 |  |  | 1A2-VMS-35 (9ZB06AC36) | ACDB2-FDR35-P35 | VMS AT CCR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 43 | [5 empty] | POWER SUPPLY |  | ZZ99- , CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, ZZ99-
37 | ACDB2 |  |  | 1A2-CCTV-36 (9ZB06AC37) | ACDB2-FDR36-P36 | CCTV(UNIT)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY |  | CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC38-03, CC47-03, CC46-02, ZZ99-
38 | ACDB2 |  |  | 1A2-CCTV-37 (9ZB06AC38) | ACDB2-FDR37-P37 | CCTV(CPA)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 33 | [5 empty] | POWER SUPPLY |  | CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC38-03, CC47-03, CC46-02, ZZ99-
39 | ACDB2 |  |  | 1A2-EIS-38 (9ZB06AC39) | ACDB2-FDR38-P38 | EIS(CCR)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
40 | ACDB2 |  |  | 1A2-EMS-39 (9ZB06AC40) | ACDB2-FDR39-P39 | EMS(CCR)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
41 | ACDB2 |  |  | 1A2-GEN-INST-4 0 (9ZB06AC41) | ACDB2-FDR40-P40 | GEN INST CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY |  | CC17-03, CC16-02, CC15-02, ZZ99-
42 | ACDB2 |  |  | 1A2-GEN-WDG-41 (9ZB06AC42) | ACDB2-FDR41-P41 | GEN WDG VIB SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 24 | [5 empty] | POWER SUPPLY |  | CC17-03, CC16-02, CC15-02, ZZ99-
43 | ACDB2 |  |  | 1A2-H2-GAS-42 (9ZB06AC43) | ACDB2-FDR42-P42 | H2 GAS ANA-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 393 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
44 | ACDB2 |  |  | 1A2-MOIST-MEAS -43 (9ZB06AC44) | ACDB2-FDR43-P43 | MOIS MEAS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
45 | ACDB2 |  |  | 1A2-FLMSCN-44 (9ZB06AC45) | ACDB2-FDR44-P44 | FLAME SCAN AMP-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
46 | ACDB2 |  |  | 1A2-GRAVI-45 (9ZB06AC46) | ACDB2-FDR45-P45 | GRAVI FEEDER REM CTRL CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC06-03, CC04-03, CC02-03, ZZ99-
47 | ACDB2 |  |  | 1A2-GRAVI-46 (9ZB06AC47) | ACDB2-FDR46-P46 | GRAVI FEEDER REM CTRL CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC06-03, CC04-03, CC02-03, ZZ99-
48 | ACDB2 |  |  | 1A2-GRAVI-47 (9ZB06AC48) | ACDB2-FDR47-P47 | GRAVI FEEDER REM CTRL CAB-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC06-03, CC04-03, CC02-03, ZZ99-
49 | ACDB2 |  |  | 1A2-HEA-48 (9ZB06AC49) | ACDB2-FDR48-P48 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
50 | ACDB2 |  |  | 1A2-HEA-49 (9ZB06AC50) | ACDB2-FDR49-P49 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
51 | ACDB2 |  |  | 1A2-HEA-50 (9ZB06AC51) | ACDB2-FDR50-P50 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
52 | ACDB2 |  |  | 1A2-HEA-51 (9ZB06AC52) | ACDB2-FDR51-P51 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
53 | ACDB2 |  |  | 1A2-HEA-52 (9ZB06AC53) | ACDB2-FDR52-P52 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
54 | ACDB2 |  |  | 1A2-HEA-53 (9ZB06AC54) | ACDB2-FDR53-P53 | HEA IGNITOR BOX-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 170 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
55 | ACDB2 |  |  | 1A2-BLR-MAINT- 54 (9ZB06AC55) | ACDB2-FDR54-P54 | BLR MAINT STN-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
56 | ACDB2 |  |  | 1A2-VFD-55 (9ZB06AC56) | ACDB2-FDR55-P55 | VFD(MMI)-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 60 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
57 | ACDB2 |  |  | 1A2-AH-SOV-56 (9ZB06AC57) | ACDB2-FDR56-P56 | AH AIR MOTOR SOL VLV-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 180 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC28-03, CC37-03, CC38-03, CC47-03, CC48-03, CC49-03, CC50-03, CC70-03, CC69-03, CC41-01, CC43-03, CC87-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BD17-02, BD16-02, BR40-02, BC26-02, ZZ99-
58 | ACDB2 |  |  | 1A2-AH-SPEED-5 7 (9ZB06AC58) | ACDB2-FDR57-P57 | APH ROTOR SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 237 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC28-03, CC37-03, CC38-03, CC47-03, CC48-03, CC49-03, CC50-03, CC70-03, CC69-03, CC41-01, CC43-03, CC87-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99-
59 | ACDB2 |  |  | 1A2-AH-SPEED-5 8 (9ZB06AC59) | ACDB2-FDR58-P58 | APH ROTOR SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 215 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, ZZ99-
60 | ACDB2 |  |  | 1A2-TURB-LIFE- 59 (9ZB06AC60) | ACDB2-FDR59-P59 | TURB LIFE ASSES-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
61 | ACDB2 |  |  | 1A2-APHLVL-60 (9ZB06AC61) | ACDB2-FDR60-P60 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 201 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, BD25-02, BD26-02, ZZ99-
62 | ACDB2 |  |  | 1A2-APHLVL-61 (9ZB06AC62) | ACDB2-FDR61-P61 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 201 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BR42-02, BD24-02, BD25-02, BD26-02, ZZ99-
63 | ACDB2 |  |  | 1A2-APHLVL-62 (9ZB06AC63) | ACDB2-FDR62-P62 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 205 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, BD27-02, ZZ99-
64 | ACDB2 |  |  | 1A2-APHLVL-63 (9ZB06AC64) | ACDB2-FDR63-P63 | APH HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 205 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BR43-02, BD29-02, BD28-02, BD27-02, ZZ99-
65 | ACDB2 |  |  | 1A2-ECOLVL-64 (9ZB06AC65) | ACDB2-FDR64-P64 | ECO HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 229 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BK04-02, BK05-02, BK06-02, BK07-02, ZZ99-
66 | ACDB2 |  |  | 1A2-ECOLVL-65 (9ZB06AC66) | ACDB2-FDR65-P65 | ECO HOPPER ASH LVL S/W-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 229 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR04-03, BR05-03, BR06-03, BR07-04, BR08-04, BR09-04, BR10-02, BK01-02, BK02-02, BK04-02, BK05-02, BK06-02, BK07-02, ZZ99-
67 | ACDB2 |  |  | 1A2-DRMLVL-66 (9ZB06AC67) | ACDB2-FDR66-P66 | LOC DRM LVL GAUGE-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 230 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC26-02, CC25-02, CC66-03, CC67-03, CC34-02, CC42-02, CC85-02, CC86-02, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, BR21-04, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BR68-02, BO04-02, ZZ99-
68 | ACDB2 |  |  | 1A2-HYDSCP-67 (9ZB06AC68) | ACDB2-FDR67-P67 | POS TX OF HYD SCOUP TUBE-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 111 | [5 empty] | POWER SUPPLY |  | CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99-
69 | ACDB2 |  |  | 1A2-REV-ROT-68 (9ZB06AC69) | ACDB2-FDR68-P68 | REV ROT IND-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 150 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
70 | ACDB2 |  |  | 1A2-FIREALM-69 (9ZB06AC70) | ACDB2-FDR69-P69 | FIRE ALM SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 53 | [5 empty] | POWER SUPPLY |  | CC17-03, CC18-03, CC27-03, CC28-03, CC29-02, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, ZZ99-
71 | ACDB2 |  |  | 1A2-PASYS-70 (9ZB06AC71) | ACDB2-FDR70-P70 | PA SYSTEM-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | CC17-03, CC18-03, CC27-03, CC28-03, CC37-03, CC38-03, CC39-02, ZZ99-
72 | ACDB2 |  |  | 1A2-PC-PRNTR-E LEC-71 (9ZB06AC72) | ACDB2-FDR71-P71 | PC, PRNTR FOR ELEC-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
73 | ACDB2 |  |  | 1A2-COMP-AIR-7 2 (9ZB06AC73) | ACDB2-FDR72-P72 | COMPRESSED AIR SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 257 | [5 empty] | POWER SUPPLY |  | CC17-03, CC09-02, CC10-02, CC11-02, CC74-02, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L3, LV29-L4, LV30-L4, LV31-L4, LV61-05, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM06-L3, CM07-L3, CM08-L3, CM09-L3, ZZ99-
74 | ACDB2 |  |  | 1A2-COMP-AIR-7 3 (9ZB06AC74) | ACDB2-FDR73-P73 | COMPRESSED AIR SYS-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 257 | [5 empty] | POWER SUPPLY |  | CC17-03, CC09-02, CC10-02, CC11-02, CC74-02, CC73-03, CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L3, LV29-L4, LV30-L4, LV31-L4, LV61-05, LV19-L4, LV68-02, LV69-02, LV02-L4, LV01-02, LR01-03, TY13-L4, TY12-L4, TY11-L4, TY36-03, TY37-03, TY38-03, TY39-03, YR03-03, TY40-03, TY41-03, TY42-03, TY43-03, NR01-03, CM04-L3, CM05-L3, CM06-L3, CM07-L3, CM08-L3, CM09-L3, ZZ99-
75 | ACDB2 |  |  | 1A2-OPAC-74 (9ZB06AC75) | ACDB2-FDR74-P74 | OPACITY MONITOR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 393 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
76 | ACDB2 |  |  | 1A2-OPAC-75 (9ZB06AC76) | ACDB2-FDR75-P75 | OPACITY MONITOR-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 393 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
77 | ACDB2 |  |  | 1A2-WTR-LK-BFP -76 (9ZB06AC77) | ACDB2-FDR76-P76 | WTR LEAK DET MDBFP-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 151 | [5 empty] | POWER SUPPLY |  | CC17-03, CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
78 | ACDB2 |  |  | 1A2-HTMTRSPEED -77 (9ZB06AC78) | ACDB2-FDR77-P77 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 145 | [5 empty] | POWER SUPPLY |  | CC17-03, CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
79 | ACDB2 |  |  | 1A2-HTMTRSPEED -78 (9ZB06AC79) | ACDB2-FDR78-P78 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 145 | [5 empty] | POWER SUPPLY |  | CC17-03, CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
80 | ACDB2 |  |  | 1A2-HTMTRSPEED -79 (9ZB06AC80) | ACDB2-FDR79-P79 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 145 | [5 empty] | POWER SUPPLY |  | CC17-03, CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
81 | ACDB2 |  |  | 1A2-HTMTRSPEED -80 (9ZB06AC81) | ACDB2-FDR80-P80 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 130 | [5 empty] | POWER SUPPLY |  | CC17-03, CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
82 | ACDB2 |  |  | 1A2-HTMTRSPEED -81 (9ZB06AC82) | ACDB2-FDR81-P81 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | POWER SUPPLY |  | CC17-02, CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
83 | ACDB2 |  |  | 1A2-HTMTRSPEED -82 (9ZB06AC83) | ACDB2-FDR82-P82 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 129 | [5 empty] | POWER SUPPLY |  | CC17-02, CC16-02, CC15-02, CC14-02, CC76-02, CC77-03, CC79-03, CC90-03, LR07-03, MR08-03, MA07-03, MV44-L2, MV27-L2, MV26-L2, MV08-L2, MV07-L2, MV06-L2, MR18-02, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
84 | ACDB2 |  |  | 1A2-HTMTRSPEED -83 (9ZB06AC84) | ACDB2-FDR83-P83 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 102 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99-
85 | ACDB2 |  |  | 1A2-HTMTRSPEED -84 (9ZB06AC85) | ACDB2-FDR84-P84 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, CC68-03, CC41-01, CC43-03, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99-
86 | ACDB2 |  |  | 1A2-HTMTRSPEED -85 (9ZB06AC86) | ACDB2-FDR85-P85 | HT MOTORS SPEED SWITCH-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 104 | [5 empty] | POWER SUPPLY |  | CC17-02, CC18-03, CC27-03, CC28-03, CC37-03, CC36-02, CC35-02, CC68-03, CC41-01, CC43-03, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV74-03, MV75-03, TR51-03, TG69-03, TG70-03, ZZ99-
87 | ACDB2 |  |  | 1A2-MAIN-FIRE- ALM-86 (9ZB06AC87) | ACDB2-FDR86-P86 | MAIN FIRE ALM-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 120 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
88 | ACDB2 |  |  | 1A2-PRINTER-87 (9ZB06AC88) | ACDB2-FDR87-P87 | PRINTER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
89 | ACDB2 |  |  | 1A2-BNKR-LVL-8 8 (9ZB06AC89) | ACDB2-FDR88-P88 | COAL BUNKER LVL MON-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | POWER SUPPLY |  | SITE ROUTING
90 | ACDB2 |  |  | 1A2-MERCURY-10 0 (9ZB06AC90) | ACDB2-FDR100-P100 | MERCURY ANALYSER-P | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 393 | [5 empty] | POWER SUPPLY |  | CC17-03, CC08-03, CC07-03, IR20-02, IM08-02, IM09-05, IM10-04, IM11-L7, IM12-L7, IM13-L5, IM14-L5, IM15-L5, IM16-L5, IM17-L5, IM18-L5, IM19-L5, IM20-L5, IM21-L5, IM32-L5, IM33-L5, IR31-L4, IM34-L5, IM35-L5, IM36-L5, IM37-L5, IM38-L2, IR22-L2, IM39-L2, IM40-L2, IM41-L2, IM42-L2, IM43-L2, IR30-03, IM44-03, IM46-01, IM47-01, IM48-01, IM49-01, IM50-01, ZZ99-
1 | ANAD |  |  | CVP01-MD-D001 (9ZI03AC01) | 1HNC01AA152 , El: 0.0 mtr, NEAR ID FAN-A | CVP01 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 366 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , IM45-04, IM44-04, IR30-04, IM43-R2, IM42-R2, IM41-R2, IM40-R2, IM39-R2, IR22-R2, IM38-R2, IM37-L6, IM36-L6, IM35-L6, IM34-L6, IR31-L3, IM33-L6, IM32-L6, IM21-L4, IM20-L4, IM19-L4, IM18-L4, IM17-L4, IM16-L4, IM15-L4, IM14-L4, IM13-L4, IM12-L6, IM11-L6, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99-
2 | ANAD |  |  | CVP01-MD-D002 (9ZI03AC02) | 1HNC02AA152 , El: 0.0 mtr, NEAR ID FAN-B | CVP01 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 321 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , IM59-04, IM58-04, IM57-04, IR21-04, IM37-L6, IM36-L6, IM35-L6, IM34-L6, IR31-L3, IM33-L6, IM32-L6, IM21-L4, IM20-L4, IM19-L4, IM18-L4, IM17-L4, IM16-L4, IM15-L4, IM14-L4, IM13-L4, IM12-L6, IM11-L6, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, ZZ99-
3 | ANAD |  |  | CVP02-MD-D001 (9ZI03AC03) | 1HLB01AA151 , El: 0.0 mtr, NEAR FD FAN-A | CVP02 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 180 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , IC23-03, IC22-03, IC19-R2, IC17-R2, IC14-R2, IR10-04, IC13-04, IC12-04, IC11-04, IC10-04, IC09-04, IC08-04, IR08-04, IC07-R4, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03, ZZ99-
4 | ANAD |  |  | CVP02-MD-D002 (9ZI03AC04) | 1HLB02AA151 , El: 0.0 mtr, NEAR FD FAN-B | CVP02 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 170 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , IM70-04, IR26-03, IM69-04, IM68-06, IM67-06, IM66-06, IM65-06, IM64-06, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC10-03, CC63-04, CC64-04, CC65-04, CC66-04, CC31-03, ZZ99-
5 | ANAD |  |  | CVP03-MD-D001 (9ZI03AC05) | 1HFE01AA151 , El: 0.0 mtr, NEAR PA FAN-A | CVP03 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 173 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , IC18-03, IC17-R2, IC14-R2, IR10-04, IC13-04, IC12-04, IC11-04, IC10-04, IC09-04, IC08-04, IR08-04, IC07-R4, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03, ZZ99-
6 | ANAD |  |  | CVP03-MD-D002 (9ZI03AC06) | 1HFE02AA151 , El: 0.0 mtr, NEAR PA FAN-B | CVP03 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 173 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , IM71-04, IM70-04, IR26-03, IM69-04, IM68-06, IM67-06, IM66-06, IM65-06, IM64-06, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC10-03, CC63-04, CC64-04, CC65-04, CC66-04, CC31-03, ZZ99-
7 | ANAD |  |  | CVP03-MD-D003 (9ZI03AC07) | 1HLC20AA101 , El: 7 mtr, NEAR : S15R | CVP03 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 129 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC33-04, CC31-03, ZZ99-
8 | ANAD |  |  | CVP04-BD-D004 (9ZI03AC08) | 1HBK65AA002 , EL: 56.85 mtr, Near S10R | CVP04 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 134 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
9 | ANAD |  |  | CVP04-BD-D005 (9ZI03AC09) | 1HLC30AA101 , El: 7 mtr, NEAR : S15L | CVP04 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 162 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BA12-03, BA11-03, BA10-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
10 | ANAD |  |  | CVP04-BD-D005A (9ZI03AC10) | 1HBK60AA002 , EL: 56.85 mtr, Near S10L | CVP04 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 160 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BR21-05, BR20-05, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
11 | ANAD |  |  | CVP05-MD-D001 (9ZI03AC11) | 1HFE52AA101 , Near Mill B @ 17.75m | CVP05 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 197 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC15-03, BC14-03, BC11-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
12 | ANAD |  |  | CVP05-MD-D002 (9ZI03AC12) | 1HFE62AA101 , Near Mill B @ 17.75m | CVP05 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 197 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC15-03, BC14-03, BC11-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
13 | ANAD |  |  | CVP05-MD-D003 (9ZI03AC13) | 1HFW02AA101 , Between mill C&D @ 0.0m | CVP05 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 243 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , IM90-03, IR35-03, IM89-03, IM88-03, IM87-04, IM86-04, IM85-04, IM80-04, IM79-04, IR32-04, IM78-04, IM77-04, IM76-04, IR28-04, IM75-04, IM72-06, IM68-06, IM67-06, IM66-06, IM65-06, IM64-06, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, ZZ99-
14 | ANAD |  |  | CVP05-MD-D004 (9ZI03AC14) | 1HFE51AA101 , Near Mill A @ 17.75m | CVP05 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 207 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC16-03, BC15-03, BC14-03, BC11-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
15 | ANAD |  |  | CVP05-MD-D005 (9ZI03AC15) | 1HFE61AA101 , Near Mill A @ 17.75m | CVP05 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 207 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC16-03, BC15-03, BC14-03, BC11-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
16 | ANAD |  |  | CVP05-MD-D006 (9ZI03AC16) | 1HFW01AA101 , Between mill C&D @ 0.0m | CVP05 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 243 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , IM90-03, IR35-03, IM89-03, IM88-03, IM87-04, IM86-04, IM85-04, IM80-04, IM79-04, IR32-04, IM78-04, IM77-04, IM76-04, IR28-04, IM75-04, IM72-06, IM68-06, IM67-06, IM66-06, IM65-06, IM64-06, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, ZZ99-
17 | ANAD |  |  | CVP06-MD-D001 (9ZI03AC17) | 1HFE54AA101 , Near Mill D @ 17.75m | CVP06 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 154 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC19-03, BC18-03, BC17-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
18 | ANAD |  |  | CVP06-MD-D002 (9ZI03AC18) | 1HFE64AA101 , Near Mill D @ 17.75m | CVP06 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 154 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC19-03, BC18-03, BC17-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
19 | ANAD |  |  | CVP06-MD-D003 (9ZI03AC19) | 1HFE53AA101 , Near Mill C @ 17.75m | CVP06 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 176 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC13-03, BC12-03, BC11-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
20 | ANAD |  |  | CVP06-MD-D004 (9ZI03AC20) | 1HFE63AA101 , Near Mill C @ 17.75m | CVP06 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 176 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC13-03, BC12-03, BC11-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
21 | ANAD |  |  | CVP07-MD-D001 (9ZI03AC21) | 1HFE56AA101 , Near Mill F @ 17.75m | CVP07 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 153 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC22-03, BC21-03, BC20-03, BC17-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
22 | ANAD |  |  | CVP07-MD-D002 (9ZI03AC22) | 1HFE66AA101 , Near Mill F @ 17.75m | CVP07 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 204 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC22-03, BC21-03, BC20-03, BC17-03, BC08-03, BC07-03, BC06-03, BC05-03, BC04-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
23 | ANAD |  |  | CVP07-MD-D003 (9ZI03AC23) | 1HFE55AA101 , Near Mill E @ 17.75m | CVP07 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 155 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC21-03, BC20-03, BC17-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
24 | ANAD |  |  | CVP07-MD-D004 (9ZI03AC24) | 1HFE65AA101 , Near Mill E @ 17.75m | CVP07 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 155 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BC21-03, BC20-03, BC17-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, ZZ99-
25 | ANAD |  |  | CVP09-MD-D001 (9ZI03AC25) | 1HAN31AA101 , El: 21 mtr, Row: B-C BAY, Col: 4-5 | CVP09 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 169 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TD37-03, TD36-03, TD35-03, TR41-03, TR28-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC87-03, CC44-03, CC45-03, ZZ99-
26 | ANAD |  |  | CVP09-MD-D002 (9ZI03AC26) | 1LAB60AA102 , El: 15.5 mtr, Row: C, Col: 6 | CVP09 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 117 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC87-03, CC44-03, CC45-03, ZZ99-
27 | ANAD |  |  | CVP09-MD-D003 (9ZI03AC27) | 1LAB60AA103 , El: 15.5 mtr, Row: C, Col: 6 | CVP09 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 117 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC87-03, CC44-03, CC45-03, ZZ99-
28 | ANAD |  |  | CVP09-MD-D004 (9ZI03AC28) | 1LAB10AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 4-5 | CVP09 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 138 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC87-03, CC44-03, CC45-03, ZZ99-
29 | ANAD |  |  | CVP09-MD-D005 (9ZI03AC29) | 1LAB20AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 5-7 | CVP09 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC87-03, CC44-03, CC45-03, ZZ99-
30 | ANAD |  |  | CVP09-MD-D006 (9ZI03AC30) | 1LAB30AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 6-8 | CVP09 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC87-03, CC44-03, CC45-03, ZZ99-
31 | ANAD |  |  | CVP10-MD-D001 (9ZI03AC31) | 1HBK12AA101 , Near S11L @ 20.3m | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 125 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
32 | ANAD |  |  | CVP10-MD-D002 (9ZI03AC32) | 1HBK14AA101 , Near S9R @ 20.3m | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD07-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
33 | ANAD |  |  | CVP10-MD-D003 (9ZI03AC33) | 1LAE40AA101 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
34 | ANAD |  |  | CVP10-MD-D004 (9ZI03AC34) | 1LAE40AA102 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
35 | ANAD |  |  | CVP10-MD-D005 (9ZI03AC35) | 1LAE40AA103 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
36 | ANAD |  |  | CVP10-MD-D006 (9ZI03AC36) | 1LAE40AA104 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
37 | ANAD |  |  | CVP10-MD-D007 (9ZI03AC37) | 1HBK11AA101 , Near S9L @ 20.3m | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 87 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD10-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
38 | ANAD |  |  | CVP10-MD-D008 (9ZI03AC38) | 1HBK13AA101 , Near S11R @ 20.3M | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 94 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD11-03, BD10-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03, ZZ99-
39 | ANAD |  |  | CVP10-MD-D009 (9ZI03AC39) | 1LAE30AA101 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC51-04, CC70-04, CC45-03, ZZ99-
40 | ANAD |  |  | CVP10-MD-D010 (9ZI03AC40) | 1LAE30AA102 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC51-04, CC70-04, CC45-03, ZZ99-
41 | ANAD |  |  | CVP10-MD-D011 (9ZI03AC41) | 1LAE30AA103 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC51-04, CC70-04, CC45-03, ZZ99-
42 | ANAD |  |  | CVP10-MD-D012 (9ZI03AC42) | 1LAE30AA104 , EL: 21.0mtr, NEAR SH/RH CNTRL STN | CVP10 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , BD03-03, BD02-03, BD01-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-07, CC51-04, CC70-04, CC45-03, ZZ99-
43 | ANAD |  |  | CVP11-MD-D001 (9ZI03AC43) | 1LAA10AA001 , El: 21 mtr, Row: C, Col: 6 | CVP11 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 170 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TD39-03, TD38-03, TD37-03, TD36-03, TD35-03, TR41-03, TR28-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
44 | ANAD |  |  | CVP11-MD-D002 (9ZI03AC44) | 1LBG20AA101 , El: 15.5 mtr, Row: C, Col: 3 | CVP11 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 138 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP18-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
45 | ANAD |  |  | CVP11-MD-D003 (9ZI03AC45) | 1LCA42AA101 , El: 0 mtr, Row: Near B, Col: 4 | CVP11 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TG07-04, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
46 | ANAD |  |  | CVP11-MD-D004 (9ZI03AC46) | 1LCA40AA101 , El: 0 mtr, Row: Near B, Col: 4 | CVP11 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TG07-04, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
47 | ANAD |  |  | CVP11-MD-D005 (9ZI03AC47) | 1LCA41AA101 , El: 0 mtr, Row: Near B, Col: 4 | CVP11 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TG07-04, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
48 | ANAD |  |  | CVP11-MD-D006 (9ZI03AC48) | 1LBS50AA101 , El: 21 mtr, Row: C, Col: 6 | CVP11 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 170 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TD39-03, TD38-03, TD37-03, TD36-03, TD35-03, TR41-03, TR28-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
49 | ANAD |  |  | CVP12-MD-D001 (9ZI03AC49) | 1LCR56AA101 , El: 0 mtr, NEAR DM WTR TNK (OUTSIDE TG BLDG) | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 375 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-03, CC41-03, ZZ99-
50 | ANAD |  |  | CVP12-MD-D002 (9ZI03AC50) | 1LCR56AA102 , El: 0 mtr, NEAR DM WTR TNK (OUTSIDE TG BLDG) | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 375 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-03, CC41-03, ZZ99-
51 | ANAD |  |  | CVP12-MD-D003 (9ZI03AC51) | 1LCA31AA101 , El: 0 mtr, Row: Near B, Col: 4 | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | MODE | ZZ99- , TG07-04, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
52 | ANAD |  |  | CVP12-MD-D004 (9ZI03AC52) | 1LCH11AA101 , El: 9 mtr, Row: p, Col: 5 | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 195 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
53 | ANAD |  |  | CVP12-MD-D005 (9ZI03AC53) | 1LCH12AA101 , El: 9 mtr, Row: p, Col: 5 | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 195 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
54 | ANAD |  |  | CVP12-MD-D006 (9ZI03AC54) | 1LCH13AA101 , El: 9 mtr, Row: p, Col: 5 | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 195 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
55 | ANAD |  |  | CVP12-MD-D007 (9ZI03AC55) | 1LCH22AA101 , El: 9 mtr, Row: p, Col: 5 | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 195 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
56 | ANAD |  |  | CVP12-MD-D008 (9ZI03AC56) | 1LCH23AA101 , El: 9 mtr, Row: p, Col: 5 | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 195 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
57 | ANAD |  |  | CVP12-MD-D009 (9ZI03AC57) | 1LCA33AA101 , El: 0 mtr, Row: Near B, Col: 4 | CVP12 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TG07-04, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
58 | ANAD |  |  | CVP13-MD-D001 (9ZI03AC58) | 1LCJ10AA101 , El: 9 mtr, Row: p, Col: 4 | CVP13 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 202 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
59 | ANAD |  |  | CVP13-MD-D002 (9ZI03AC59) | 1LCJ11AA101 , El: 9 mtr, Row: p, Col: 4 | CVP13 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 202 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
60 | ANAD |  |  | CVP13-MD-D003 (9ZI03AC60) | 1LCJ20AA101 , El: 9 mtr, Row: p, Col: 4 | CVP13 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 202 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
61 | ANAD |  |  | CVP13-MD-D004 (9ZI03AC61) | 1LCJ20AA102 , El: 9 mtr, Row: p, Col: 4 | CVP13 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 202 | [5 empty] | CONTROL AND MONITORING | MOD | ZZ99- , TP41-03, TP40-03, TP35-03, TP34-03, TP32-03, TP31-03, TP30-03, TP29-03, TP28-03, TP27-03, TP22-03, TP20-02, TP21-02, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
62 | ANAD |  |  | CVP14-MD-D001 (9ZI03AC62) | 1LFN21AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 2-3 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 158 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
63 | ANAD |  |  | CVP14-MD-D002 (9ZI03AC63) | 1LFN22AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 2-3 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 158 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
64 | ANAD |  |  | CVP14-MD-D003 (9ZI03AC64) | 1LFN31AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 2-3 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 158 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
65 | ANAD |  |  | CVP14-MD-D004 (9ZI03AC65) | 1LFN32AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 2-3 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 161 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
66 | ANAD |  |  | CVP14-MD-D005 (9ZI03AC66) | 1LFN51AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 2-3 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 161 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
67 | ANAD |  |  | CVP14-MD-D006 (9ZI03AC67) | 1LFN52AA101 , El: 0.0 mtr, Row: B-C BAY, Col: 2-3 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 161 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
68 | ANAD |  |  | CVP14-MD-D007 (9ZI03AC68) | 1LFN61AA101 , El: 21 mtr, Row: B-C BAY, Col: 7-8 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 141 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TR40-03, TR26-03, TP04-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
69 | ANAD |  |  | CVP14-MD-D008 (9ZI03AC69) | 1LFN62AA101 , El: 21 mtr, Row: B-C BAY, Col: 7-8 | CVP14 , EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 141 | [5 empty] | CONTROL AND MONITORING | ASC | ZZ99- , TR40-03, TR26-03, TP04-03, TP03-03, TP02-03, TP01-03, TR23-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03, ZZ99-
1 | BID |  |  | CVP01-BD-D001 (9ZI04AC01) | 1HTA10AA101, Near X1 @ 20.0m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 112 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD04-03, BD05-03, BD06-03, BD07-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03
2 | BID |  |  | CVP01-BD-D002 (9ZI04AC02) | 1HTA20AA201, Near V8 @ 20.0m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 132 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD21-02, BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03
3 | BID |  |  | CVP01-BD-D003 (9ZI04AC03) | 1HTA30AA001, Near Y2 @ 20.0m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 129 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
4 | BID |  |  | CVP01-BD-D004 (9ZI04AC04) | 1HTA30AA201, Near Y2 @ 20.0m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 129 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
5 | BID |  |  | CVP01-BD-D005 (9ZI04AC05) | 1HNC01AA201, Near V1 @ 3.4m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 180 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA35-02, BR35-03, BA09-03, BA08-03, BA07-03, BA05-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
6 | BID |  |  | CVP01-BD-D006 (9ZI04AC06) | 1HTA10AA201, Near X1 @ 20.0m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 114 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD04-03, BD05-03, BD06-03, BD07-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
7 | BID |  |  | CVP01-BD-D007 (9ZI04AC07) | 1HTA20AA001, Near V8 @ 20.0m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 135 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD21-02, BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
8 | BID |  |  | CVP01-BD-D008 (9ZI04AC08) | 1HNA44AA001, Near P7 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 124 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
9 | BID |  |  | CVP01-BD-D009 (9ZI04AC09) | 1HNA44AA002, Near R7 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD23-02, BD22-02, BD21-02, BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
10 | BID |  |  | CVP01-BD-D010 (9ZI04AC10) | 1HNC01AA001, Near T2 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD10-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
11 | BID |  |  | CVP01-BD-D011 (9ZI04AC11) | 1HNC01AA003, Near T2 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 102 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD12-03, BD11-03, BD10-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
12 | BID |  |  | CVP01-BD-D012 (9ZI04AC12) | 1HNA42AA001, Near P3 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 150 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD26-03, BD27-03, BD28-03, BD29-03, BR43-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
13 | BID |  |  | CVP01-BD-D013 (9ZI04AC13) | 1HNA42AA002, Near R3 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 144 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD27-03, BD28-03, BD29-03, BR43-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
14 | BID |  |  | CVP01-BD-D014 (9ZI04AC14) | 1HNA43AA001, Near P6 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 117 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
15 | BID |  |  | CVP01-BD-D015 (9ZI04AC15) | 1HNA43AA002, Near R5 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 129 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
16 | BID |  |  | CVP01-BD-D016 (9ZI04AC16) | 1HLB01AA001, Near FH7L @ 3.5m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 175 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA35-02, BR35-03, BA09-03, BA08-03, BA07-03, BA05-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
17 | BID |  |  | CVP01-BD-D017 (9ZI04AC17) | 1HLB10AA001, Near FH7L @ 3.5m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 175 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA35-02, BR35-03, BA09-03, BA08-03, BA07-03, BA05-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
18 | BID |  |  | CVP01-BD-D018 (9ZI04AC18) | 1HNA41AA001, Near P2 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 91 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD10-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
19 | BID |  |  | CVP01-BD-D019 (9ZI04AC19) | 1HNA41AA002, Near R1 @ 20.3m | CVP01, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 102 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD12-03, BD11-03, BD10-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
34 | BID |  |  | CVP02-BD-D001 (9ZI04AC34) | 1HNC02AA201, Near V8 @ 3.4m | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 88 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
35 | BID |  |  | CVP02-BD-D002 (9ZI04AC35) | 1HLB02AA001, Near FH7R @ 3.5m | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 186 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA33-02, BA30-03, BR34-04, BA15-04, BA14-04, BA16-03, BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
36 | BID |  |  | CVP02-BD-D003 (9ZI04AC36) | 1HLB20AA001, Near FH7R @ 3.5m | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 186 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA33-02, BA30-03, BR34-04, BA15-04, BA14-04, BA16-03, BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
37 | BID |  |  | CVP02-BD-D004 (9ZI04AC37) | 1HNC02AA001, Near T6 @ 20.3m | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD23-02, BD22-02, BD21-02, BD20-03, BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
38 | BID |  |  | CVP02-BD-D005 (9ZI04AC38) | 1HNC02AA003, Near V8 @ 3.4m | CVP02, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 88 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03
47 | BID |  |  | CVP03-BD-D001 (9ZI04AC47) | 1HBK60AA001, Near S21 @ 36.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 178 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BI07-02, BI08-02, BI14-01, BI15-01, BI16-01, BI20-03, BI21-03, BI22-03, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
48 | BID |  |  | CVP03-BD-D002 (9ZI04AC48) | 1HLA30AA001, Near S23 @ 22.5m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 156 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD26-03, BD27-03, BD28-03, BD29-03, BR43-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
49 | BID |  |  | CVP03-BD-D003 (9ZI04AC49) | 1HLA30AA201, Near S23 @ 22.5m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 156 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD26-03, BD27-03, BD28-03, BD29-03, BR43-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
50 | BID |  |  | CVP03-BD-D004 (9ZI04AC50) | 1HNA15AA001, Near S20 @ 36.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 176 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BI05-01, BI04-01, BI17-03, BI18-03, BI19-03, BI20-03, BI21-03, BI22-03, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
51 | BID |  |  | CVP03-BD-D005 (9ZI04AC51) | 1HNA30AA001, Near S16L @ 24.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 141 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
52 | BID |  |  | CVP03-BD-D006 (9ZI04AC52) | 1HAS10AA001, Near S21 @ 35.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 185 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BH05-01, BH04-02, BH03-01, BH02-01, BR49-03, BR48-03, BR46-03, BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
53 | BID |  |  | CVP03-BD-D007 (9ZI04AC53) | 1HFE30AA201, Near S16L @ 23.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 156 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
54 | BID |  |  | CVP03-BD-D008 (9ZI04AC54) | 1HLA10AA003, Near S26L @ 5.4m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 196 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA32-01, BA31-02, BA30-03, BR34-04, BA15-04, BA14-04, BA16-03, BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
55 | BID |  |  | CVP03-BD-D009 (9ZI04AC55) | 1HLA10AA004, Near S26L @ 8.3m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA12-03, BA11-03, BA10-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
56 | BID |  |  | CVP03-BD-D010 (9ZI04AC56) | 1HAS10AA002, Near S21 @ 34.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 158 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BH07-01, BR51-03, BG21-03, BG20-03, BG15-03, BR47-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
57 | BID |  |  | CVP03-BD-D011 (9ZI04AC57) | 1HFE10AA001, Near FH6L @ 3.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 186 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA35-02, BR35-03, BA09-03, BA08-03, BA07-03, BA05-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
58 | BID |  |  | CVP03-BD-D012 (9ZI04AC58) | 1HFE30AA001, Near S26L @ 8.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA12-03, BA11-03, BA10-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
59 | BID |  |  | CVP03-BD-D013 (9ZI04AC59) | 1HFE30AA002, Near S16L @ 23.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 156 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
60 | BID |  |  | CVP03-BD-D014 (9ZI04AC60) | 1HFE10AA101, Near FH6L @ 3.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 186 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA35-02, BR35-03, BA09-03, BA08-03, BA07-03, BA05-03, BA04-03, BA03-03, BA02-03, BA01-03, BR16-03, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
61 | BID |  |  | CVP03-BD-D015 (9ZI04AC61) | 1HLA10AA002, Near S26L @ 5.4m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 196 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA32-01, BA31-02, BA30-03, BR34-04, BA15-04, BA14-04, BA16-03, BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
62 | BID |  |  | CVP03-BD-D016 (9ZI04AC62) | 1HNA15AA201, Near S20 @ 36.0m | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 176 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BI05-01, BI04-01, BI17-03, BI18-03, BI19-03, BI20-03, BI21-03, BI22-03, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
78 | BID |  |  | CVP04-BD-D001 (9ZI04AC78) | 1HBK65AA001, Near S21 @ 36.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 178 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BI07-02, BI08-02, BI14-01, BI15-01, BI16-01, BI20-03, BI21-03, BI22-03, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
79 | BID |  |  | CVP04-BD-D002 (9ZI04AC79) | 1HLA40AA001, Near S3 @ 22.5m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
80 | BID |  |  | CVP04-BD-D003 (9ZI04AC80) | 1HLA40AA201, Near S3 @ 22.5m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 135 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD19-03, BD18-03, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-04, CC30-03
81 | BID |  |  | CVP04-BD-D004 (9ZI04AC81) | 1HNA25AA001, Near S20 @ 36.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 182 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BI05-01, BI04-01, BI17-03, BI18-03, BI19-03, BI20-03, BI21-03, BI22-03, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-04, CC30-03
82 | BID |  |  | CVP04-BD-D005 (9ZI04AC82) | 1HNA35AA001, Near S16R @ 24.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 119 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-04, CC30-03
83 | BID |  |  | CVP04-BD-D006 (9ZI04AC83) | 1HAS20AA001, Near S21 @ 35.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 163 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BH13-02, BH12-02, BH11-02, BH10-01, BR50-03, BR47-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
84 | BID |  |  | CVP04-BD-D007 (9ZI04AC84) | 1HFE40AA201, Near S16R @ 23.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 138 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BE08-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
85 | BID |  |  | CVP04-BD-D008 (9ZI04AC85) | 1HLA20AA003, Near S26R @ 5.4m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 197 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA33-02, BA30-03, BR34-04, BA15-04, BA14-04, BA16-03, BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
86 | BID |  |  | CVP04-BD-D009 (9ZI04AC86) | 1HLA20AA004, Near S26R @ 8.3m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 154 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA16-03, BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
87 | BID |  |  | CVP04-BD-D010 (9ZI04AC87) | 1HAS20AA002, Near S21 @ 34.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BH07-01, BR51-03, BG21-03, BG20-03, BG15-03, BR47-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
88 | BID |  |  | CVP04-BD-D011 (9ZI04AC88) | 1HFE20AA001, Near FH6R @ 3.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA34-02, BR33-03, BA23-03, BA22-03, BA21-03, BA20-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
89 | BID |  |  | CVP04-BD-D012 (9ZI04AC89) | 1HFE40AA001, Near S26R @ 8.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 141 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
90 | BID |  |  | CVP04-BD-D013 (9ZI04AC90) | 1HFE40AA002, Near S16R @ 23.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 138 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BE08-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
91 | BID |  |  | CVP04-BD-D014 (9ZI04AC91) | 1HFE20AA101, Near FH6R @ 3.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA34-02, BR33-03, BA23-03, BA22-03, BA21-03, BA20-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
92 | BID |  |  | CVP04-BD-D015 (9ZI04AC92) | 1HLA20AA002, Near S26R @ 5.4m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 197 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BA33-02, BA30-03, BR34-04, BA15-04, BA14-04, BA16-03, BA17-03, BA18-03, BA19-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
93 | BID |  |  | CVP04-BD-D016 (9ZI04AC93) | 1HNA25AA201, Near S20 @ 36.0m | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 182 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BI05-01, BI04-01, BI17-03, BI18-03, BI19-03, BI20-03, BI21-03, BI22-03, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC67-02, CC30-03
109 | BID |  |  | CVP05-BD-D001 (9ZI04BC10) | 1HFX02AA001, Near Mills | CVP05, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 234 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , IC32-04, IC30-04, IR13-03, IC29-04, IR12-04, IC28-04, IC27-04, IR11-04, IC26-04, IC25-04, IC24-04, IR09-04, IC13-04, IC12-04, IC11-04, IC10-04, IC09-04, IC08-04, IR08-04, IC07-R4, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03
110 | BID |  |  | CVP05-BD-D002 (9ZI04BC11) | 1HFX01AA001, Near Mills | CVP05, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 248 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , IC37-04, IC35-04, IR14-03, IC34-04, IC33-04, IC29-04, IR12-04, IC28-04, IC27-04, IR11-04, IC26-04, IC25-04, IC24-04, IR09-04, IC13-04, IC12-04, IC11-04, IC10-04, IC09-04, IC08-04, IR08-04, IC07-R4, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC82-03, CC31-01, CC30-03
111 | BID |  |  | CVP06-BD-D001 (9ZI04BC12) | 1HFX04AA001, Near Mills | CVP06, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 260 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , IC43-04, IC41-04, IR15-03, IC40-04, IC39-04, IC38-04, IC34-04, IC33-04, IC29-04, IR12-04, IC28-04, IC27-04, IR11-04, IC26-04, IC25-04, IC24-04, IR09-04, IC13-04, IC12-04, IC11-04, IC10-04, IC09-04, IC08-04, IR08-04, IC07-R4, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC84-04, CC86-04, CC87-03, CC44-03
112 | BID |  |  | CVP06-BD-D002 (9ZI04BC13) | 1HFX03AA001, Near Mills | CVP06, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 251 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , IM93-03, IM91-03, IM90-03, IR35-03, IM89-03, IM88-03, IM87-04, IM86-04, IM85-04, IM80-04, IM79-04, IR32-04, IM78-04, IM77-04, IM76-04, IR28-04, IM75-04, IM72-06, IM68-06, IM67-06, IM66-06, IM65-06, IM64-06, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01, CC69-02, CC44-03
113 | BID |  |  | CVP07-BD-D001 (9ZI04BC14) | 1HFX06AA001, Near Mills | CVP07, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 238 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , IM98-03, IM97-03, IR34-03, IM87-04, IM86-04, IM85-04, IM80-04, IM79-04, IR32-04, IM78-04, IM77-04, IM76-04, IR28-04, IM75-04, IM72-06, IM68-06, IM67-06, IM66-06, IM65-06, IM64-06, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01, CC69-02, CC44-03
114 | BID |  |  | CVP07-BD-D002 (9ZI04BC15) | 1HFX05AA001, Near Mills | CVP07, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 225 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , IM83-03, IM82-03, IM81-03, IR33-03, IM80-04, IM79-04, IR32-04, IM78-04, IM77-04, IM76-04, IR28-04, IM75-04, IM72-06, IM68-06, IM67-06, IM66-06, IM65-06, IM64-06, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01, CC69-02, CC44-03
115 | BID |  |  | CVP08-BD-D001 (9ZI04BC16) | 1HAN20AA011, EL: 56.85 mtr, Near S10R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
116 | BID |  |  | CVP08-BD-D002 (9ZI04BC17) | 1HAN37AA002, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 110 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC34-03, CC68-02, CC69-02, CC45-03
117 | BID |  |  | CVP08-BD-D003 (9ZI04BC18) | 1HAN20AA007, EL. 60.4M BETWEEN S10R & S13R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP08-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
118 | BID |  |  | CVP08-BD-D004 (9ZI04BC19) | 1HAN20AA008, EL: 56.85 mtr, Near S10R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
119 | BID |  |  | CVP08-BD-D005 (9ZI04BC20) | 1HAN20AA009, EL: 56.85 mtr, Near S10L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 162 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
120 | BID |  |  | CVP08-BD-D006 (9ZI04BC21) | 1HAN20AA010, EL: 56.85 mtr, Near S10R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
121 | BID |  |  | CVP08-BD-D007 (9ZI04BC22) | 1HAN20AA003, EL. 60.4M BETWEEN S10L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 171 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP01-03, BR70-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
122 | BID |  |  | CVP08-BD-D008 (9ZI04BC23) | 1HAN20AA004, EL. 60.4M BETWEEN S10L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 171 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP01-03, BR70-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
123 | BID |  |  | CVP08-BD-D009 (9ZI04BC24) | 1HAN20AA005, EL. 60.4M BETWEEN S10R & S13R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP08-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
124 | BID |  |  | CVP08-BD-D010 (9ZI04BC25) | 1HAN20AA006, EL. 60.4M BETWEEN S10R & S13R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP08-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
125 | BID |  |  | CVP08-BD-D011 (9ZI04BC26) | 1HAN15AA005, EL.20.7M, NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 104 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
126 | BID |  |  | CVP08-BD-D012 (9ZI04BC27) | 1HAN15AA006, EL.20.7M, NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 104 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
127 | BID |  |  | CVP08-BD-D013 (9ZI04BC28) | 1HAN20AA001, EL.60.4M, NEAR S10L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 171 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP01-03, BR70-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
128 | BID |  |  | CVP08-BD-D014 (9ZI04BC29) | 1HAN20AA002, EL.16.6M, NEAR S11R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 105 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
129 | BID |  |  | CVP08-BD-D015 (9ZI04BC30) | 1HAN15AA001, EL.60.4M, NEAR S10L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 171 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP01-03, BR70-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
130 | BID |  |  | CVP08-BD-D016 (9ZI04BC31) | 1HAN15AA002, EL.60.4M, NEAR S10R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP07-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
131 | BID |  |  | CVP08-BD-D017 (9ZI04BC32) | 1HAN15AA003, EL.3.5M, NEAR S3L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 152 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BR33-03, BA23-03, BA22-03, BA21-03, BA20-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
132 | BID |  |  | CVP08-BD-D018 (9ZI04BC33) | 1HAN15AA004, EL.20.7M, NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 104 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
133 | BID |  |  | CVP08-BD-D019 (9ZI04BC34) | 1LBC12AA001, El: 0 mtr, Row: B/w A&B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 110 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC34-03, CC68-02, CC69-02, CC45-03
134 | BID |  |  | CVP08-BD-D020 (9ZI04BC35) | 1HAN36AA002, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 110 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC34-03, CC68-02, CC69-02, CC45-03
135 | BID |  |  | CVP08-BD-D021 (9ZI04BC36) | 1LBB12AA001, El: 56.85 mtr, Row: S4L&S5L, Col: S1L&S9L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 179 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO02-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
136 | BID |  |  | CVP08-BD-D022 (9ZI04BC37) | 1LBB22AA001, El: 56.85 mtr, Row: S4R&S5R, Col: S1R&S9R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 155 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
137 | BID |  |  | CVP08-BD-D023 (9ZI04BC38) | 1LBA20AA002, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
138 | BID |  |  | CVP08-BD-D024 (9ZI04BC39) | 1LBA22AA001, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
139 | BID |  |  | CVP08-BD-D025 (9ZI04BC40) | 1LBA10AA001, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
140 | BID |  |  | CVP08-BD-D026 (9ZI04BC41) | 1LBA10AA002, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
141 | BID |  |  | CVP08-BD-D027 (9ZI04BC42) | 1LBA12AA001, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 110 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC34-03, CC68-02, CC69-02, CC45-03
142 | BID |  |  | CVP08-BD-D028 (9ZI04BC43) | 1LBA20AA001, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 110 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC34-03, CC68-02, CC69-02, CC45-03
143 | BID |  |  | CVP08-IN-D001 (9ZI04BC44) | 1HAN15AA051, EL. 3.5M NEAR S3L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 152 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BR33-03, BA23-03, BA22-03, BA21-03, BA20-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
144 | BID |  |  | CVP08-IN-D002 (9ZI04BC45) | 1HAN15AA051, EL. 3.5M NEAR S3L | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 134 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BR33-03, BA23-03, BA22-03, BA21-03, BA20-03, BA29-03, BA28-03, BA27-03, BA26-03, BA25-03, BR01-03, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
145 | BID |  |  | CVP08-IN-D003 (9ZI04BC46) | 1HAN15AA053, EL. 20.7M NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 104 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, LR10-R4, LV77-04, LR06-02, CC91-02, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
146 | BID |  |  | CVP08-IN-D004 (9ZI04BC47) | 1HAN15AA053, EL. 20.7M NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
147 | BID |  |  | CVP08-IN-D005 (9ZI04BC48) | 1HAN15AA054, EL. 20.7M NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 83 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
148 | BID |  |  | CVP08-IN-D006 (9ZI04BC49) | 1HAN15AA054, EL. 20.7M NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
149 | BID |  |  | CVP08-IN-D007 (9ZI04BC50) | 1HAN20AA051, EL. 16.6M NEAR S11R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
150 | BID |  |  | CVP08-IN-D008 (9ZI04BC51) | 1HAN20AA051, EL. 16.6M NEAR S11R | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 88 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
151 | BID |  |  | CVP08-IN-D009 (9ZI04BC52) | 1HAN15AA052, EL. 20.7M NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 83 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
152 | BID |  |  | CVP08-IN-D010 (9ZI04BC53) | 1HAN15AA052, EL. 20.7M NEAR S17 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
153 | BID |  |  | CVP08-IN-D011 (9ZI04BC54) | 1LBA10AA051, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 111 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC86-04, CC87-03, CC44-03, CC45-03
154 | BID |  |  | CVP08-IN-D012 (9ZI04BC55) | 1LBA10AA051, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 110 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
155 | BID |  |  | CVP08-IN-D013 (9ZI04BC56) | 1LBA20AA051, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 111 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC86-04, CC87-03, CC44-03, CC45-03
156 | BID |  |  | CVP08-IN-D014 (9ZI04BC57) | 1LBA20AA051, El: 0 mtr, Row: B, Col: 6 | CVP08, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 110 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03
157 | BID |  |  | CVP09-BD-D001 (9ZI04BC58) | 1HAC10AA003, EL.24.2M, NEAR S12R | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 108 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BF02-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
158 | BID |  |  | CVP09-BD-D002 (9ZI04BC59) | 1HAC10AA004, EL.24.2M, NEAR S19 | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 108 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BF02-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
159 | BID |  |  | CVP09-BD-D003 (9ZI04BC60) | 1HAC10AA001, EL.24.2M, NEAR S12R | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 108 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BF02-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
160 | BID |  |  | CVP09-BD-D004 (9ZI04BC61) | 1HAC10AA002, EL.24.2M, NEAR S12R | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 108 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BF02-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03
161 | BID |  |  | CVP09-BD-D005 (9ZI04BC62) | 1LAB60AA003, El: 15.5 mtr, Row: C, Col: 6 | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 131 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC86-04, CC87-03, CC44-03, CC45-03
162 | BID |  |  | CVP09-BD-D006 (9ZI04BC63) | 1LAB60AA005, El: 15.5 mtr, Row: C, Col: 6 | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 131 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC86-04, CC87-03, CC44-03, CC45-03
163 | BID |  |  | CVP09-BD-D007 (9ZI04BC64) | 1LAB60AA013, El: 15.5 mtr, Row: C, Col: 6 | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 131 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC86-04, CC87-03, CC44-03, CC45-03
164 | BID |  |  | CVP09-BD-D008 (9ZI04BC65) | 1LAB60AA015, El: 15.5 mtr, Row: C, Col: 6 | CVP09, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 131 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC86-04, CC87-03, CC44-03, CC45-03
165 | BID |  |  | CVP10-BD-D001 (9ZI04BC66) | 1HAN35AA001, EL. 60.4M NEAR S10L & S11L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 150 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP01-03, BR70-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03
166 | BID |  |  | CVP10-BD-D002 (9ZI04BC67) | 1HAN35AA002, EL. 60.4M NEAR S10L & S11L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 150 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP01-03, BR70-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03
167 | BID |  |  | CVP10-BD-D003 (9ZI04BC68) | 1HAJ35AA001, EL.60.4M, NEAR S12R & S13R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BP09-03, BR72-03, BO09-03, BO08-03, BR69-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03
168 | BID |  |  | CVP10-BD-D004 (9ZI04BC69) | 1HAH20AA001, EL.56.8M, BETWEEN S10R & S13R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO07-03, BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03
169 | BID |  |  | CVP10-BD-D005 (9ZI04BC70) | 1HAH20AA002, EL.56.8M, BETWEEN S10R & S13R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , BO07-03, BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03
170 | BID |  |  | CVP10-IN-D001 (9ZI04BC71) | 1HAN20AA054, EL. 16.6M NEAR S11R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
171 | BID |  |  | CVP10-IN-D002 (9ZI04BC72) | 1HAN20AA054, EL. 16.6M NEAR S11R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 88 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
172 | BID |  |  | CVP10-IN-D003 (9ZI04BC73) | 1HAH20AA051, EL.56.8M, BETWEEN S10R & S13R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BO07-03, BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
173 | BID |  |  | CVP10-IN-D004 (9ZI04BC74) | 1HAH20AA051, EL.56.8M, BETWEEN S10R & S13R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BO07-03, BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
174 | BID |  |  | CVP10-IN-D005 (9ZI04BC75) | 1HAJ35AA051, EL.60.4M, NEAR S12R & S13R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BP09-03, BR72-03, BO09-03, BO08-03, BR69-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
175 | BID |  |  | CVP10-IN-D006 (9ZI04BC76) | 1HAJ35AA051, EL.60.4M, NEAR S12R & S13R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 154 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BP09-03, BR72-03, BO09-03, BO08-03, BR69-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
176 | BID |  |  | CVP10-IN-D007 (9ZI04BC77) | 1HAN20AA052, EL. 16.6M NEAR S11R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
177 | BID |  |  | CVP10-IN-D008 (9ZI04BC78) | 1HAN20AA052, EL. 16.6M NEAR S11R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 88 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
178 | BID |  |  | CVP10-IN-D009 (9ZI04BC79) | 1HAN20AA053, EL. 16.6M NEAR S11R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R4, IC01-R4, CR01-R4, CC71-07, CC52-04, CC44-03, CC45-03
179 | BID |  |  | CVP10-IN-D010 (9ZI04BC80) | 1HAN20AA053, EL. 16.6M NEAR S11R | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 88 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03
180 | BID |  |  | CVP11-BD-D001 (9ZI04BC81) | 1PCB41AA002, El: 0.0 mtr, Near ACWPs | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 115 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG85-03, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
181 | BID |  |  | CVP11-BD-D002 (9ZI04BC82) | 1LCA41AA001, El: 0 mtr, Row: Near B, Col: 4 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV42-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02
182 | BID |  |  | CVP11-BD-D003 (9ZI04BC83) | 1LCA42AA001, El: 0 mtr, Row: Near B, Col: 4 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV42-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02
183 | BID |  |  | CVP11-BD-D004 (9ZI04BC84) | 1PGL10AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 90 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
184 | BID |  |  | CVP11-BD-D005 (9ZI04BC85) | 1PCB31AA001, El: 0.0 mtr, Near ACWPs | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 115 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG85-03, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
185 | BID |  |  | CVP11-BD-D006 (9ZI04BC86) | 1PCB31AA002, El: 0.0 mtr, Near ACWPs | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 115 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG85-03, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
186 | BID |  |  | CVP11-BD-D007 (9ZI04BC87) | 1PCB41AA001, El: 0.0 mtr, Near ACWPs | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 115 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG85-03, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
187 | BID |  |  | CVP11-BD-D008 (9ZI04BC88) | 1PCA01AA001, El: 0.0 mtr, Near SCS-A, B/w A&B, Near 7 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 112 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG80-02, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02
188 | BID |  |  | CVP11-BD-D009 (9ZI04BC89) | 1PCB30AA001, El: 0.0 mtr, Near CWPs | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 148 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG76-03, TG75-03, TG74-03, TG73-03, TR16-03, TG72-03, TG71-03, TR48-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV47-05, LV28-R4, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02
189 | BID |  |  | CVP11-BD-D010 (9ZI04BC90) | 1PCB30AA002, El: 0 mtr, Row: q, Col: 8, Near ACWP | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG90-03, TR02-03, MR15-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-02, CC93-02, CC42-04, CC41-02
190 | BID |  |  | CVP11-BD-D011 (9ZI04BC91) | 1PCB30AA004, El: 0.0 mtr, Near ACWPs | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 115 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG85-03, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
191 | BID |  |  | CVP11-BD-D012 (9ZI04BC92) | 1LAB10AA001, El: 15.5 mtr, Row: B/w B-C, Col: 6 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 118 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
192 | BID |  |  | CVP11-BD-D013 (9ZI04BC93) | 1LAB10AA011, El: 15.5 mtr, Row: B/w B-C, Col: 6 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 118 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
193 | BID |  |  | CVP11-BD-D014 (9ZI04BC94) | 1LBS40AA003, El: 9mtr, Row: B/w B-C, Col: 5 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 130 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
194 | BID |  |  | CVP11-BD-D015 (9ZI04BC95) | 1LCA10AA001, El: 0 mtr, Row: Near B, Col: 4 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV42-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02
201 | BID |  |  | CVP11-IN-D001 (9ZI04CC03) | 1LBG20AA051, El: 21 mtr, Row: C, Col: 6 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 209 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TD40-03, TR44-02, TD39-03, TD38-03, TD37-03, TD36-03, TD35-03, TR41-03, TR28-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
202 | BID |  |  | CVP11-IN-D002 (9ZI04CC04) | 1LBG20AA051, El: 21 mtr, Row: C, Col: 6 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 209 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TD40-03, TR44-02, TD39-03, TD38-03, TD37-03, TD36-03, TD35-03, TR41-03, TR28-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
203 | BID |  |  | CVP11-IN-D003 (9ZI04CC05) | 1LBS51AA201, El: 21 mtr, Row: C, Col: 6 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 209 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TD40-03, TR44-02, TD39-03, TD38-03, TD37-03, TD36-03, TD35-03, TR41-03, TR28-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
204 | BID |  |  | CVP11-IN-D004 (9ZI04CC06) | 1LBS51AA201, El: 21 mtr, Row: C, Col: 6 | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 209 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TD40-03, TR44-02, TD39-03, TD38-03, TD37-03, TD36-03, TD35-03, TR41-03, TR28-03, TP17-03, TP16-03, TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
207 | BID |  |  | CVP12-BD-D001 (9ZI04CC09) | 1PGL20AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 90 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
208 | BID |  |  | CVP12-BD-D002 (9ZI04CC10) | 1LAB52AA001, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 119 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-02, CC93-02, CC42-04, CC41-02
209 | BID |  |  | CVP12-BD-D003 (9ZI04CC11) | 1LAB52AA011, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 118 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
210 | BID |  |  | CVP12-BD-D004 (9ZI04CC12) | 1LAB51AA011, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 118 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
211 | BID |  |  | CVP12-BD-D005 (9ZI04CC13) | 1PCB42AA001, El: 0.0 mtr, Near ACWPs | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
212 | BID |  |  | CVP12-BD-D006 (9ZI04CC14) | 1PCB42AA002, El: 0.0 mtr, Near ACWPs | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
213 | BID |  |  | CVP12-BD-D007 (9ZI04CC15) | 1PCB70AA001, El: 0.0 mtr, Near ACWPs | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
214 | BID |  |  | CVP12-BD-D008 (9ZI04CC16) | 1PCB30AA003, El: 0 mtr, Row: q, Col: 8, Near ACWP | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 85 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG90-03, TR02-03, MR15-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-02, CC93-02, CC42-04, CC41-02
215 | BID |  |  | CVP12-BD-D009 (9ZI04CC17) | 1PCB30AA005, El: 0.0 mtr, Near ACWPs | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
216 | BID |  |  | CVP12-BD-D010 (9ZI04CC18) | 1PCB32AA001, El: 0.0 mtr, Near ACWPs | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
217 | BID |  |  | CVP12-BD-D011 (9ZI04CC19) | 1PCB32AA002, El: 0.0 mtr, Near ACWPs | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
218 | BID |  |  | CVP12-BD-D012 (9ZI04CC20) | 1LAB53AA001, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 118 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
219 | BID |  |  | CVP12-BD-D013 (9ZI04CC21) | 1LAB51AA001, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 118 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
220 | BID |  |  | CVP12-BD-D014 (9ZI04CC22) | 1PCA02AA001, El: 0.0 mtr, Near SCS-B, B/w A&B, Near 7 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 109 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG83-02, TG82-04, MR17-06, MV99-05, MV03-R2, MV04-R2, MV05-R2, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02
221 | BID |  |  | CVP12-BD-D015 (9ZI04CC23) | 1LBQ54AA001, El: 4.5mtr, Row: AB, Col: 4-5 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV42-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC86-04, CC87-03, CC43-04, CC41-02
222 | BID |  |  | CVP12-BD-D016 (9ZI04CC24) | 1LBQ60AA301, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 114 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-02, CC93-02, CC42-04, CC41-02
223 | BID |  |  | CVP12-BD-D017 (9ZI04CC25) | 1LBQ62AA001, El: 0mtr, Row: B, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 103 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR20-03, TG58-03, TG59-03, TG60-03, TG61-03, TG63-03, TR18-03, TG66-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
224 | BID |  |  | CVP12-BD-D018 (9ZI04CC26) | 1LCA20AA001, El: 0 mtr, Row: Near B, Col: 4 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
225 | BID |  |  | CVP12-BD-D019 (9ZI04CC27) | 1LAB42AA001, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-02
226 | BID |  |  | CVP12-BD-D020 (9ZI04CC28) | 1LAB42AA011, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02
227 | BID |  |  | CVP12-BD-D021 (9ZI04CC29) | 1LAB43AA001, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02
228 | BID |  |  | CVP12-BD-D022 (9ZI04CC30) | 1LBQ50AA001, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02
229 | BID |  |  | CVP12-BD-D023 (9ZI04CC31) | 1LAB20AA001, El: 15.5 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TD02-01, TD01-01, TR26-03, TP04-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02
230 | BID |  |  | CVP12-BD-D024 (9ZI04CC32) | 1LAB20AA011, El: 15.5 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02
231 | BID |  |  | CVP12-BD-D025 (9ZI04CC33) | 1LAB41AA001, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02
232 | BID |  |  | CVP12-BD-D026 (9ZI04CC34) | 1LAB41AA011, El: 9 mtr, Row: B/w B-C, Col: 6 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 133 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02
240 | BID |  |  | CVP12-IN-D002 (9ZI04CC42) | 1LCA32AA051, El: 0 mtr, Row: Near B, Col: 4 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
241 | BID |  |  | CVP12-IN-D003 (9ZI04CC43) | 1LCA43AA051, El: 0 mtr, Row: Near B, Col: 4 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
242 | BID |  |  | CVP12-IN-D004 (9ZI04CC44) | 1LCA43AA051, El: 0 mtr, Row: Near B, Col: 4 | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 113 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03
243 | BID |  |  | CVP12-IN-D005 (9ZI04CC45) | 1LCR56AA511, El: 0 mtr, NEAR DM WTR TNK (OUTSIDE TG BLDG) | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 372 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01, CC41-03
244 | BID |  |  | CVP12-IN-D006 (9ZI04CC46) | 1LCR56AA511, El: 0 mtr, NEAR DM WTR TNK (OUTSIDE TG BLDG) | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 372 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , IM31-04, IM30-04, IM29-04, IM28-04, IM27-04, IM26-04, IM25-04, IM24-04, IM23-04, IM22-04, IM21-R5, IM20-R5, IM19-R5, IM18-R5, IM17-R5, IM16-R5, IM15-R5, IM14-R5, IM13-R5, IM12-R7, IM11-R7, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-01, CC41-03
247 | BID |  |  | CVP13-BD-D001 (9ZI04CC49) | 1PGL30AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
248 | BID |  |  | CVP13-BD-D002 (9ZI04CC50) | 1LCA40AA301, El: 9 mtr, Row: p, Col: 4 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 179 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG48-03, TG43-03, TG38-04, TG37-04, TG36-04, TG30-04, TG29-04, TR05-04, TG28-04, TG27-04, TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV42-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC67-02, CC35-03, CC59-05, CC40-01
249 | BID |  |  | CVP13-BD-D003 (9ZI04CC51) | 1LCA60AA001, El: 9 mtr, Row: B/w B-C, Col: 4 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 127 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
250 | BID |  |  | CVP13-BD-D004 (9ZI04CC52) | 1LCA60AA002, El: 9 mtr, Row: B/w B-C, Col: 5 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
251 | BID |  |  | CVP13-BD-D005 (9ZI04CC53) | 1LCA70AA001, El: 9 mtr, Row: B/w B-C, Col: 5 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
252 | BID |  |  | CVP13-BD-D006 (9ZI04CC54) | 1LBS31AA301, El: 9 mtr, Row: B/w B-C, Col: 5 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 158 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
253 | BID |  |  | CVP13-BD-D007 (9ZI04CC55) | 1LCA50AA001, El: 9 mtr, Row: B/w B-C, Col: 4 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 127 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
254 | BID |  |  | CVP13-BD-D008 (9ZI04CC56) | 1LCA50AA002, El: 9 mtr, Row: B/w B-C, Col: 4 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 127 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
255 | BID |  |  | CVP13-BD-D009 (9ZI04CC57) | 1LCA53AA001, El: 9 mtr, Row: p, Col: 4 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 179 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG48-03, TG43-03, TG38-04, TG37-04, TG36-04, TG30-04, TG29-04, TR05-04, TG28-04, TG27-04, TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV42-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC31-01, CC67-02, CC35-03, CC59-05, CC40-01
256 | BID |  |  | CVP13-BD-D010 (9ZI04CC58) | 1PAB10AA001, El: 0.0 mtr, Near CWPs | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 200 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR11-02, TG46-02, TG45-02, TG44-02, TG43-03, TG38-04, TG37-04, TG36-04, TG30-04, TG29-04, TR05-04, TG28-04, TG27-04, TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV42-04, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
257 | BID |  |  | CVP13-BD-D011 (9ZI04CC59) | 1PAB20AA001, El: 0.0 mtr, Near CWPs | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 142 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG76-03, TG75-03, TG74-03, TG73-03, TR16-03, TG72-03, TG71-03, TR48-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
258 | BID |  |  | CVP13-BD-D012 (9ZI04CC60) | 1PAB10AA002, El: 0.0 mtr, Near CWPs | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 180 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TR11-02, TG46-02, TG45-02, TG44-02, TG43-03, TG38-04, TG37-04, TG36-04, TG30-04, TG29-04, TR05-04, TG28-04, TG27-04, TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
259 | BID |  |  | CVP13-BD-D013 (9ZI04CC61) | 1LBS21AA001, El: 9mtr, Row: B/w B-C, Col: 5 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 158 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
260 | BID |  |  | CVP13-BD-D014 (9ZI04CC62) | 1LAB30AA001, El: 15.5 mtr, Row: B/w B-C, Col: 6 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
261 | BID |  |  | CVP13-BD-D015 (9ZI04CC63) | 1LAB30AA011, El: 15.5 mtr, Row: B/w B-C, Col: 6 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 146 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TP08-03, TP06-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
262 | BID |  |  | CVP13-BD-D016 (9ZI04CC64) | 1PAB20AA002, El: 0.0 mtr, Near CWPs | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 138 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG76-03, TG75-03, TG74-03, TG73-03, TR16-03, TG72-03, TG71-03, TR48-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV47-05, LV28-R4, LV27-R4, LV26-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
271 | BID |  |  | CVP13-IN-D001 (9ZI04CC73) | 1LCA51AA051, El: 9 mtr, Row: B/w B-C, Col: 4 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 127 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
272 | BID |  |  | CVP13-IN-D002 (9ZI04CC74) | 1LCA51AA051, El: 9 mtr, Row: B/w B-C, Col: 4 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 127 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TG26-04, TG25-04, TG24-04, TG23-04, TR04-04, TG22-04, TR03-04, TG68-04, TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
273 | BID |  |  | CVP13-IN-D003 (9ZI04CC75) | 1LCA61AA051, El: 9 mtr, Row: B/w B-C, Col: 5 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 158 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP54-03, TP55-03, TR25-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV11-R4, LV48-05, LV23-R4, LV24-R4, LV25-R4, LV74-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
274 | BID |  |  | CVP13-IN-D004 (9ZI04CC76) | 1LCA61AA051, El: 9 mtr, Row: B/w B-C, Col: 5 | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(I) ( 225 V ) | 137 | [5 empty] | CONTROL AND MONITORING | BIDI | ZZ99- , TP15-03, TP14-03, TP13-03, TP12-03, TP11-03, TP10-03, TP05-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-02, CC91-02, CC83-02, CC93-02, CC42-04, CC41-03, CC40-01
277 | BID |  |  | CVP14-BD-D001 (9ZI04CC79) | 1PGC13AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
278 | BID |  |  | CVP14-BD-D002 (9ZI04CC80) | 1PGB02AA001, El: 0 mtr, Row: Near B, Col: B/w 7&8 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 95 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC82-03, CC83-02, CC84-04, CC85-03, CC41-02, CC40-01
279 | BID |  |  | CVP14-BD-D003 (9ZI04CC81) | 1PGC01AA002, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
280 | BID |  |  | CVP14-BD-D004 (9ZI04CC82) | 1PGC31AA002, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
281 | BID |  |  | CVP14-BD-D005 (9ZI04CC83) | 1PGB01AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
282 | BID |  |  | CVP14-BD-C006 (9ZI04CC84) | 1LCP51AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP14, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
287 | BID |  |  | CVP15-BD-D001 (9ZI04CC89) | 1PGC02AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP15, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
288 | BID |  |  | CVP15-BD-D002 (9ZI04CC90) | 1PGC32AA001, El: 0 mtr, Row: B, Col: B/w 7&8 | CVP15, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
289 | BID |  |  | CVP15-BD-D003 (9ZI04CC91) | 1LCR57AA101, El: 0 mtr, Row: Near B, Col: B/w 7&8 | CVP15, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 96 | [5 empty] | CONTROL AND MONITORING | BID | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MV08-R2, MV26-R2, MV27-R2, MV44-R2, MA07-04, MR08-04, LR07-04, CC90-04, CC81-04, CC33-04, CC93-02, CC84-04, CC85-03, CC41-02, CC40-01
1 | BIO |  |  | CVP01-BI-C001 (9ZI06AC01) | IDF-A MTR JB, Near ID Fan-A | CRE02,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 356 | [7 empty] | ZZ99- , IM45-04, IM44-04, IR30-04, IM43-R2, IM42-R2, IM41-R2, IM40-R2, IM39-R2, IR22-R2, IM38-R2, IM37-L6, IM36-L6, IM35-L6, IM34-L6, IR31-L3, IM33-L6, IM32-L6, IM21-L4, IM20-L4, IM19-L4, IM18-L4, IM17-L4, IM16-L4, IM15-L4, IM14-L4, IM13-L4, IM12-L6, IM11-L6, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, CC82-03
2 | BIO |  |  | CVP01-BI-C002 (9ZI06AC02) | DDC-JB-3A , Near Eco Hopper-left | CRE02,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 150 | [7 empty] | ZZ99- , BF01-03, BR46-03, BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03
3 | BIO |  |  | CVP01-BI-C003 (9ZI06AC03) | DDC-JB-3B , Near Eco Hopper-right | CRE02,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 150 | [7 empty] | ZZ99- , BF01-03, BR46-03, BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03
4 | BIO |  |  | CVP01-BI-C004 (9ZI06AC04) | DDC-JB-8, Near ID Fan-A | CRE02,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 356 | [7 empty] | ZZ99- , IM45-04, IM44-04, IR30-04, IM43-R2, IM42-R2, IM41-R2, IM40-R2, IM39-R2, IR22-R2, IM38-R2, IM37-L6, IM36-L6, IM35-L6, IM34-L6, IR31-L3, IM33-L6, IM32-L6, IM21-L4, IM20-L4, IM19-L4, IM18-L4, IM17-L4, IM16-L4, IM15-L4, IM14-L4, IM13-L4, IM12-L6, IM11-L6, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, CC82-03
5 | BIO |  |  | CVP01-BI-C005 (9ZI06AC05) | DDC-JB-9, Near FGD | CRE02,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 323 | [7 empty] | ZZ99- , IM58-04, IM57-04, IR21-04, IM37-L6, IM36-L6, IM35-L6, IM34-L6, IR31-L3, IM33-L6, IM32-L6, IM21-L4, IM20-L4, IM19-L4, IM18-L4, IM17-L4, IM16-L4, IM15-L4, IM14-L4, IM13-L4, IM12-L6, IM11-L6, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, CC82-03
6 | BIO |  |  | CVP01-BI-C006 (9ZI06AC06) | DDC-JB-10, Near FGD | CRE02,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 323 | [7 empty] | ZZ99- , IM58-04, IM57-04, IR21-04, IM37-L6, IM36-L6, IM35-L6, IM34-L6, IR31-L3, IM33-L6, IM32-L6, IM21-L4, IM20-L4, IM19-L4, IM18-L4, IM17-L4, IM16-L4, IM15-L4, IM14-L4, IM13-L4, IM12-L6, IM11-L6, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03, CC82-03
7 | BIO |  |  | CVP02-BI-C001 (9ZI06AC07) | IDF-B MTR JB, Near ID Fan-B | CRE04,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 309 | [7 empty] | ZZ99- , IM59-04, IM58-04, IM57-04, IR21-04, IM37-L6, IM36-L6, IM35-L6, IM34-L6, IR31-L3, IM33-L6, IM32-L6, IM21-L4, IM20-L4, IM19-L4, IM18-L4, IM17-L4, IM16-L4, IM15-L4, IM14-L4, IM13-L4, IM12-L6, IM11-L6, IM10-05, IM09-06, IM07-06, IM06-03, IR19-03, CC05-05, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC30-03, CC31-03
8 | BIO |  |  | CVP03-BI-C001 (9ZI06AC08) | DDC-JB-5, Near AH-A | CRE06,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , BC10-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03
9 | BIO |  |  | CVP03-BI-C002 (9ZI06AC09) | DDC-JB-6, Near AH-A | CRE06,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , BC10-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03
10 | BIO |  |  | CVP03-BI-C003 (9ZI06AC10) | DDC-JB-1A, Near AH-A | CRE06,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , BC10-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03
11 | BIO |  |  | CVP03-BI-C004 (9ZI06AC11) | DDC-JB-2A , Near AH-A | CRE06,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 171 | [7 empty] | ZZ99- , BC10-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03, ZZ99-
12 | BIO |  |  | CVP03-BI-C005 (9ZI06AC12) | DDC-JB-7 , Near AH-A | CRE06,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , BC10-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03
13 | BIO |  |  | CVP03-BI-C006 (9ZI06AC13) | DDC-JB-4A, Near AH-A | CRE06,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , BC10-03, BC31-03, BC30-03, BC29-03, BC03-03, BC02-03, BC01-03, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC84-04, CC83-04, CC82-03, CC31-03
14 | BIO |  |  | CVP04-BI-C001 (9ZI06AC14) | DDC-JB-5, Near AH-B | CRE08,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [7 empty] | ZZ99- , BC09-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03, CC42-04, CC34-03, CC67-04, CC30-03
15 | BIO |  |  | CVP04-BI-C002 (9ZI06AC15) | DDC-JB-6, Near AH-B | CRE08,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [7 empty] | ZZ99- , BC09-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
16 | BIO |  |  | CVP04-BI-C003 (9ZI06AC16) | DDC-JB-1B, Near AH-B | CRE08,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 135 | [7 empty] | ZZ99- , BC09-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03
17 | BIO |  |  | CVP04-BI-C004 (9ZI06AC17) | DDC-JB-2B , Near AH-B | CRE08,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [7 empty] | ZZ99- , BC09-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
18 | BIO |  |  | CVP04-BI-C005 (9ZI06AC18) | DDC-JB-7 , Near AH-B | CRE08,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [7 empty] | ZZ99- , BC09-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
19 | BIO |  |  | CVP04-BI-C006 (9ZI06AC19) | DDC-JB-4B, Near AH-B | CRE08,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 145 | [7 empty] | ZZ99- , BC09-03, BC08-03, BC07-03, BC06-03, BC23-03, BC24-03, BC25-03, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03
20 | BIO |  |  | CVP05-BI-C001 (9ZI06AC20) | GFDR PNL-A, EER, 15.5 Mtr | CRE10,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC30-03
21 | BIO |  |  | CVP05-BI-C003 (9ZI06AC21) | GFDR PNL-B, EER, 15.5 Mtr | CRE10,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC30-03
22 | BIO |  |  | CVP05-BI-C002 (9ZI06AC22) | GFDR PNL-A, EER, 15.5 Mtr | CRE09,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC30-03
23 | BIO |  |  | CVP05-BI-C004 (9ZI06AC23) | GFDR PNL-B, EER, 15.5 Mtr | CRE09,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 48 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC30-03
24 | BIO |  |  | CVP06-BI-C001 (9ZI06AC24) | GFDR PNL-C, EER, 15.5 Mtr | CRE12,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 46 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC34-03, CC93-03, CC84-04, CC86-04, CC88-04
25 | BIO |  |  | CVP06-BI-C003 (9ZI06AC25) | GFDR PNL-D, EER, 15.5 Mtr | CRE12,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 46 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC34-03, CC93-03, CC84-04, CC86-04, CC88-04
26 | BIO |  |  | CVP06-BI-C002 (9ZI06AC26) | GFDR PNL-C, EER, 15.5 Mtr | CRE11,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 46 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC34-03, CC93-03, CC84-04, CC86-04, CC88-04
27 | BIO |  |  | CVP06-BI-C004 (9ZI06AC27) | GFDR PNL-D, EER, 15.5 Mtr | CRE11,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 46 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC34-03, CC93-03, CC84-04, CC86-04, CC88-04
28 | BIO |  |  | CVP07-BI-C001 (9ZI06AC28) | GFDR PNL-E, EER, 15.5 Mtr | CRE14,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 54 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC68-02, CC69-02, CC44-03
29 | BIO |  |  | CVP07-BI-C003 (9ZI06AC29) | GFDR PNL-F, EER, 15.5 Mtr | CRE14,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 54 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC68-02, CC69-02, CC44-03
30 | BIO |  |  | CVP07-BI-C002 (9ZI06AC30) | GFDR PNL-E, EER, 15.5 Mtr | CRE13,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 54 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC68-02, CC69-02, CC44-03
31 | BIO |  |  | CVP07-BI-C004 (9ZI06AC31) | GFDR PNL-F, EER, 15.5 Mtr | CRE13,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 54 | [7 empty] | ZZ99- , CC04-04, CC62-04, CC63-04, CC64-04, CC65-04, CC66-04, CC67-04, CC68-02, CC69-02, CC44-03
32 | BIO |  |  | CVP09-BI-C001 (9ZI06AC32) | EWLI JB-L, Near DRUM-L | CRE17,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 162 | [7 empty] | ZZ99- , BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BR21-05, BR20-05, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03 |  | 0 | 0
33 | BIO |  |  | CVP09-BI-C002 (9ZI06AC33) | EWLI JB-R, Near DRUM-R | CRE17,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 136 | [7 empty] | ZZ99- , BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03 |  | 0 | 0
34 | BIO |  |  | CVP09-BI-C003 (9ZI06AC34) | SWAS PNL, Él. 9.0 Mtr Row: B/w B-C, Col: b/w7-8 | CRE17,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 73 | [7 empty] | ZZ99- , TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC69-02, CC45-03 |  | 0 | 0
35 | BIO |  |  | CVP10-BI-C004 (9ZI06AC35) | BRNR TLT SHR PIN BOX-4, NEAR WINDBOX | CRE20,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 117 | [7 empty] | ZZ99- , BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03 |  | 0 | 0
36 | BIO |  |  | CVP10-BI-C003 (9ZI06AC36) | BRNR TLT SHR PIN BOX-3, NEAR WINDBOX | CRE20,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 136 | [7 empty] | ZZ99- , BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC89-04, CC88-04, CC87-03, CC44-03, CC45-03 |  | 0 | 0
37 | BIO |  |  | CVP10-BI-C001 (9ZI06AC37) | BRNR TLT SHR PIN BOX-1, NEAR WINDBOX | CRE20,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 115 | [7 empty] | ZZ99- , BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-02, CC45-03 |  | 0 | 0
38 | BIO |  |  | CVP10-BI-C002 (9ZI06AC38) | BRNR TLT SHR PIN BOX-2, NEAR WINDBOX | CRE20,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 127 | [7 empty] | ZZ99- , BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, LR10-R4, LV77-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC69-02, CC45-03 |  | 0 | 0
39 | BIO |  |  | CVP11-BI-C001 (9ZI06AC39) | JB-10, El: 0 mtr, Row: B, Col: B/w 7&8 | CRE21,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 56 | [7 empty] | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC88-04, CC86-04 |  | 0 | 0
40 | BIO |  |  | CVP11-BI-C002 (9ZI06AC40) | BFP-A MTR JB, El. 0 mtr, Row:B/w B-C, Col 4-5 | CRE22,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 134 | [7 empty] | ZZ99- , TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03 |  | 0 | 0
41 | BIO |  |  | CVP11-BI-C003 (9ZI06AC41) | JB-19, El: 0.0 mtr, Near ACWPs | CRE22,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 84 | [7 empty] | ZZ99- , TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MR16-06, TR48-06, LV64-07, LV04-R4, LV05-R4, LV06-R2, LV07-R2, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03 |  | 0 | 0
42 | BIO |  |  | CVP11-BI-C006 (9ZI06AC42) | LAB10AA511, El. 0 mtr, Row:B/w B-C, Col 4-5 | CRE22,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 137 | [7 empty] | ZZ99- , TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03 |  | 0 | 0
43 | BIO |  |  | CVP11-BI-C007 (9ZI06AC43) | RC VLV PUMP-A JB, El. 0 mtr, Row:B/w B-C, Col 4-5 | CRE22,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 137 | [7 empty] | ZZ99- , TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03 |  | 0 | 0
44 | BIO |  |  | CVP11-BI-C005 (9ZI06AC44) | MDBFP VOITH JB, El. 0 mtr, Row:B/w B-C, Col 4-5 | CRE22,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 134 | [7 empty] | ZZ99- , TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03 |  | 0 | 0
45 | BIO |  |  | CVP11-BI-C008 (9ZI06AC45) | 1LAC10CP100, El. 0 mtr, Row:B/w B-C, Col 4-5 | CRE22,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 137 | [7 empty] | ZZ99- , TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03 |  | 0 | 0
46 | BIO |  |  | CVP11-BI-C004 (9ZI06AC46) | SWAS PNL, El: 9.0 mtr, SWAS Room | CRE22,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 55 | [7 empty] | ZZ99- , TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC84-04, CC85-03 |  | 0 | 0
47 | BIO |  |  | CVP12-BI-C001 (9ZI06AC47) | JB-10, El: 0 mtr, Row: B, Col: B/w 7&8 | CRE23,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 62 | [7 empty] | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03 |  | 0 | 0
48 | BIO |  |  | CVP12-BI-C002 (9ZI06AC48) | BFP-B MOTOR JB, El. 0 mtr, Row:B/w B-C, Col 5-6 | CRE24,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 132 | [7 empty] | ZZ99- , TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03, CC41-03 |  | 0 | 0
49 | BIO |  |  | CVP12-BI-C003 (9ZI06AC49) | JB-19, El: 0.0 mtr, Near ACWPs | CRE24,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 77 | [7 empty] | ZZ99- , TG81-04, TG82-04, MR17-06, MR16-06, TR48-06, LV64-07, LV04-R4, LV05-R4, LV06-R2, LV07-R2, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03 |  | 0 | 0
50 | BIO |  |  | CVP12-BI-C006 (9ZI06AC50) | LAB20AA001, El. 0 mtr, Row:B/w B-C, Col 5-6 | CRE24,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 132 | [7 empty] | ZZ99- , TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03, CC41-03 |  | 0 | 0
51 | BIO |  |  | CVP12-BI-C007 (9ZI06AC51) | RC VLV PUMP-B JB, El. 0 mtr, Row:B/w B-C, Col 5-6 | CRE24,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 132 | [7 empty] | ZZ99- , TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03, CC41-03 |  | 0 | 0
52 | BIO |  |  | CVP12-BI-C005 (9ZI06AC52) | MDBFP VOITH JB, El. 0 mtr, Row:B/w B-C, Col 5-6 | CRE24,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 129 | [7 empty] | ZZ99- , TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC89-04, CC88-04, CC86-04, CC85-03, CC41-03 |  | 0 | 0
53 | BIO |  |  | CVP12-BI-C008 (9ZI06AC53) | 1LAC20CP100, El. 0 mtr, Row:B/w B-C, Col 5-6 | CRE24,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 132 | [7 empty] | ZZ99- , TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC42-04, CC41-03 |  | 0 | 0
54 | BIO |  |  | CVP13-BI-C001 (9ZI06AC54) | JB-10, El: 0 mtr, Row: B, Col: B/w 7&8 | CRE25,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 62 | [7 empty] | ZZ99- , TG89-03, TG20-03, TG21-03, MA04-03, MR18-04, MV06-R2, MV07-R2, MA05-04, MR10-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03 |  | 0 | 0
55 | BIO |  |  | CVP13-BI-C002 (9ZI06AC55) | BFP-C MTR JB, El. 0 mtr, Row:B/w B-C, Col 6-7 | CRE26,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 125 | [7 empty] | ZZ99- , TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03 |  | 0 | 0
56 | BIO |  |  | CVP13-BI-C006 (9ZI06AC56) | LAB30AA511, El. 0 mtr, Row:B/w B-C, Col 6-7 | CRE26,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [7 empty] | ZZ99- , TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
57 | BIO |  |  | CVP13-BI-C007 (9ZI06AC57) | RC VLV PUMP-C JB, El. 0 mtr, Row:B/w B-C, Col 6-7 | CRE26,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [7 empty] | ZZ99- , TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
58 | BIO |  |  | CVP13-BI-C005 (9ZI06AC58) | MDBFP VOITH JB, El. 0 mtr, Row:B/w B-C, Col 6-7 | CRE26,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 121 | [7 empty] | ZZ99- , TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
59 | BIO |  |  | CVP13-BI-C008 (9ZI06AC59) | 1LAC30CP100, El. 0 mtr, Row:B/w B-C, Col 6-7 | CRE26,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 113 | [7 empty] | ZZ99- , TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
60 | BIO |  |  | CVP14-BI-C001 (9ZI06AC60) | PHOS DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 152 | [7 empty] | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
61 | BIO |  |  | CVP14-BI-C002 (9ZI06AC61) | PHOS DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 152 | [7 empty] | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-07, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
62 | BIO |  |  | CVP14-BI-C003 (9ZI06AC62) | PHOS DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 152 | [7 empty] | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
63 | BIO |  |  | CVP14-BI-C004 (9ZI06AC63) | PHOS DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 155 | [7 empty] | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
64 | BIO |  |  | CVP14-BI-C005 (9ZI06AC64) | PHOS DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 155 | [7 empty] | ZZ99- , TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
65 | BIO |  |  | CVP14-BI-C006 (9ZI06AC65) | JB-04, El: 0 mtr, Row: A, Col: 6 | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 116 | [7 empty] | ZZ99- , TG76-03, TG75-03, TG74-03, TG73-03, TR16-03, TG72-03, TG71-03, TR48-06, LV64-07, LV63-06, LV13-R4, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC40-03 |  | 0 | 0
66 | BIO |  |  | CVP14-BI-C007 (9ZI06AC66) | JB-22, El: 0.0 mtr, Near DMCW BPs | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 98 | [7 empty] | ZZ99- , TG14-R3, TG15-R3, TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MR16-06, TR48-06, LV64-07, LV04-R4, LV05-R4, LV06-R4, LV07-R2, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
67 | BIO |  |  | CVP14-BI-C008 (9ZI06AC67) | JB-23, El: 0.0 mtr, Near DMCWPs | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 98 | [7 empty] | ZZ99- , TG16-R3, TG86-04, TG84-04, TG81-04, TG82-04, MR17-06, MR16-06, TR48-06, LV64-07, LV04-R4, LV05-R4, LV06-R4, LV07-R2, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
68 | BIO |  |  | CVP14-BI-C010 (9ZI06AC68) | SWAS PNL, Él. 9.0 Mtr Row: B/w B-C, Col: b/w7-8 | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 65 | [7 empty] | ZZ99- , TG67-04, TR52-04, LV45-04, LV44-04, LV43-04, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC40-03 |  | 0 | 0
69 | BIO |  |  | CVP14-BI-C011 (9ZI06AC69) | AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 152 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
70 | BIO |  |  | CVP14-BI-C012 (9ZI06AC70) | AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
71 | BIO |  |  | CVP14-BI-C013 (9ZI06AC71) | AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
72 | BIO |  |  | CVP14-BI-C014 (9ZI06AC72) | AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
73 | BIO |  |  | CVP14-BI-C015 (9ZI06AC73) | AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
74 | BIO |  |  | CVP14-BI-C016 (9ZI06AC74) | AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
75 | BIO |  |  | CVP14-BI-C017 (9ZI06AC75) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 161 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-07, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
76 | BIO |  |  | CVP14-BI-C018 (9ZI06AC76) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 152 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
77 | BIO |  |  | CVP14-BI-C019 (9ZI06AC77) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
78 | BIO |  |  | CVP14-BI-C020 (9ZI06AC78) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
79 | BIO |  |  | CVP14-BI-C021 (9ZI06AC79) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
80 | BIO |  |  | CVP14-BI-C022 (9ZI06AC80) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
81 | BIO |  |  | CVP14-BI-C023 (9ZI06AC81) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-04, CC40-03 |  | 0 | 0
82 | BIO |  |  | CVP14-BI-C024 (9ZI06AC82) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-02, CC40-03 |  | 0 | 0
83 | BIO |  |  | CVP14-BI-C025 (9ZI06AC83) | BULK AMMN DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | ,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [7 empty] | ZZ99- , TG01-02, TG02-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC82-03, CC31-03, CC30-03, CC57-05 |  | 0 | 0
84 | BIO |  |  | CVP14-BI-C026 (9ZI06AC84) | NAOH DOS PNL, EL. 21.0 Mtr, Row: B/w B-C, Col: B/w 7-8 | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 149 | [7 empty] | ZZ99- , TR40-03, TR26-03, TP04-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC40-03 |  | 0 | 0
85 | BIO |  |  | CVP14-BI-C027 (9ZI06AC85) | NAOH DOS PNL, EL. 21.0 Mtr, Row: B/w B-C, Col: B/w 7-8 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 149 | [7 empty] | ZZ99- , TR40-03, TR26-03, TP04-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC40-03 |  | 0 | 0
86 | BIO |  |  | CVP14-BI-C028 (9ZI06AC86) | NAOH DOS PNL, EL. 21.0 Mtr, Row: B/w B-C, Col: B/w 7-8 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 149 | [7 empty] | ZZ99- , TR40-03, TR26-03, TP04-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC40-03 |  | 0 | 0
87 | BIO |  |  | CVP14-BI-C029 (9ZI06AC87) | NAOH DOS PNL, EL. 21.0 Mtr, Row: B/w B-C, Col: B/w 7-8 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 149 | [7 empty] | ZZ99- , TR40-03, TR26-03, TP04-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC40-03 |  | 0 | 0
88 | BIO |  |  | CVP14-BI-C030 (9ZI06AC88) | NAOH DOS PNL, EL. 21.0 Mtr, Row: B/w B-C, Col: B/w 7-8 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 149 | [7 empty] | ZZ99- , TR40-03, TR26-03, TP04-03, TP03-03, TP49-03, TP52-03, TP53-03, TR24-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-02, CC40-03 |  | 0 | 0
89 | BIO |  |  | CVP14-BI-C031 (9ZI06AC89) | HYD DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 149 | [7 empty] | ZZ99- , TG03-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
90 | BIO |  |  | CVP14-BI-C032 (9ZI06AC90) | HYD DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 160 | [7 empty] | ZZ99- , TG03-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-02, CC40-03 |  | 0 | 0
91 | BIO |  |  | CVP14-BI-C033 (9ZI06AC91) | HYD DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 160 | [7 empty] | ZZ99- , TG03-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-02, CC40-03 |  | 0 | 0
92 | BIO |  |  | CVP14-BI-C034 (9ZI06AC92) | HYD DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 160 | [7 empty] | ZZ99- , TG03-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-02, CC40-03 |  | 0 | 0
93 | BIO |  |  | CVP14-BI-C035 (9ZI06AC93) | HYD DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 160 | [7 empty] | ZZ99- , TG03-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV05-R4, LV06-R4, LV07-R4, LV76-05, LV79-04, LR10-R4, CR01-L3, CC71-06, CC51-04, CC70-04, CC69-02, CC40-03 |  | 0 | 0
94 | BIO |  |  | CVP14-BI-C036 (9ZI06AC94) | HYD DOS PNL, EL. 0.0 Mtr, Row: C, Col: B/w 2-3 | CRE28,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 161 | [7 empty] | ZZ99- , TG03-02, TG04-02, TG05-02, TG06-02, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG86-04, TG85-03, TR02-03, MR15-03, TR50-03, LV59-03, LV58-03, LV12-R4, LV52-03, LV22-R4, LV23-R4, LV24-R4, LV75-04, LR06-04, CC91-04, CC83-04, CC93-03, CC34-03, CC68-04, CC40-03 |  | 0 | 0
95 | BIO |  |  | CVP15-BI-C001 (9ZI06AC95) | JB-22, El: 0.0 mtr, Near DMCW BPs | CRE30,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 89 | [7 empty] | ZZ99- , TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R2, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
96 | BIO |  |  | CVP15-BI-C002 (9ZI06AC96) | JB-23, El: 0.0 mtr, Near DMCWPs | CRE30,EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 86 | [7 empty] | ZZ99- , TG16-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R2, LV76-05, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, CC40-03 |  | 0 | 0
97 | BIO |  |  | CVP15-BI-C003 (9ZI06AC97) | UPS-1 PNL, EER, 15.5 Mtr | CRE29,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 25 | [7 empty] | ZZ99- , CC35-03, CC67-04, CC30-03 |  | 0 | 0
98 | BIO |  |  | CVP15-BI-C004 (9ZI06AC98) | UPS-2 PNL, EER, 15.5 Mtr | CRE29,EER, 15.5 Mtr | 08P X 0.5 Paired Screened(O) ( 225 V ) | 39 | [7 empty] | ZZ99- , CC06-04, CC53-05, CC54-05, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-03 |  | 0 | 0
99 | BIO |  |  | CVP15-BI-C005 (9ZI06AC99) | CHARGER PNL-1A, EER, 15.5 Mtr | CRE29,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 34 | [7 empty] | ZZ99- , CC16-03, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-03 |  | 0 | 0
100 | BIO |  |  | CVP15-BI-C006 (9ZI06BC01) | CHARGER PNL-1B, EER, 15.5 Mtr | CRE29,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 34 | [7 empty] | ZZ99- , CC16-03, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-03 |  | 0 | 0
101 | BIO |  |  | CVP15-BI-C007 (9ZI06BC02) | CHARGER PNL-2A, EER, 15.5 Mtr | CRE29,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 34 | [7 empty] | ZZ99- , CC16-03, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-03 |  | 0 | 0
102 | BIO |  |  | CVP15-BI-C008 (9ZI06BC03) | CHARGER PNL-2B, EER, 15.5 Mtr | CRE29,EER, 15.5 Mtr | 12P X 0.5 Paired Screened(O) ( 225 V ) | 34 | [7 empty] | ZZ99- , CC16-03, CC55-05, CC56-05, CC57-05, CC58-05, CC59-05, CC40-03 |  | 0 | 0
1 | TRYFLD |  |  | ID-CBL-TT-1A-0 1 (9ZT06AC01) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
2 | TRYFLD |  |  | ID-CBL-TT-1A-0 2 (9ZT06AC02) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
3 | TRYFLD |  |  | ID-CBL-TT-1A-0 3 (9ZT06AC03) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
4 | TRYFLD |  |  | ID-CBL-TT-1A-0 4 (9ZT06AC04) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
5 | TRYFLD |  |  | ID-CBL-TT-1A-0 5 (9ZT06AC05) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
6 | TRYFLD |  |  | ID-CBL-TT-1A-0 6 (9ZT06AC06) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
7 | TRYFLD |  |  | ID-CBL-TT-1A-0 7 (9ZT06AC07) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
8 | TRYFLD |  |  | ID-CBL-TT-1A-0 8 (9ZT06AC08) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-2 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
9 | TRYFLD |  |  | ID-CBL-TT-1A-0 9 (9ZT06AC09) | ID FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB-2 ID FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
10 | TRYFLD |  |  | ID-CBL-TT-1B-0 1 (9ZT06AC10) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
11 | TRYFLD |  |  | ID-CBL-TT-1B-0 2 (9ZT06AC11) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
12 | TRYFLD |  |  | ID-CBL-TT-1B-0 3 (9ZT06AC12) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
13 | TRYFLD |  |  | ID-CBL-TT-1B-0 4 (9ZT06AC13) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
14 | TRYFLD |  |  | ID-CBL-TT-1B-0 5 (9ZT06AC14) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
15 | TRYFLD |  |  | ID-CBL-TT-1B-0 6 (9ZT06AC15) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
16 | TRYFLD |  |  | ID-CBL-TT-1B-0 7 (9ZT06AC16) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-1 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
17 | TRYFLD |  |  | ID-CBL-TT-1B-0 8 (9ZT06AC17) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-2 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
18 | TRYFLD |  |  | ID-CBL-TT-1B-0 9 (9ZT06AC18) | ID FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB-2 ID FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR ID FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ID FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
19 | TRYFLD |  |  | FD-CBL-TT-1A-0 1 (9ZT06AC19) | FD FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
20 | TRYFLD |  |  | FD-CBL-TT-1A-0 2 (9ZT06AC20) | FD FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
21 | TRYFLD |  |  | FD-CBL-TT-1A-0 3 (9ZT06AC21) | FD FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
22 | TRYFLD |  |  | FD-CBL-TT-1A-0 4 (9ZT06AC22) | FD FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
23 | TRYFLD |  |  | FD-CBL-TT-1A-0 5 (9ZT06AC23) | FD FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
24 | TRYFLD |  |  | FD-CBL-TT-1B-0 1 (9ZT06AC24) | FD FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
25 | TRYFLD |  |  | FD-CBL-TT-1B-0 2 (9ZT06AC25) | FD FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
26 | TRYFLD |  |  | FD-CBL-TT-1B-0 3 (9ZT06AC26) | FD FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
27 | TRYFLD |  |  | FD-CBL-TT-1B-0 4 (9ZT06AC27) | FD FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
28 | TRYFLD |  |  | FD-CBL-TT-1B-0 5 (9ZT06AC28) | FD FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB FD FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0: NEAR FD FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FD FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
29 | TRYFLD |  |  | PA-CBL-TT-1A-0 1 (9ZT06AC29) | PA FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
30 | TRYFLD |  |  | PA-CBL-TT-1A-0 2 (9ZT06AC30) | PA FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
31 | TRYFLD |  |  | PA-CBL-TT-1A-0 3 (9ZT06AC31) | PA FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
32 | TRYFLD |  |  | PA-CBL-TT-1A-0 4 (9ZT06AC32) | PA FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
33 | TRYFLD |  |  | PA-CBL-TT-1A-0 5 (9ZT06AC33) | PA FAN-A MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
34 | TRYFLD |  |  | PA-CBL-TT-1B-0 1 (9ZT06AC34) | PA FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
35 | TRYFLD |  |  | PA-CBL-TT-1B-0 2 (9ZT06AC35) | PA FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
36 | TRYFLD |  |  | PA-CBL-TT-1B-0 3 (9ZT06AC36) | PA FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
37 | TRYFLD |  |  | PA-CBL-TT-1B-0 4 (9ZT06AC37) | PA FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
38 | TRYFLD |  |  | PA-CBL-TT-1B-0 5 (9ZT06AC38) | PA FAN-B MOTOR WINDING & BEARING RTDs INTEGRAL JB PA FAN B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 0 : NEAR PA FAN B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PA FAN BEARING EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
39 | TRYFLD |  |  | APHA-CE-CBL-TT -01 (9ZT06AC39) | APH-A COLD END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
40 | TRYFLD |  |  | APHA-CE-CBL-TT -02 (9ZT06AC40) | APH-A COLD END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
41 | TRYFLD |  |  | APHA-CE-CBL-TT -03 (9ZT06AC41) | APH-A COLD END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
42 | TRYFLD |  |  | APHA-CE-CBL-TT -04 (9ZT06AC42) | APH-A COLD END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
43 | TRYFLD |  |  | APHA-CE-CBL-TT -05 (9ZT06AC43) | APH-A COLD END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
44 | TRYFLD |  |  | APHA-CE-CBL-TT -06 (9ZT06AC44) | APH-A COLD END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
45 | TRYFLD |  |  | APHA-HE-CBL-TT -01 (9ZT06AC45) | APH-A HOT END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
46 | TRYFLD |  |  | APHA-HE-CBL-TT -02 (9ZT06AC46) | APH-A HOT END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
47 | TRYFLD |  |  | APHA-HE-CBL-TT -03 (9ZT06AC47) | APH-A HOT END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
48 | TRYFLD |  |  | APHA-HE-CBL-TT -04 (9ZT06AC48) | APH-A HOT END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
49 | TRYFLD |  |  | APHA-HE-CBL-TT -05 (9ZT06AC49) | APH-A HOT END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
50 | TRYFLD |  |  | APHA-HE-CBL-TT -06 (9ZT06AC50) | APH-A HOT END FIRE SENSING T/C EL 16100: APH-A | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
51 | TRYFLD |  |  | APHB-CE-CBL-TT -01 (9ZT06AC51) | APH-B COLD END FIRE SENSING T/C EL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
52 | TRYFLD |  |  | APHB-CE-CBL-TT -02 (9ZT06AC52) | APH-B COLD END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
53 | TRYFLD |  |  | APHB-CE-CBL-TT -03 (9ZT06AC53) | APH-B COLD END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
54 | TRYFLD |  |  | APHB-CE-CBL-TT -04 (9ZT06AC54) | APH-B COLD END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
55 | TRYFLD |  |  | APHB-CE-CBL-TT -05 (9ZT06AC55) | APH-B COLD END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
56 | TRYFLD |  |  | APHB-CE-CBL-TT -06 (9ZT06AC56) | APH-B COLD END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
57 | TRYFLD |  |  | APHB-HE-CBL-TT -01 (9ZT06AC57) | APH-B HOT END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
58 | TRYFLD |  |  | APHB-HE-CBL-TT -02 (9ZT06AC58) | APH-B HOT END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
59 | TRYFLD |  |  | APHB-HE-CBL-TT -03 (9ZT06AC59) | APH-B HOT END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
60 | TRYFLD |  |  | APHB-HE-CBL-TT -04 (9ZT06AC60) | APH-B HOT END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
61 | TRYFLD |  |  | APHB-HE-CBL-TT -05 (9ZT06AC61) | APH-B HOT END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
62 | TRYFLD |  |  | APHB-HE-CBL-TT -06 (9ZT06AC62) | APH-B HOT END FIRE SENSING T/CEL 16100: APH-B | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 02C X 0.5 Compensating ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH FIRE SENSING THERMOCOUPLES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
63 | TRYFLD |  |  | APHA-CBL-TT-1 (9ZT06AC63) | APH-A BEARING RTDs INTEGRAL JBEL 16100: NEAR S16L | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
64 | TRYFLD |  |  | APHA-CBL-TT-2 (9ZT06AC64) | APH-A BEARING RTDs INTEGRAL JBEL 16100: NEAR S16L | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
65 | TRYFLD |  |  | APHA-CBL-TT-3 (9ZT06AC65) | APH-A BEARING RTDs INTEGRAL JBEL 16100: NEAR S16L | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
66 | TRYFLD |  |  | APHA-CBL-TT-4 (9ZT06AC66) | APH-A BEARING RTDs INTEGRAL JBEL 16100: NEAR S16L | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
67 | TRYFLD |  |  | APHA-CBL-TT-1 (9ZT06AC67) | APH-B BEARING RTDs INTEGRAL JBEL 16100: NEAR S16R | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
68 | TRYFLD |  |  | APHA-CBL-TT-2 (9ZT06AC68) | APH-B BEARING RTDs INTEGRAL JBEL 16100: NEAR S16R | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
69 | TRYFLD |  |  | APHA-CBL-TT-3 (9ZT06AC69) | APH-B BEARING RTDs INTEGRAL JBEL 16100: NEAR S16R | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
70 | TRYFLD |  |  | APHA-CBL-TT-4 (9ZT06AC70) | APH-B BEARING RTDs INTEGRAL JBEL 16100: NEAR S16R | DUAL INPUT TEMPERATURE TRANSMITTER ENCLOSURE EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B RTDs | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
71 | TRYFLD |  |  | APHA-CBL-JB1A- 1 (9ZT06AC71) | APH-A GUIDE BRG FLOW SWITCHEL 16100 NEAR S16L | DDC-JB-1A (24 WAYS)EL 16100 NEAR S16L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
72 | TRYFLD |  |  | APHA-CBL-JB1A- 2 (9ZT06AC72) | APH-A SUPRT BRG FLOW SWITCHEL 16100 NEAR S16L | DDC-JB-1A (24 WAYS)EL 16100 NEAR S16L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
73 | TRYFLD |  |  | APHA-CBL-JB2A- 1 (9ZT06AC73) | APH-A AIR MOTOR PR. SWITCHEL 16100 NEAR S16L | DDC-JB-2A (24 WAYS)EL 16100 NEAR S16L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
74 | TRYFLD |  |  | APHA-CBL-JB2A- 2 (9ZT06AC74) | APH-A AIR MOTOR PR. SWITCHEL 16100 NEAR S16L | DDC-JB-2A (24 WAYS)EL 16100 NEAR S16L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
75 | TRYFLD |  |  | APHA-CBL-JB2A- 3 (9ZT06AC75) | SPEED SENSOR (GO SWITCH)EL 16100 NEAR S16L | DDC-JB-2A (24 WAYS)EL 16100 NEAR S16L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
76 | TRYFLD |  |  | APHA-CBL-JB1B- 1 (9ZT06AC76) | APH-B GUIDE BRG FLOW SWITCHEL 16100: NEAR S16R | DDC-JB-1B (24 WAYS)EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - B EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
77 | TRYFLD |  |  | APHA-CBL-JB1B- 2 (9ZT06AC77) | APH-B SUPRT BRG FLOW SWITCHEL 16100: NEAR S16R | DDC-JB-1B (24 WAYS)EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - B EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
78 | TRYFLD |  |  | APHA-CBL-JB2B- 1 (9ZT06AC78) | APH-B AIR MOTOR PR. SWITCHEL 16100: NEAR S16R | DDC-JB-2B (24 WAYS)EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - B EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
79 | TRYFLD |  |  | APHA-CBL-JB2B- 2 (9ZT06AC79) | APH-B AIR MOTOR PR. SWITCHEL 16100: NEAR S16R | DDC-JB-2B (24 WAYS)EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - B EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
80 | TRYFLD |  |  | APHA-CBL-JB2B- 3 (9ZT06AC80) | SPEED SENSOR (GO SWITCH)EL 16100: NEAR S16R | DDC-JB-2B (24 WAYS)EL 16100: NEAR S16R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - B EQUIPMENT | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
81 | TRYFLD |  |  | DDC-CBL-JB3A-1 (9ZT06AC81) | ECO. ASH HOPPER LEVEL SWITCH EL 23300: NEAR S19 | DDC-JB-3A (24 WAYS) EL 23300: NEAR S19 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ECONOMISER ASH HOPPER LEVEL SWI | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
82 | TRYFLD |  |  | DDC-CBL-JB3A-2 (9ZT06AC82) | ECO. ASH HOPPER LEVEL SWITCH EL 23300: NEAR S19 | DDC-JB-3A (24 WAYS) EL 23300: NEAR S19 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ECONOMISER ASH HOPPER LEVEL SWI | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
83 | TRYFLD |  |  | DDC-CBL-JB3B-1 (9ZT06AC83) | ECO. ASH HOPPER LEVEL SWITCH EL 23300: NEAR S19 | DDC-JB-3A (24 WAYS) EL 23300: NEAR S19 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ECONOMISER ASH HOPPER LEVEL SWI | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
84 | TRYFLD |  |  | DDC-CBL-JB3B-2 (9ZT06AC84) | ECO. ASH HOPPER LEVEL SWITCH EL 23300: NEAR S19 | DDC-JB-3A (24 WAYS) EL 23300: NEAR S19 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR ECONOMISER ASH HOPPER LEVEL SWI | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
85 | TRYFLD |  |  | APH-CBL-JB4A-1 (9ZT06AC85) | APH-A ASH HOPPER LEVEL SWITCHEL 4500: NEAR S23 | DDC-JB-4A (24 WAYS)EL 4500: NEAR S23 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B ASH HOPPER | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
86 | TRYFLD |  |  | APH-CBL-JB4A-2 (9ZT06AC86) | APH-A ASH HOPPER LEVEL SWITCHEL 4500: NEAR S23 | DDC-JB-4A (24 WAYS)EL 4500: NEAR S23 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B ASH HOPPER | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
87 | TRYFLD |  |  | APH-CBL-JB4B-1 (9ZT06AC87) | APH-B ASH HOPPER LEVEL SWITCHEL 4500: NEAR S23 | DDC-JB-4B (24 WAYS)EL 4500: NEAR S23 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B ASH HOPPER | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
88 | TRYFLD |  |  | APH-CBL-JB4B-2 (9ZT06AC88) | APH-B ASH HOPPER LEVEL SWITCHEL 4500: NEAR S23 | DDC-JB-4B (24 WAYS)EL 4500: NEAR S23 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR AIR PREHEATER - A&B ASH HOPPER | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
89 | TRYFLD |  |  | DDC-CBL-JB5-1 (9ZT06AC89) | HOT PA SEAL AIR PR. SWITCH EL 19800: NEAR S22 | DDC-JB-5 (24 WAYS)EL 19800: NEAR S22 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PRIMARY & SECONDARY SEAL AIR PR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
90 | TRYFLD |  |  | DDC-CBL-JB5-2 (9ZT06AC90) | HOT PA SEAL AIR PR. SWITCH EL 19800: NEAR S22 | DDC-JB-5 (24 WAYS)EL 19800: NEAR S22 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PRIMARY & SECONDARY SEAL AIR PR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
91 | TRYFLD |  |  | DDC-CBL-JB6-1 (9ZT06AC91) | HOT PA SEAL AIR PR. SWITCH EL 19800: NEAR S22 | DDC-JB-6 (24 WAYS)EL 19800: NEAR S22 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PRIMARY & SECONDARY SEAL AIR PR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
92 | TRYFLD |  |  | DDC-CBL-JB6-2 (9ZT06AC92) | HOT PA SEAL AIR PR. SWITCH EL 19800: NEAR S22 | DDC-JB-6 (24 WAYS)EL 19800: NEAR S22 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR PRIMARY & SECONDARY SEAL AIR PR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
93 | TRYFLD |  |  | DDC-CBL-JB7-1 (9ZT06AC93) | APH INLET FG PR. SWITCH EL 19800: NEAR S22 | DDC-JB-7 (24 WAYS)EL 19800: NEAR S22 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH INLET FG & ID FAN SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
94 | TRYFLD |  |  | DDC-CBL-JB7-2 (9ZT06AC94) | APH INLET FG PR. SWITCH EL 19800: NEAR S22 | DDC-JB-7 (24 WAYS)EL 19800: NEAR S22 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH INLET FG & ID FAN SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
95 | TRYFLD |  |  | DDC-CBL-JB8-1 (9ZT06AC95) | ID FAN- SEAL AIR PR. SWITCH EL 0: NEAR ID FAN A/B | DDC-JB-8 (24 WAYS)EL 0: NEAR ID FAN A/B | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH INLET FG & ID FAN SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
96 | TRYFLD |  |  | DDC-CBL-JB8-2 (9ZT06AC96) | ID FAN- SEAL AIR PR. SWITCH EL 0: NEAR ID FAN A/B | DDC-JB-8 (24 WAYS)EL 0: NEAR ID FAN A/B | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FIELD CONNECTION DIAGRAM FOR APH INLET FG & ID FAN SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
97 | TRYFLD |  |  | DDC-CBL-JB9-1 (9ZT06AC97) | FGD INLET SEAL AIR PR. SWITCH EL 8500: NEAR W6 | DDC-JB-9 (24WAYS)EL 8500: NEAR W6 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FGD SEAL AIR PRESSURE SWITCH | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
98 | TRYFLD |  |  | DDC-CBL-JB9-2 (9ZT06AC98) | FGD OUTLET SEAL AIR PR. SWITCH EL 8500: NEAR W6 | DDC-JB-9 (24WAYS)EL 8500: NEAR W6 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FGD SEAL AIR PRESSURE SWITCH | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
99 | TRYFLD |  |  | DDC-CBL-JB10-1 (9ZT06AC99) | FGD BYPASS SEAL AIR PR. SWITCH EL 8500: NEAR W6 | DDC-JB-10 (12 WAYS)EL 8500: NEAR W6 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FIELD CONNECTION DIAGRAM FOR FGD SEAL AIR PRESSURE SWITCH | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
1 | FOPH |  |  | FOPI-CBL-001 (9ZT03AC01) | FOPI PANEL | FOPI-JB-01 (24 WAYS) FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
2 | FOPH |  |  | FOPI-CBL-JB01- 01 (9ZT03AC02) | FOPI-JB-01 (24 WAYS) | LDO DISCHARGE TRANSMITTER FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
3 | FOPH |  |  | FOPI-CBL-JB01- 02 (9ZT03AC03) | FOPI-JB-01 (24 WAYS) | LDO DISCHARGE PRESSURE FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
4 | FOPH |  |  | FOPI-CBL-002 (9ZT03AC04) | FOPI PANEL | FOPI-JB-02 (36 WAYS) FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
5 | FOPH |  |  | FOPI-CBL-003 (9ZT03AC05) | FOPI PANEL | FOPI-JB-02 (36 WAYS) FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
6 | FOPH |  |  | FOPI-CBL-JB02- 01 (9ZT03AC06) | FOPI-JB-02 (36 WAYS) | LDO SUCTION PRESSURE FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
7 | FOPH |  |  | FOPI-CBL-JB02- 02 (9ZT03AC07) | FOPI-JB-02 (36 WAYS) | LDO SUCTION PRESSURE FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
8 | FOPH |  |  | FOPI-CBL-JB02- 03 (9ZT03AC08) | FOPI-JB-02 (36 WAYS) | LDO STORAGE TANK LEVEL FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 225 V ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO TRANSMITTERS | PEM SCOPE CABLE | SITE ROUTING |  | 0 | 0
9 | FOPH |  |  | FOPI-CBL-004 (9ZT03AC09) | FOPI PANEL | FOPI-JB-03 (24 WAYS) FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO SWITCHES / TRANSMITTE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
10 | FOPH |  |  | FOPI-CBL-JB03- 01 (9ZT03AC10) | FOPI-JB-03 (24 WAYS) | LDO SUCTION DP TRANSMITTERS FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO SWITCHES / TRANSMITTE | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
11 | FOPH |  |  | FOPI-CBL-JB03- 02 (9ZT03AC11) | FOPI-JB-03 (24 WAYS) | LDO SUCTION DP TRANSMITTERS FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO SWITCHES / TRANSMITTE | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
12 | FOPH |  |  | FOPI-CBL-005 (9ZT03AC12) | FOPI PANEL | FO MCC (LDO PUMP-A) FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO SWITCHES / TRANSMITTE | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
13 | FOPH |  |  | FOPI-CBL-006 (9ZT03AC13) | FOPI PANEL | FO MCC (LDO PUMP-B) FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM LDO SWITCHES / TRANSMITTE | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
14 | FOPH |  |  | FOPI-CBL-007 (9ZT03AC14) | FOPI PANEL | FO MCC (LDO PUMP IN PUMP HOUSE) FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM DRAIN OIL PUMP IN PUMP HO | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
15 | FOPH |  |  | FOPI-CBL-008 (9ZT03AC15) | FOPI PANEL | FOPI-JB-04 (24 WAYS) FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM DRAIN OIL SYSTEM IN PUMP | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
16 | FOPH |  |  | FOPI-CBL-JB04- 01 (9ZT03AC16) | FOPI-JB-04 (24 WAYS) | DRAIN OIL TANK LEVEL TRANSMITTER FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM DRAIN OIL SYSTEM IN PUMP | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
17 | FOPH |  |  | FOPI-CBL-009 (9ZT03AC17) | FOPI PANEL | FOPI-JB-05 (24 WAYS) FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM DRAIN OIL SYSTEM IN PUMP | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
18 | FOPH |  |  | FOPI-CBL-JB05- 01 (9ZT03AC18) | FOPI-JB-05 (24 WAYS) | DRAIN OIL TANK LEVEL TRANSMITTER FUEL OIL PUMP HOUSE | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 45 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM DRAIN OIL SYSTEM IN PUMP | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
19 | FOPH |  |  | FOPI-CBL-010 (9ZT03AC19) | FOPI PANEL | MOTOR OPERATED VALVE LOPCV - ISOL FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM MOTOR OPERATED VALVE | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
20 | FOPH |  |  | FOPI-CBL-011 (9ZT03AC20) | FOPI PANEL | MOTOR OPERATED VALVE LOPCV - ISOL (BY PASS) FUEL OIL PUMP HOUSE | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 380 | [5 empty] | FOPI PANEL INTERCONNECTION DIAGRAM MOTOR OPERATED VALVE | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
1 | FSSS |  |  | FS-CBL-U-01 (9ZT10AC01) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1U (24 WAYS) EL 56850: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 201 | [5 empty] | FSSS INTERCONNECTION DIAGRAM I/P CONTACTS FROM DDCMIS TO OTH | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-05, CC57-04, CC30-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-04, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-02, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, ZZ99- |  | 0 | 0
2 | FSSS |  |  | FS-CBL-JB-1U-1 (9ZT10AC02) | FSSS-JB-1U (24 WAYS) EL 56850: NEAR S9L | EWLI SYSTEM RIGHT INDICATION BOX EL 56850: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 68 | [5 empty] | FSSS INTERCONNECTION DIAGRAM I/P CONTACTS FROM DDCMIS TO OTH | TRICHY SCOPE CABLE | ZZ99- , BO01-03, BR30-03, BP03-02, BP04-02, BP05-02, BP06-02, BR15-03, BO05-03, ZZ99- |  | 0 | 0
3 | FSSS |  |  | FS-CBL-JB-1U-2 (9ZT10AC03) | FSSS-JB-1U (24 WAYS) EL 56850: NEAR S9L | EWLI SYSTEM LEFT INDICATION BOX EL 56850: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 27 | [5 empty] | FSSS INTERCONNECTION DIAGRAM I/P CONTACTS FROM DDCMIS TO OTH | TRICHY SCOPE CABLE | ZZ99- , BO01-03, ZZ99- |  | 0 | 0
4 | FSSS |  |  | FS-CBL-JB-1U-3 (9ZT10AC04) | FSSS-JB-1U (24 WAYS) EL 56850: NEAR S9L | EWLI SYSTEM RIGHT VALIDATION BOX EL 56850: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 68 | [5 empty] | FSSS INTERCONNECTION DIAGRAM I/P CONTACTS FROM DDCMIS TO OTH | TRICHY SCOPE CABLE | ZZ99- , BO01-03, BR30-03, BP03-02, BP04-02, BP05-02, BP06-02, BR15-03, BO05-03, ZZ99- |  | 0 | 0
5 | FSSS |  |  | FS-CBL-JB-1U-4 (9ZT10AC05) | FSSS-JB-1U (24 WAYS) EL 56850: NEAR S9L | EWLI SYSTEM LEFT VALIDATION BOX EL 56850: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 27 | [5 empty] | FSSS INTERCONNECTION DIAGRAM I/P CONTACTS FROM DDCMIS TO OTH | TRICHY SCOPE CABLE | ZZ99- , BO01-03, ZZ99- |  | 0 | 0
6 | FSSS |  |  | FS-CBL-U-02 (9ZT10AC06) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2U (24 WAYS) EL 20300: NEAR S2R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 150 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN. FAN & SCAN. EMERG.DAMPER | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BD10-03, ZZ99- |  | 0 | 0
7 | FSSS |  |  | FS-CBL-U-03 (9ZT10AC07) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2U (24 WAYS) EL 20300: NEAR S2R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 150 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN. FAN & SCAN. EMERG.DAMPER | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BD10-03, ZZ99- |  | 0 | 0
8 | FSSS |  |  | FS-CBL-JB-2U-1 (9ZT10AC08) | FSSS-JB-2U (24 WAYS) EL 20300: NEAR S2R | SCANNER FAN -B DC-STARTER EL 20300: NEAR S2R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN. FAN & SCAN. EMERG.DAMPER | TRICHY SCOPE CABLE | ZZ99- , BD10-03, ZZ99- |  | 0 | 0
9 | FSSS |  |  | FS-CBL-JB-2U-2 (9ZT10AC09) | FSSS-JB-2U (24 WAYS) EL 20300: NEAR S2R | SCANNER EMERG. DAMPER EL 20300: NEAR S2R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN. FAN & SCAN. EMERG.DAMPER | TRICHY SCOPE CABLE | ZZ99- , BD10-03, ZZ99- |  | 0 | 0
10 | FSSS |  |  | FS-CBL-U-04 (9ZT10AC10) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | SCANNER AIR FAN-A STARTER EL 20300: NEAR S2R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 152 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN.-SEAL AIR FAN STARTER | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-04, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BD10-03, ZZ99- |  | 0 | 0
11 | FSSS |  |  | FS-CBL-U-05 (9ZT10AC11) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | SEAL AIR FAN-A MCCLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN.-SEAL AIR FAN STARTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV62-06, LV63-06, ZZ99- |  | 0 | 0
12 | FSSS |  |  | FS-CBL-U-06 (9ZT10AC12) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | SEAL AIR FAN-B MCCLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN.-SEAL AIR FAN STARTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV62-06, LV63-06, ZZ99- |  | 0 | 0
13 | FSSS |  |  | FS-CBL-U-07 (9ZT10AC13) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | SCANNER AIR FAN-A STARTER EL 20300: NEAR S2R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 163 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCAN.-SEAL AIR FAN STARTER | TRICHY SCOPE CABLE | ZZ99- , CC54-03, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BD10-02, BD11-02, ZZ99- |  | 0 | 0
14 | FSSS |  |  | FS-CBL-U-08 (9ZT10AC14) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3U (48 WAYS) EL 20300: NEAR S2L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 164 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LORV | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, BD18-03, ZZ99- |  | 0 | 0
15 | FSSS |  |  | FS-CBL-JB-3U-1 (9ZT10AC15) | FSSS-JB-3U (48 WAYS) EL 20300: NEAR S2L | LDO RECIRCLE VALVE (HJF87AA201) EL 20300: NEAR S3L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LORV | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
16 | FSSS |  |  | FS-CBL-JB-3U-2 (9ZT10AC16) | FSSS-JB-3U (48 WAYS) EL 20300: NEAR S2L | LIGHT OIL TRIP VALVE (HJF80AA201) EL 20300: NEAR S3L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LORV | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
17 | FSSS |  |  | FS-CBL-U-09 (9ZT10AC17) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-4U (24WAYS) EL 20300: NEAR S2L | 10C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LORV | TRICHY SCOPE CABLE | ZZ99- , CC54-03, CC55-03, CC56-03, CC57-03, CC58-03, CC35-02, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BD18-02, ZZ99- |  | 0 | 0
18 | FSSS |  |  | FS-CBL-JB-4U-1 (9ZT10AC18) | FSSS-JB-4U (24WAYS) EL 20300: NEAR S2L | LDO RECIRCLE VALVE EL 20300: NEAR S3L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LORV | TRICHY SCOPE CABLE | ZZ99- , BD18-02, BD19-02 |  | 0 | 0
19 | FSSS |  |  | FS-CBL-JB-4U-2 (9ZT10AC19) | FSSS-JB-4U (24WAYS) EL 20300: NEAR S2L | LIGHT OIL TRIP VALVE EL 20300: NEAR S3L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 27 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LORV | TRICHY SCOPE CABLE | ZZ99- , BD18-02, BD19-02 |  | 0 | 0
20 | FSSS |  |  | FS-CBL-JB-4U-3 (9ZT10AC20) | FSSS-JB-4U (24WAYS) EL 20300: NEAR S2L | SCANNER EMERG. DAMPER EL 20300: NEAR S2R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 68 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LORV | TRICHY SCOPE CABLE | ZZ99- , BD18-02, BD17-02, BD16-02, BD15-02, BD14-02, BD13-02, BD10-02, BD11-02, ZZ99- |  | 0 | 0
21 | FSSS |  |  | FS-CBL-U-10 (9ZT10AC21) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-5U (72 WAYS) EL 20300: NEAR S12R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 172 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-04, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BD10-03, BD11-03, BD12-03, ZZ99- |  | 0 | 0
22 | FSSS |  |  | FS-CBL-JB-5U-1 (9ZT10AC22) | FSSS-JB-5U (72 WAYS) EL 20300: NEAR S12R | FU EL AIR DAMPER PRESSURE SWITCH- EL. A EL 21100: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
23 | FSSS |  |  | FS-CBL-JB-5U-2 (9ZT10AC23) | FSSS-JB-5U (72 WAYS) EL 20300: NEAR S12R | AUX. AIR DAMPER PRESSURE SWITCH- EL. AB EL 21800: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
24 | FSSS |  |  | FS-CBL-JB-5U-3 (9ZT10AC24) | FSSS-JB-5U (72 WAYS) EL 20300: NEAR S12R | FU EL AIR DAMPER PRESSURE SWITCH- EL. B EL 22500: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
25 | FSSS |  |  | FS-CBL-JB-5U-4 (9ZT10AC25) | FSSS-JB-5U (72 WAYS) EL 20300: NEAR S12R | AUX. AIR DAMPER PRESSURE SWITCH- EL. BC EL 23300: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
26 | FSSS |  |  | FS-CBL-JB-5U-5 (9ZT10AC26) | FSSS-JB-5U (72 WAYS) EL 20300: NEAR S12R | FU EL AIR DAMPER PRESSURE SWITCH- EL. C EL 23900: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
27 | FSSS |  |  | FS-CBL-JB-5U-6 (9ZT10AC27) | FSSS-JB-5U (72 WAYS) EL 20300: NEAR S12R | AUX. AIR DAMPER PRESSURE SWITCH- EL. CD EL 24600: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
28 | FSSS |  |  | FS-CBL-U-11 (9ZT10AC28) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-6U (72 WAYS) EL 20300: NEAR S12R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
29 | FSSS |  |  | FS-CBL-JB-6U-1 (9ZT10AC29) | FSSS-JB-6U (72 WAYS) EL 20300: NEAR S12R | FU EL AIR DAMPER PRESSURE SWITCH- EL. D EL 25300: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
30 | FSSS |  |  | FS-CBL-JB-6U-2 (9ZT10AC30) | FSSS-JB-6U (72 WAYS) EL 20300: NEAR S12R | AUX. AIR DAMPER PRESSURE SWITCH- EL. DE EL 26100: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
31 | FSSS |  |  | FS-CBL-JB-6U-3 (9ZT10AC31) | FSSS-JB-6U (72 WAYS) EL 20300: NEAR S12R | FU EL AIR DAMPER PRESSURE SWITCH- EL. E EL 26800: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
32 | FSSS |  |  | FS-CBL-JB-6U-4 (9ZT10AC32) | FSSS-JB-6U (72 WAYS) EL 20300: NEAR S12R | AUX. AIR DAMPER PRESSURE SWITCH- EL. EF EL 27500: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
33 | FSSS |  |  | FS-CBL-JB-6U-5 (9ZT10AC33) | FSSS-JB-6U (72 WAYS) EL 20300: NEAR S12R | FU EL AIR DAMPER PRESSURE SWITCH- EL. F EL 28200: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
34 | FSSS |  |  | FS-CBL-JB-6U-6 (9ZT10AC34) | FSSS-JB-6U (72 WAYS) EL 20300: NEAR S12R | AUX. AIR DAMPER PRESSURE SWITCH- EL. FF EL 28700: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
35 | FSSS |  |  | FS-CBL-U-12 (9ZT10AC35) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-7U (24 WAYS) EL 7000: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 206 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC30-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-04, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BR71-03, BR69-03, ZZ99- |  | 0 | 0
36 | FSSS |  |  | FS-CBL-7U-01 (9ZT10AC36) | FSSS-JB-7U (24 WAYS) EL 7000: NEAR S4R | OVER FIRE DAMPER PRESSURE SWITCH-OFA UPPER EL 29500: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 112 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | ZZ99- , BR69-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BG19-01, BG18-01, BG17-01, BG16-01, BG15-03, BG20-03, BG21-03, ZZ99- |  | 0 | 0
37 | FSSS |  |  | FS-CBL-7U-02 (9ZT10AC37) | FSSS-JB-7U (24 WAYS) EL 7000: NEAR S4R | OVER FIRE DAMPER PRESSURE SWITCH-OFA LOWER EL 29100: NEAR S18 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 112 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SADC PRESSURE SWITCHES | TRICHY SCOPE CABLE | ZZ99- , BR69-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BG19-01, BG18-01, BG17-01, BG16-01, BG15-03, BG20-03, BG21-03, ZZ99- |  | 0 | 0
38 | FSSS |  |  | FS-CBL-U-13 (9ZT10AC38) | ASP CABINETCONTROL EQUIPMENT ROOM (CER) | SEAL AIR FAN-A MCCLTMCC room | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM CURRENT SIGNAL FROM MCC | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV62-06, LV63-06, ZZ99- |  | 0 | 0
39 | FSSS |  |  | FS-CBL-U-14 (9ZT10AC39) | ASP CABINETCONTROL EQUIPMENT ROOM (CER) | SEAL AIR FAN-B MCCLTMCC room | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM CURRENT SIGNAL FROM MCC | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV62-06, LV63-06, ZZ99- |  | 0 | 0
40 | FSSS |  |  | FS-CBL-S-AA1-1 (9ZT10AC40) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AA1 (6 WAYS) EL 20300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 164 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, BD18-03, ZZ99- |  | 0 | 0
41 | FSSS |  |  | FS-CBL-S-AA1-2 (9ZT10AC41) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AA2 (6 WAYS) EL 20300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 176 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-02, BD18-03, BD19-03, BD20-03, ZZ99- |  | 0 | 0
42 | FSSS |  |  | FS-CBL-S-AA1-3 (9ZT10AC42) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AA3 (6 WAYS) EL 20300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 165 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
43 | FSSS |  |  | FS-CBL-S-AA1-4 (9ZT10AC43) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AA4 (6 WAYS) EL 20300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 165 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
44 | FSSS |  |  | FS-CBL-JB-S-AA 1-1 (9ZT10AC44) | FSSS-JB-S-AA1 (6 WAYS) EL 20300: NEAR S9L | BH EL SCAN HEAD ASSEMBLY- EL. AA1 EL 20263: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
45 | FSSS |  |  | FS-CBL-JB-S-AA 1-2 (9ZT10AC45) | FSSS-JB-S-AA2 (6 WAYS) EL 20300: NEAR S12L | BH EL SCAN HEAD ASSEMBLY- EL. AA2 EL 20263: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
46 | FSSS |  |  | FS-CBL-JB-S-AA 1-3 (9ZT10AC46) | FSSS-JB-S-AA3 (6 WAYS) EL 20300: NEAR S12R | BH EL SCAN HEAD ASSEMBLY- EL. AA3 EL 20263: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
47 | FSSS |  |  | FS-CBL-JB-S-AA 1-4 (9ZT10AC47) | FSSS-JB-S-AA4 (6 WAYS) EL 20300: NEAR S9R | BH EL SCAN HEAD ASSEMBLY- EL. AA4 EL 20263: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
48 | FSSS |  |  | FS-CBL-S-AB1-1 (9ZT10AC48) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AB1 (6 WAYS) EL 20300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 170 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-02, ZZ99- |  | 0 | 0
49 | FSSS |  |  | FS-CBL-S-AB1-2 (9ZT10AC49) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AB2 (6 WAYS) EL 20300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 170 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-02, ZZ99- |  | 0 | 0
50 | FSSS |  |  | FS-CBL-S-AB1-3 (9ZT10AC50) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AB3 (6 WAYS) EL 20300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 166 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
51 | FSSS |  |  | FS-CBL-S-AB1-4 (9ZT10AC51) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-AB4 (6 WAYS) EL 20300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 165 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
52 | FSSS |  |  | FS-CBL-JB-S-AB 1-1 (9ZT10AC52) | FSSS-JB-S-AB1 (6 WAYS) EL 20300: NEAR S9L | BH EL SCAN HEAD ASSEMBLY- EL. AB1 EL 21793: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
53 | FSSS |  |  | FS-CBL-JB-S-AB 1-2 (9ZT10AC53) | FSSS-JB-S-AB2 (6 WAYS) EL 20300: NEAR S12L | BH EL SCAN HEAD ASSEMBLY- EL. AB2 EL 21793: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
54 | FSSS |  |  | FS-CBL-JB-S-AB 1-3 (9ZT10AC54) | FSSS-JB-S-AB3 (6 WAYS) EL 20300: NEAR S12R | BH EL SCAN HEAD ASSEMBLY- EL. AB3 EL 21793: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
55 | FSSS |  |  | FS-CBL-JB-S-AB 1-4 (9ZT10AC55) | FSSS-JB-S-AB4 (6 WAYS) EL 20300: NEAR S9R | BH EL SCAN HEAD ASSEMBLY- EL. AB4 EL 21793: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
56 | FSSS |  |  | FS-CBL-S-BC1-1 (9ZT10AC56) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-BC1 (6 WAYS) EL 20300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 170 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC54-04, CC55-04, CC56-04, CC57-04, CC58-04, CC35-03, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, ZZ99- |  | 0 | 0
57 | FSSS |  |  | FS-CBL-S-BC1-2 (9ZT10AC57) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-BC2 (6 WAYS) EL 20300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 165 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, ZZ99- |  | 0 | 0
58 | FSSS |  |  | FS-CBL-S-BC1-3 (9ZT10AC58) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-BC3 (6 WAYS) EL 20300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 161 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
59 | FSSS |  |  | FS-CBL-S-BC1-4 (9ZT10AC59) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-BC4 (6 WAYS) EL 20300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 161 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
60 | FSSS |  |  | FS-CBL-JB-S-BC 1-1 (9ZT10AC60) | FSSS-JB-S-BC1 (6 WAYS) EL 20300: NEAR S9L | BH EL SCAN HEAD ASSEMBLY- EL. BC1 EL 23300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
61 | FSSS |  |  | FS-CBL-JB-S-BC 1-2 (9ZT10AC61) | FSSS-JB-S-BC2 (6 WAYS) EL 20300: NEAR S12L | BH EL SCAN HEAD ASSEMBLY- EL. BC2 EL 23300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
62 | FSSS |  |  | FS-CBL-JB-S-BC 1-3 (9ZT10AC62) | FSSS-JB-S-BC3 (6 WAYS) EL 20300: NEAR S12R | BH EL SCAN HEAD ASSEMBLY- EL. BC3 EL 23300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
63 | FSSS |  |  | FS-CBL-JB-S-BC 1-4 (9ZT10AC63) | FSSS-JB-S-BC4 (6 WAYS) EL 20300: NEAR S9R | BH EL SCAN HEAD ASSEMBLY- EL. BC4 EL 23300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
64 | FSSS |  |  | FS-CBL-S-CD1-1 (9ZT10AC64) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-CD1 (6 WAYS) EL 23300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 169 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, ZZ99- |  | 0 | 0
65 | FSSS |  |  | FS-CBL-S-CD1-2 (9ZT10AC65) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-CD2 (6 WAYS) EL 23300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 168 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, ZZ99- |  | 0 | 0
66 | FSSS |  |  | FS-CBL-S-CD1-3 (9ZT10AC66) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-CD3 (6 WAYS) EL 23300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 160 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
67 | FSSS |  |  | FS-CBL-S-CD1-4 (9ZT10AC67) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-CD4 (6 WAYS) EL 23300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 160 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
68 | FSSS |  |  | FS-CBL-JB-S-CD 1-1 (9ZT10AC68) | FSSS-JB-S-CD1 (6 WAYS) EL 23300: NEAR S9L | BH EL SCAN HEAD ASSEMBLY- EL. CD1 EL 24633: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
69 | FSSS |  |  | FS-CBL-JB-S-CD 1-2 (9ZT10AC69) | FSSS-JB-S-CD2 (6 WAYS) EL 23300: NEAR S12L | BH EL SCAN HEAD ASSEMBLY- EL. CD2 EL 24633: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
70 | FSSS |  |  | FS-CBL-JB-S-CD 1-3 (9ZT10AC70) | FSSS-JB-S-CD3 (6 WAYS) EL 23300: NEAR S12R | BH EL SCAN HEAD ASSEMBLY- EL. CD3 EL 24633: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
71 | FSSS |  |  | FS-CBL-JB-S-CD 1-4 (9ZT10AC71) | FSSS-JB-S-CD4 (6 WAYS) EL 23300: NEAR S9R | BH EL SCAN HEAD ASSEMBLY- EL. CD4 EL 24633: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
72 | FSSS |  |  | FS-CBL-S-DE1-1 (9ZT10AC72) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-DE1 (6 WAYS) EL 23300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 166 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, ZZ99- |  | 0 | 0
73 | FSSS |  |  | FS-CBL-S-DE1-2 (9ZT10AC73) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-DE2 (6 WAYS) EL 23300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 166 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, ZZ99- |  | 0 | 0
74 | FSSS |  |  | FS-CBL-S-DE1-3 (9ZT10AC74) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-DE3 (6 WAYS) EL 23300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 160 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-04, ZZ99- |  | 0 | 0
75 | FSSS |  |  | FS-CBL-S-DE1-4 (9ZT10AC75) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-DE4 (6 WAYS) EL 23300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 161 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | ZZ99- , CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC34-03, CC93-02, CC84-02, CC86-04, CC88-02, CC92-04, LR05-04, LV79-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
76 | FSSS |  |  | FS-CBL-JB-S-DE 1-1 (9ZT10AC76) | FSSS-JB-S-DE1 (6 WAYS) EL 23300: NEAR S9L | BH EL SCAN HEAD ASSEMBLY- EL. DE1 EL 26300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
77 | FSSS |  |  | FS-CBL-JB-S-DE 1-2 (9ZT10AC77) | FSSS-JB-S-DE2 (6 WAYS) EL 23300: NEAR S12L | BH EL SCAN HEAD ASSEMBLY- EL. DE2 EL 26300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
78 | FSSS |  |  | FS-CBL-JB-S-DE 1-3 (9ZT10AC78) | FSSS-JB-S-DE3 (6 WAYS) EL 23300: NEAR S12R | BH EL SCAN HEAD ASSEMBLY- EL. DE3 EL 26300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
79 | FSSS |  |  | FS-CBL-JB-S-DE 1-4 (9ZT10AC79) | FSSS-JB-S-DE4 (6 WAYS) EL 23300: NEAR S9R | BH EL SCAN HEAD ASSEMBLY- EL. DE4 EL 26300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
80 | FSSS |  |  | FS-CBL-S-EF1-1 (9ZT10AC80) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-EF1 (6 WAYS) EL 26300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
81 | FSSS |  |  | FS-CBL-S-EF1-2 (9ZT10AC81) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-EF2 (6 WAYS) EL 26300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
82 | FSSS |  |  | FS-CBL-S-EF1-3 (9ZT10AC82) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-EF3 (6 WAYS) EL 26300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
83 | FSSS |  |  | FS-CBL-S-EF1-4 (9ZT10AC83) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-EF4 (6 WAYS) EL 26300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
84 | FSSS |  |  | FS-CBL-JB-S-EF 1-1 (9ZT10AC84) | FSSS-JB-S-EF1 (6 WAYS) EL 26300: NEAR S9L | BH EL SCAN HEAD ASSEMBLY- EL. EF1 EL 27473: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
85 | FSSS |  |  | FS-CBL-JB-S-EF 1-2 (9ZT10AC85) | FSSS-JB-S-EF2 (6 WAYS) EL 26300: NEAR S12L | BH EL SCAN HEAD ASSEMBLY- EL. EF2 EL 27473: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
86 | FSSS |  |  | FS-CBL-JB-S-EF 1-3 (9ZT10AC86) | FSSS-JB-S-EF3 (6 WAYS) EL 26300: NEAR S12R | BH EL SCAN HEAD ASSEMBLY- EL. EF3 EL 27473: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
87 | FSSS |  |  | FS-CBL-JB-S-EF 1-4 (9ZT10AC87) | FSSS-JB-S-EF4 (6 WAYS) EL 26300: NEAR S9R | BH EL SCAN HEAD ASSEMBLY- EL. EF4 EL 27473: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
88 | FSSS |  |  | FS-CBL-S-FF1-1 (9ZT10AC88) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-FF1 (6 WAYS) EL 26300: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
89 | FSSS |  |  | FS-CBL-S-FF1-2 (9ZT10AC89) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-FF2 (6 WAYS) EL 26300: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
90 | FSSS |  |  | FS-CBL-S-FF1-3 (9ZT10AC90) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-FF3 (6 WAYS) EL 26300: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
91 | FSSS |  |  | FS-CBL-S-FF1-4 (9ZT10AC91) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-S-FF4 (6 WAYS) EL 26300: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
92 | FSSS |  |  | FS-CBL-JB-S-FF 1-1 (9ZT10AC92) | FSSS-JB-S-FF1 (6 WAYS) EL 26300: NEAR S9L | BH EL SCAN HEAD ASSEMBLY- EL. FF1 EL 28700: NEAR S9L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
93 | FSSS |  |  | FS-CBL-JB-S-FF 1-2 (9ZT10AC93) | FSSS-JB-S-FF2 (6 WAYS) EL 26300: NEAR S12L | BH EL SCAN HEAD ASSEMBLY- EL. FF2 EL 28700: NEAR S12L | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
94 | FSSS |  |  | FS-CBL-JB-S-FF 1-3 (9ZT10AC94) | FSSS-JB-S-FF3 (6 WAYS) EL 26300: NEAR S12R | BH EL SCAN HEAD ASSEMBLY- EL. FF3 EL 28700: NEAR S12R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
95 | FSSS |  |  | FS-CBL-JB-S-FF 1-4 (9ZT10AC95) | FSSS-JB-S-FF4 (6 WAYS) EL 26300: NEAR S9R | BH EL SCAN HEAD ASSEMBLY- EL. FF4 EL 28700: NEAR S9R | 02P X 1.3 Paired Screened(I) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME SCANNER HEAD ASSEMBLY | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
96 | FSSS |  |  | FS-CBL-S-AA (9ZT10AC96) | FSSS CABINET (FLAME SCAN. AMPLIFIER)CONTROL EQUIPMENT ROOM (CER) | SADC PAN ELCONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME INTENSITY SIGNAL | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
97 | FSSS |  |  | FS-CBL-S-AB (9ZT10AC97) | FSSS CABINET (FLAME SCAN. AMPLIFIER)CONTROL EQUIPMENT ROOM (CER) | SADC PAN ELCONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME INTENSITY SIGNAL | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
98 | FSSS |  |  | FS-CBL-S-BC (9ZT10AC98) | FSSS CABINET (FLAME SCAN. AMPLIFIER)CONTROL EQUIPMENT ROOM (CER) | SADC PAN ELCONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME INTENSITY SIGNAL | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
99 | FSSS |  |  | FS-CBL-S-CD (9ZT10AC99) | FSSS CABINET (FLAME SCAN. AMPLIFIER)CONTROL EQUIPMENT ROOM (CER) | SADC PAN ELCONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME INTENSITY SIGNAL | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
100 | FSSS |  |  | FS-CBL-S-DE (9ZT10BC01) | FSSS CABINET (FLAME SCAN. AMPLIFIER)CONTROL EQUIPMENT ROOM (CER) | SADC PAN ELCONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME INTENSITY SIGNAL | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
101 | FSSS |  |  | FS-CBL-S-EF (9ZT10BC02) | FSSS CABINET (FLAME SCAN. AMPLIFIER)CONTROL EQUIPMENT ROOM (CER) | SADC PAN ELCONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME INTENSITY SIGNAL | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
102 | FSSS |  |  | FS-CBL-S-FF (9ZT10BC03) | FSSS CABINET (FLAME SCAN. AMPLIFIER)CONTROL EQUIPMENT ROOM (CER) | SADC PAN ELCONTROL EQUIPMENT ROOM (CER) | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FLAME INTENSITY SIGNAL | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
103 | FSSS |  |  | FS-CBL-U-15 (9ZT10BC04) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SA HDR/COLD AIR DP TRANSMITTER) [FSSS-LIE-1] EL 0 NEAR MILL C & D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 150 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FURNACE PR. TRANSMITTER | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
104 | FSSS |  |  | FS-CBL-U-16 (9ZT10BC05) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (Furnace Pr. Transmitter) [FSSS-LIE-2] EL 56850; NEAR S10L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 172 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FURNACE PR. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, BR06-05, BG23-03, BG24-03, BG22-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, ZZ99- |  | 0 | 0
105 | FSSS |  |  | FS-CBL-U-17 (9ZT10BC06) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (Furnace Pr. Transmitter) [FSSS-LIE-3] EL 56850; NEAR S10R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 147 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FURNACE PR. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, ZZ99- |  | 0 | 0
106 | FSSS |  |  | FS-CBL-U-18 (9ZT10BC07) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (Furnace Pr. Transmitter) [FSSS-LIE-3] EL 56850; NEAR S10R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 147 | [5 empty] | FSSS INTERCONNECTION DIAGRAM FURNACE PR. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, ZZ99- |  | 0 | 0
107 | FSSS |  |  | FS-CBL-U-19 (9ZT10BC08) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (PA HDR PRESSURE TRANSMITTER) [FSSS-LIE-4] EL 21000 ; NEAR S25 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 150 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PA HEADER TRANSMITTERS | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
108 | FSSS |  |  | FS-CBL-U-20 (9ZT10BC09) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (PA HDR PRESSURE TRANSMITTER) [FSSS-LIE-4] EL 21000 ; NEAR S25 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 150 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PA HEADER TRANSMITTERS | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
109 | FSSS |  |  | FS-CBL-U-21 (9ZT10BC10) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (PA HDR PRESSURE TRANSMITTER) [FSSS-LIE-4] EL 21000 ; NEAR S25 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 150 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PA HEADER TRANSMITTERS | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
110 | FSSS |  |  | FS-CBL-U-22 (9ZT10BC11) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-8U (48 WAYS) EL 20300: NEAR S2L | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CR01-L3, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, ZZ99- |  | 0 | 0
111 | FSSS |  |  | FS-CBL-JB-8U-1 (9ZT10BC12) | FSSS-JB-8U (48 WAYS) EL 20300: NEAR S2L | LO SUPPLY PRESSURE TRANSMITTER EL 20300 NEAR S3L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
112 | FSSS |  |  | FS-CBL-JB-8U-2 (9ZT10BC13) | FSSS-JB-8U (48 WAYS) EL 20300: NEAR S2L | LO HEADER PRESSURE TRANSMITTER EL 20300 NEAR S3L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
113 | FSSS |  |  | FS-CBL-JB-8U-3 (9ZT10BC14) | FSSS-JB-8U (48 WAYS) EL 20300: NEAR S2L | LO HEADER PRESSURE TRANSMITTER EL 20300 NEAR S3L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
114 | FSSS |  |  | FS-CBL-JB-8U-4 (9ZT10BC15) | FSSS-JB-8U (48 WAYS) EL 20300: NEAR S2L | LO HEADER PRESSURE TRANSMITTER EL 20300 NEAR S3L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
115 | FSSS |  |  | FS-CBL-JB-8U-5 (9ZT10BC16) | FSSS-JB-8U (48 WAYS) EL 20300: NEAR S2L | ATOM. AIR PRESSURE TRANSMITTER EL 20300 NEAR S3L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
116 | FSSS |  |  | FS-CBL-JB-8U-6 (9ZT10BC17) | FSSS-JB-8U (48 WAYS EL 20300: NEAR S2L | ATOM. AIR PRESSURE TRANSMITTER EL 20300 NEAR S3L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
117 | FSSS |  |  | FS-CBL-JB-8U-7 (9ZT10BC18) | FSSS-JB-8U (48 WAYS) EL 20300: NEAR S2L | ATOM. AIR PRESSURE TRANSMITTER EL 20300 NEAR S3L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM LO & ATOM AIR TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  | 0 | 0
118 | FSSS |  |  | FS-CBL-U-23 (9ZT10BC19) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SCANNER AIR PR/DP TRANSMITTERS) [FSSS-LIE-5] EL 20300 ; NEAR S3R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 114 | [5 empty] | FSSS INTERCONNECTION DIAGRAM SCANNER LINE TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BD10-03, BD11-03, ZZ99- |  | 0 | 0
119 | FSSS |  |  | FS- CBL-AB-01 (9ZT10BC20) | FSSS CABINETCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-AB ( 24 WAYS) EL 20300: NEAR S9L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 163 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, ZZ99- |  | 0 | 0
120 | FSSS |  |  | FS- CBL-JB-AB- 01 (9ZT10BC21) | FSSS-JB-AB ( 24 WAYS) EL 20300: NEAR S9L | HEA EXCITER (CORNER-1) EL 21793: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
121 | FSSS |  |  | FS- CBL-JB-AB- 02 (9ZT10BC22) | FSSS-JB-AB ( 24 WAYS) EL 20300: NEAR S9L | HEA EXCITER (CORNER-2) EL 21793: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
122 | FSSS |  |  | FS- CBL-JB-AB- 03 (9ZT10BC23) | FSSS-JB-AB ( 24 WAYS) EL 20300: NEAR S9L | HEA EXCITER (CORNER-3) EL 21793: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
123 | FSSS |  |  | FS- CBL-JB-AB- 04 (9ZT10BC24) | FSSS-JB-AB ( 24 WAYS) EL 20300: NEAR S9L | HEA EXCITER (CORNER-4) EL 21793: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
124 | FSSS |  |  | FS- CBL-CD-01 (9ZT10BC25) | FSA CABINETCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-CD (24 WAYS) EL 23300: NEAR S9L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, ZZ99- |  | 0 | 0
125 | FSSS |  |  | FS- CBL-JB-CD- 01 (9ZT10BC26) | FSSS-JB-CD (24 WAYS) EL 23300: NEAR S9L | HEA EXCITER (CORNER-1) EL 24633: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
126 | FSSS |  |  | FS- CBL-JB-CD- 02 (9ZT10BC27) | FSSS-JB-CD (24 WAYS) EL 23300: NEAR S9L | HEA EXCITER (CORNER-2) EL 24633: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
127 | FSSS |  |  | FS- CBL-JB-CD- 03 (9ZT10BC28) | FSSS-JB-CD (24 WAYS) EL 23300: NEAR S9L | HEA EXCITER (CORNER-3) EL 24633: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
128 | FSSS |  |  | FS- CBL-JB-CD- 04 (9ZT10BC29) | FSSS-JB-CD (24 WAYS) EL 23300: NEAR S9L | HEA EXCITER (CORNER-4) EL 24633: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
129 | FSSS |  |  | FS- CBL-EF-01 (9ZT10BC30) | FSSS CABINET CONTROL EQUIPMENT ROOM (CER) | FSSS-JB-EF ( 24 WAYS) EL 26300: NEAR S9L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
130 | FSSS |  |  | FS- CBL-JB-EF- 01 (9ZT10BC31) | FSSS-JB-EF ( 24 WAYS) EL 26300: NEAR S9L | HEA EXCITER (CORNER-1) EL 27473: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
131 | FSSS |  |  | FS- CBL-JB-EF- 02 (9ZT10BC32) | FSSS-JB-EF ( 24 WAYS) EL 26300: NEAR S9L | HEA EXCITER (CORNER-2) EL 27473: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
132 | FSSS |  |  | FS- CBL-JB-EF- 03 (9ZT10BC33) | FSSS-JB-EF ( 24 WAYS) EL 26300: NEAR S9L | HEA EXCITER (CORNER-3) EL 27473: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
133 | FSSS |  |  | FS- CBL-JB-EF- 04 (9ZT10BC34) | FSSS-JB-EF ( 24 WAYS) EL 26300: NEAR S9L | HEA EXCITER (CORNER-4) EL 27473: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. FLAME INTENSITY SIGANAL | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
134 | FSSS |  |  | FS- CBL-AB1-01 (9ZT10BC35) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1AB1 (24 ways) EL 20300: NEAR S9L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BD18-02, ZZ99- |  | 0 | 0
135 | FSSS |  |  | FS- CBL-JB-1AB 1-1 (9ZT10BC36) | FSSS-JB-1AB1 (24 WAYS) EL 20300: NEAR S9L | HEA ADV./RET. MECHANISM EL 21793: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
136 | FSSS |  |  | FS- CBL-JB-1AB 1-2 (9ZT10BC37) | FSSS-JB-1AB1 (24 WAYS) EL 20300: NEAR S9L | SCAVENGE NOZZLE VALVE EL 21793: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
137 | FSSS |  |  | FS- CBL-JB-1AB 1-3 (9ZT10BC38) | FSSS-JB-1AB1 (24 WAYS) EL 20300: NEAR S9L | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
138 | FSSS |  |  | FS- CBL-JB-1AB 1-4 (9ZT10BC39) | FSSS-JB-1AB1 (24 WAYS) EL 20300: NEAR S9L | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
139 | FSSS |  |  | FS- CBL-JB-2AB 1-1 (9ZT10BC40) | FSSS-JB-2AB1 ( 48 WAYS) EL 20300: NEAR S9L | HEA ADV./RET. MECHANISM EL 21793: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
140 | FSSS |  |  | FS- CBL-JB-2AB 1-2 (9ZT10BC41) | FSSS-JB-2AB1 ( 48 WAYS) EL 20300: NEAR S9L | SCAVENGE NOZZLE VALVE EL 21793: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
141 | FSSS |  |  | FS- CBL-JB-2AB 1-3 (9ZT10BC42) | FSSS-JB-2AB1 ( 48 WAYS) EL 20300: NEAR S9L | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 21793: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
142 | FSSS |  |  | FS- CBL-AB2-01 (9ZT10BC43) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1AB2 ( 24 WAYS) EL 20300: NEAR S12L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 162 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BD18-02, ZZ99- |  | 0 | 0
143 | FSSS |  |  | FS- CBL-JB-1AB 2-1 (9ZT10BC44) | FSSS-JB-1AB2 ( 24 WAYS) EL 20300: NEAR S12L | HEA ADV./RET. MECHANISM EL 21793: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
144 | FSSS |  |  | FS- CBL-JB-1AB 2-2 (9ZT10BC45) | FSSS-JB-1AB2 ( 24 WAYS) EL 20300: NEAR S12L | SCAVENGE NOZZLE VALVE EL 21793: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
145 | FSSS |  |  | FS- CBL-JB-1AB 2-3 (9ZT10BC46) | FSSS-JB-1AB2 ( 24 WAYS) EL 20300: NEAR S12L | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
146 | FSSS |  |  | FS- CBL-JB-1AB 2-4 (9ZT10BC47) | FSSS-JB-1AB2 ( 24 WAYS) EL 20300: NEAR S12L | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
147 | FSSS |  |  | FS- CBL-JB-2AB 2-1 (9ZT10BC48) | FSSS-JB-2AB2 (48 WAYS) EL 20300: NEAR S12L | HEA ADV./RET. MECHANISM EL 21793: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
148 | FSSS |  |  | FS- CBL-JB-2AB 2-2 (9ZT10BC49) | FSSS-JB-2AB2 (48 WAYS) EL 20300: NEAR S12L | SCAVENGE NOZZLE VALVE EL 21793: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
149 | FSSS |  |  | FS- CBL-JB-2AB 2-3 (9ZT10BC50) | FSSS-JB-2AB2 (48 WAYS) EL 20300: NEAR S12L | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 21793: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
150 | FSSS |  |  | FS- CBL-AB3-01 (9ZT10BC51) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1AB3 (24 WAYS) EL 20300: NEAR S12R | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, ZZ99- |  | 0 | 0
151 | FSSS |  |  | FS- CBL-JB-1AB 3-01 (9ZT10BC52) | FSSS-JB-1AB3 (24 WAYS) EL 20300: NEAR S12R | HEA ADV./RET. MECHANISM EL 21793: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
152 | FSSS |  |  | FS- CBL-JB-1AB 3-02 (9ZT10BC53) | FSSS-JB-1AB3 (24 WAYS) EL 20300: NEAR S12R | SCAVENGE NOZZLE VALVE EL 21793: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
153 | FSSS |  |  | FS- CBL-JB-1AB 3-03 (9ZT10BC54) | FSSS-JB-1AB3 (24 WAYS) EL 20300: NEAR S12R | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
154 | FSSS |  |  | FS- CBL-JB-1AB 3-04 (9ZT10BC55) | FSSS-JB-1AB3 (24 WAYS) EL 20300: NEAR S12R | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
155 | FSSS |  |  | FS- CBL-JB-2AB 3-1 (9ZT10BC56) | FSSS-JB-2AB3 (48 WAYS) EL 20300: NEAR S12R | HEA ADV./RET. MECHANISM EL 21793: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
156 | FSSS |  |  | FS- CBL-JB-2AB 3-2 (9ZT10BC57) | FSSS-JB-2AB3 (48 WAYS) EL 20300: NEAR S12R | SCAVENGE NOZZLE VALVE EL 21793: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
157 | FSSS |  |  | FS- CBL-JB-2AB 3-3 (9ZT10BC58) | FSSS-JB-2AB3 (48 WAYS) EL 20300: NEAR S12R | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 21793: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
158 | FSSS |  |  | FS- CBL-AB4-01 (9ZT10BC59) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1AB4 (24 WAYS) EL 20300: NEAR S9R | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, ZZ99- |  | 0 | 0
159 | FSSS |  |  | FS- CBL-JB-1AB 4-1 (9ZT10BC60) | FSSS-JB-1AB4 (24 WAYS) EL 20300: NEAR S9R | HEA ADV./RET. MECHANISM EL 21793: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
160 | FSSS |  |  | FS- CBL-JB-1AB 4-2 (9ZT10BC61) | FSSS-JB-1AB4 (24 WAYS) EL 20300: NEAR S9R | SCAVENGE NOZZLE VALVE EL 21793: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
161 | FSSS |  |  | FS- CBL-JB-1AB 4-3 (9ZT10BC62) | FSSS-JB-1AB4 (24 WAYS) EL 20300: NEAR S9R | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
162 | FSSS |  |  | FS- CBL-JB-1AB 4-4 (9ZT10BC63) | FSSS-JB-1AB4 (24 WAYS) EL 20300: NEAR S9R | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
163 | FSSS |  |  | FS- CBL-JB-2AB 4-1 (9ZT10BC64) | FSSS-JB-2AB4 (48 WAYS) EL 20300: NEAR S9R | HEA ADV./RET. MECHANISM EL 21793: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
164 | FSSS |  |  | FS- CBL-JB-2AB 4-2 (9ZT10BC65) | FSSS-JB-2AB4 (48 WAYS) EL 20300: NEAR S9R | SCAVENGE NOZZLE VALVE EL 21793: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
165 | FSSS |  |  | FS- CBL-JB-2AB 4-3 (9ZT10BC66) | FSSS-JB-2AB4 (48 WAYS) EL 20300: NEAR S9R | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 21793: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
166 | FSSS |  |  | FS- CBL-CD1-01 (9ZT10BC67) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1CD1 (24 WAYS) EL 23300: NEAR S9L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, ZZ99- |  | 0 | 0
167 | FSSS |  |  | FS- CBL-JB-1CD 1-1 (9ZT10BC68) | FSSS-JB-1CD1 (24 WAYS) EL 23300: NEAR S9L | HEA ADV./RET. MECHANISM EL 24633: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
168 | FSSS |  |  | FS- CBL-JB-1CD 1-2 (9ZT10BC69) | FSSS-JB-1CD1 (24 WAYS) EL 23300: NEAR S9L | SCAVENGE NOZZLE VALVE EL 24633: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
169 | FSSS |  |  | FS- CBL-JB-1CD 1-3 (9ZT10BC70) | FSSS-JB-1CD1 (24 WAYS) EL 23300: NEAR S9L | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
170 | FSSS |  |  | FS- CBL-JB-1CD 1-4 (9ZT10BC71) | FSSS-JB-1CD1 (24 WAYS) EL 23300: NEAR S9L | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
171 | FSSS |  |  | FS- CBL-JB-2CD 1-1 (9ZT10BC72) | FSSS-JB-2CD1 ( 48 WAYS) EL 23300: NEAR S9L | HEA ADV./RET. MECHANISM EL 24633: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
172 | FSSS |  |  | FS- CBL-JB-2CD 1-2 (9ZT10BC73) | FSSS-JB-2CD1 ( 48 WAYS) EL 23300: NEAR S9L | SCAVENGE NOZZLE VALVE EL 24633: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
173 | FSSS |  |  | FS- CBL-JB-2CD 1-3 (9ZT10BC74) | FSSS-JB-2CD1 ( 48WAYS) EL 23300: NEAR S9L | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 24633: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
174 | FSSS |  |  | FS- CBL-CD2-01 (9ZT10BC75) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1CD2 ( 24 WAYS) EL 23300: NEAR S12L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, ZZ99- |  | 0 | 0
175 | FSSS |  |  | FS- CBL-JB-1CD 2-1 (9ZT10BC76) | FSSS-JB-1CD2 ( 24 WAYS) EL 23300: NEAR S12L | HEA ADV./RET. MECHANISM EL 24633: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
176 | FSSS |  |  | FS- CBL-JB-1CD 2-2 (9ZT10BC77) | FSSS-JB-1CD2 ( 24 WAYS) EL 23300: NEAR S12L | SCAVENGE NOZZLE VALVE EL 24633: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
177 | FSSS |  |  | FS- CBL-JB-1CD 2-3 (9ZT10BC78) | FSSS-JB-1CD2 ( 24 WAYS) EL 23300: NEAR S12L | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
178 | FSSS |  |  | FS- CBL-JB-1CD 2-4 (9ZT10BC79) | FSSS-JB-1CD2 ( 24 WAYS) EL 23300: NEAR S12L | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
179 | FSSS |  |  | FS- CBL-JB-2CD 2-1 (9ZT10BC80) | FSSS-JB-2CD2 ( 48 WAYS) EL 23300: NEAR S12L | HEA ADV./RET. MECHANISM EL 24633: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
180 | FSSS |  |  | FS- CBL-JB-2CD 2-2 (9ZT10BC81) | FSSS-JB-2CD2 ( 48 WAYS) EL 23300: NEAR S12L | SCAVENGE NOZZLE VALVE EL 24633: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
181 | FSSS |  |  | FS- CBL-JB-2CD 2-3 (9ZT10BC82) | FSSS-JB-2CD2 ( 48 WAYS) EL 23300: NEAR S12L | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 24633: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
182 | FSSS |  |  | FS- CBL-CD3-01 (9ZT10BC83) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1CD3 (24 WAYS) EL 23300: NEAR S12R | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, ZZ99- |  | 0 | 0
183 | FSSS |  |  | FS- CBL-JB-1CD 3-1 (9ZT10BC84) | FSSS-JB-1CD3 (24 WAYS) EL 23300: NEAR S12R | HEA ADV./RET. MECHANISM EL 24633: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
184 | FSSS |  |  | FS- CBL-JB-1CD 3-2 (9ZT10BC85) | FSSS-JB-1CD3 (24 WAYS) EL 23300: NEAR S12R | SCAVENGE NOZZLE VALVE EL 24633: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
185 | FSSS |  |  | FS- CBL-JB-1CD 3-3 (9ZT10BC86) | FSSS-JB-1CD3 (24 WAYS) EL 23300: NEAR S12R | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
186 | FSSS |  |  | FS- CBL-JB-1CD 3-4 (9ZT10BC87) | FSSS-JB-1CD3 (24 WAYS) EL 23300: NEAR S12R | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
187 | FSSS |  |  | FS- CBL-JB-2CD 3-1 (9ZT10BC88) | FSSS-JB-2CD3 (48 WAYS) EL 23300: NEAR S12R | HEA ADV./RET. MECHANISM EL 24633: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
188 | FSSS |  |  | FS- CBL-JB-2CD 3-2 (9ZT10BC89) | FSSS-JB-2CD3 (48 WAYS) EL 23300: NEAR S12R | SCAVENGE NOZZLE VALVE EL 24633: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
189 | FSSS |  |  | FS- CBL-JB-2CD 3-3 (9ZT10BC90) | FSSS-JB-2CD3 (48 WAYS) EL 23300: NEAR S12R | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 24633: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
190 | FSSS |  |  | FS- CBL-CD4-01 (9ZT10BC91) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1CD4 (24 ways) EL 23300: NEAR S9R | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 167 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ23-02, BQ09-02, BQ10-02, BQ25-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, ZZ99- |  | 0 | 0
191 | FSSS |  |  | FS- CBL-JB-1CD 4-01 (9ZT10BC92) | FSSS-JB-1CD4 ( 24 WAYS) EL 23300: NEAR S9R | HEA ADV./RET. MECHANISM EL 24633: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
192 | FSSS |  |  | FS- CBL-JB-1CD 4-2 (9ZT10BC93) | FSSS-JB-1CD4 (24 WAYS) EL 23300: NEAR S9R | SCAVENGE NOZZLE VALVE EL 24633: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
193 | FSSS |  |  | FS- CBL-JB-1CD 4-3 (9ZT10BC94) | FSSS-JB-1CD4 (24 WAYS) EL 23300: NEAR S9R | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
194 | FSSS |  |  | FS- CBL-JB-1CD 4-4 (9ZT10BC95) | FSSS-JB-1CD4 (48 WAYS) EL 23300: NEAR S9R | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
195 | FSSS |  |  | FS- CBL-JB-2CD 4-1 (9ZT10BC96) | FSSS-JB-2CD4 (48 WAYS) EL 23300: NEAR S9R | HEA ADV./RET. MECHANISM EL 24633: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
196 | FSSS |  |  | FS- CBL-JB-2CD 4-2 (9ZT10BC97) | FSSS-JB-2CD4 (48 WAYS) EL 23300: NEAR S9R | SCAVENGE NOZZLE VALVE EL 24633: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
197 | FSSS |  |  | FS- CBL-JB-2CD 4-3 (9ZT10BC98) | FSSS-JB-2CD4 (48 WAYS) EL 23300: NEAR S9R | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 24633: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
198 | FSSS |  |  | FS- CBL-EF1-01 (9ZT10BC99) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1EF1 (24 WAYS) EL 26300: NEAR S9L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
199 | FSSS |  |  | FS- CBL-JB-1EF 1-1 (9ZT10CC01) | FSSS-JB-1EF1 (24 WAYS) EL 26300: NEAR S9L | HEA ADV./RET. MECHANISM EL 27473: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
200 | FSSS |  |  | FS- CBL-JB-1EF 1-2 (9ZT10CC02) | FSSS-JB-1EF1 (24 WAYS) EL 26300: NEAR S9L | SCAVENGE NOZZLE VALVE EL 27473: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
201 | FSSS |  |  | FS- CBL-JB-1EF 1-3 (9ZT10CC03) | FSSS-JB-1EF1 (24 WAYS) EL 26300: NEAR S9L | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
202 | FSSS |  |  | FS- CBL-JB-1EF 1-4 (9ZT10CC04) | FSSS-JB-1EF1 (24 WAYS) EL 26300: NEAR S9L | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S9L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
203 | FSSS |  |  | FS- CBL-JB-2EF 1-1 (9ZT10CC05) | FSSS-JB-2EF1 (48 WAYS) EL 26300: NEAR S9L | HEA ADV./RET. MECHANISM EL 27473: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
204 | FSSS |  |  | FS- CBL-JB-2EF 1-2 (9ZT10CC06) | FSSS-JB-2EF1 (48 WAYS) EL 26300: NEAR S9L | SCAVENGE NOZZLE VALVE EL 27473: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
205 | FSSS |  |  | FS- CBL-JB-2EF 1-3 (9ZT10CC07) | FSSS-JB-2EF1 (48 WAYS) EL 26300: NEAR S9L | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 27473: NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
206 | FSSS |  |  | FS- CBL-EF2-01 (9ZT10CC08) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1EF2 ( 24 WAYS) EL 26300: NEAR S12L | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
207 | FSSS |  |  | FS- CBL-JB-1EF 2-1 (9ZT10CC09) | FSSS-JB-1EF2 ( 24 WAYS) EL 26300: NEAR S12L | HEA ADV./RET. MECHANISM EL 27473: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
208 | FSSS |  |  | FS- CBL-JB-1EF 2-2 (9ZT10CC10) | FSSS-JB-1EF2 ( 24 WAYS) EL 26300: NEAR S12L | SCAVENGE NOZZLE VALVE EL 27473: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
209 | FSSS |  |  | FS- CBL-JB-1EF 2-3 (9ZT10CC11) | FSSS-JB-1EF2 ( 24 WAYS) EL 26300: NEAR S12L | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
210 | FSSS |  |  | FS- CBL-JB-1EF 2-4 (9ZT10CC12) | FSSS-JB-1EF2 ( 24 WAYS) EL 26300: NEAR S12L | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S12L | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
211 | FSSS |  |  | FS- CBL-JB-2EF 2-1 (9ZT10CC13) | FSSS-JB-2EF2 (48 WAYS) EL 26300: NEAR S12L | HEA ADV./RET. MECHANISM EL 27473: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
212 | FSSS |  |  | FS- CBL-JB-2EF 2-2 (9ZT10CC14) | FSSS-JB-2EF2 (48 WAYS) EL 26300: NEAR S12L | SCAVENGE NOZZLE VALVE EL 27473: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
213 | FSSS |  |  | FS- CBL-JB-2EF 2-3 (9ZT10CC15) | FSSS-JB-2EF2 (48 WAYS) EL 26300: NEAR S12L | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 27473: NEAR S12L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
214 | FSSS |  |  | FS- CBL-EF3-01 (9ZT10CC16) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1EF3 (24 WAYS) EL 26300: NEAR S12R | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
215 | FSSS |  |  | FS- CBL-JB-1EF 3-1 (9ZT10CC17) | FSSS-JB-1EF3 (24 WAYS) EL 26300: NEAR S12R | HEA ADV./RET. MECHANISM EL 27473: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
216 | FSSS |  |  | FS- CBL-JB-1EF 3-2 (9ZT10CC18) | FSSS-JB-1EF3 (24 WAYS) EL 26300: NEAR S12R | SCAVENGE NOZZLE VALVE EL 27473: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
217 | FSSS |  |  | FS- CBL-JB-1EF 3-3 (9ZT10CC19) | FSSS-JB-1EF3 (24 WAYS) EL 26300: NEAR S12R | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
218 | FSSS |  |  | FS- CBL-JB-1EF 3-4 (9ZT10CC20) | FSSS-JB-1EF3 (24 WAYS) EL 26300: NEAR S12R | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S12R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
219 | FSSS |  |  | FS- CBL-JB-2EF 3-1 (9ZT10CC21) | FSSS-JB-2EF3 ( 48 WAYS) EL 26300: NEAR S12R | HEA ADV./RET. MECHANISM EL 27473: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
220 | FSSS |  |  | FS- CBL-JB-2EF 3-2 (9ZT10CC22) | FSSS-JB-2EF3 (48 WAYS) EL 26300: NEAR S12R | SCAVENGE NOZZLE VALVE EL 27473: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
221 | FSSS |  |  | FS- CBL-JB-2EF 3-3 (9ZT10CC23) | FSSS-JB-2EF3 (48 WAYS) EL 26300: NEAR S12R | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 27473: NEAR S12R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
222 | FSSS |  |  | FS- CBL-EF4-01 (9ZT10CC24) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1EF4 (24 WAYS) EL 26300: NEAR S9R | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
223 | FSSS |  |  | FS- CBL-JB-1EF 4-1 (9ZT10CC25) | FSSS-JB-1EF4 (24 WAYS) EL 26300: NEAR S9R | HEA ADV./RET. MECHANISM EL 27473: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
224 | FSSS |  |  | FS- CBL-JB-1EF 4-2 (9ZT10CC26) | FSSS-JB-1EF4 (24 WAYS) EL 26300: NEAR S9R | SCAVENGE NOZZLE VALVE EL 27473: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
225 | FSSS |  |  | FS- CBL-JB-1EF 4-3 (9ZT10CC27) | FSSS-JB-1EF4 (24 WAYS) EL 26300: NEAR S9R | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
226 | FSSS |  |  | FS- CBL-JB-1EF 4-4 (9ZT10CC28) | FSSS-JB-1EF4 (24 WAYS) EL 26300: NEAR S9R | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S9R | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
227 | FSSS |  |  | FS- CBL-JB-2EF 4-1 (9ZT10CC29) | FSSS-JB-2EF4 ( 48 WAYS) EL 26300: NEAR S9R | HEA ADV./RET. MECHANISM EL 27473: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
228 | FSSS |  |  | FS- CBL-JB-2EF 4-2 (9ZT10CC30) | FSSS-JB-2EF4 ( 48 WAYS) EL 26300: NEAR S9R | SCAVENGE NOZZLE VALVE EL 27473: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
229 | FSSS |  |  | FS- CBL-JB-2EF 4-3 (9ZT10CC31) | FSSS-JB-2EF4 ( 48 WAYS) EL 26300: NEAR S9R | LOCAL OIL GUN MAINTENANCE SWITCH BOX EL 27473: NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. HEA &SCAVANGE VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
230 | FSSS |  |  | FS- CBL-AB1-02 (9ZT10CC32) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2AB1 (48 WAYS) EL 20300: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 151 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-04, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-L3, IC04-L3, IC05-L3, IC06-L3, IR07-04, IC50-04, IC51-04, IC52-04, BR17-02, BR18-04, ZZ99- |  | 0 | 0
231 | FSSS |  |  | FS- CBL-AB2-02 (9ZT10CC33) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2AB2 (48 WAYS) EL 20300: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 147 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-R4, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-04, ZZ99- |  | 0 | 0
232 | FSSS |  |  | FS- CBL-AB3-02 (9ZT10CC34) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2AB3 (48 WAYS) EL 20300: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 148 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
233 | FSSS |  |  | FS- CBL-AB4-02 (9ZT10CC35) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2AB4 (48 WAYS) EL 20300: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 148 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
234 | FSSS |  |  | FS- CBL-CD1-02 (9ZT10CC36) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2CD1 ( 48 WAYS) EL 23300: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 154 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-04, BR19-03, ZZ99- |  | 0 | 0
235 | FSSS |  |  | FS- CBL-CD2-02 (9ZT10CC37) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2CD2 (48 WAYS) EL 23300: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 154 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-04, BR19-03, ZZ99- |  | 0 | 0
236 | FSSS |  |  | FS- CBL-CD3-02 (9ZT10CC38) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2CD3 (48 WAYS) EL 23300: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 148 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
237 | FSSS |  |  | FS- CBL-CD4-02 (9ZT10CC39) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2CD4 (48 WAYS) EL 23300: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 147 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
238 | FSSS |  |  | FS- CBL-EF1-02 (9ZT10CC40) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2EF1 (48 WAYS) EL 26300: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
239 | FSSS |  |  | FS- CBL-EF2-02 (9ZT10CC41) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2EF2 (48 WAYS) EL 26300: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
240 | FSSS |  |  | FS- CBL-EF3-02 (9ZT10CC42) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2EF3 ( 48 WAYS) EL 26300: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
241 | FSSS |  |  | FS- CBL-EF4-02 (9ZT10CC43) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2EF4 ( 48 WAYS) EL 26300: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LGM SWITCH BOX | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
242 | FSSS |  |  | FS- CBL-AB1-03 (9ZT10CC44) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3AB1 (72 WAYS) EL 20300: NEAR S9L | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 149 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, ZZ99- |  | 0 | 0
243 | FSSS |  |  | FSSS-CBL-JB-3A B1-1 (9ZT10CC45) | FSSS-JB-3AB1 (72 WAYS) EL 20300: NEAR S9L | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
244 | FSSS |  |  | FSSS-CBL-JB-3A B1-2 (9ZT10CC46) | FSSS-JB-3AB1 (72 WAYS) EL 20300: NEAR S9L | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
245 | FSSS |  |  | FSSS-CBL-JB-3A B1-3 (9ZT10CC47) | FSSS-JB-3AB1 (72 WAYS) EL 20300: NEAR S9L | LIGHT OIL MAN ISO VALVE EL 21793: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
246 | FSSS |  |  | FSSS-CBL-JB-3A B1-4 (9ZT10CC48) | FSSS-JB-3AB1 (72 WAYS) EL 20300: NEAR S9L | ATOM. AIR MAN ISO VALVE EL 21793: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
247 | FSSS |  |  | FSSS-CBL-JB-3A B1-5 (9ZT10CC49) | FSSS-JB-3AB1 (72 WAYS) EL 20300: NEAR S9L | OIL GUN ENGAGE-LS EL 21793: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
248 | FSSS |  |  | FS- CBL-AB2-03 (9ZT10CC50) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3AB2 (72 WAYS) EL 20300: NEAR S12L | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 152 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-02, BR18-02, ZZ99- |  | 0 | 0
249 | FSSS |  |  | FSSS-CBL-JB-3A B2-1 (9ZT10CC51) | FSSS-JB-3AB2 (72 WAYS) EL 20300: NEAR S12L | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
250 | FSSS |  |  | FSSS-CBL-JB-3A B2-2 (9ZT10CC52) | FSSS-JB-3AB2 (72 WAYS) EL 20300: NEAR S12L | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
251 | FSSS |  |  | FSSS-CBL-JB-3A B2-3 (9ZT10CC53) | FSSS-JB-3AB2 (72 WAYS) EL 20300: NEAR S12L | LIGHT OIL MAN ISO VALVE EL 21793: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
252 | FSSS |  |  | FSSS-CBL-JB-3A B2-4 (9ZT10CC54) | FSSS-JB-3AB2 (72 WAYS) EL 20300: NEAR S12L | ATOM. AIR MAN ISO VALVE EL 21793: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
253 | FSSS |  |  | FSSS-CBL-JB-3A B2-5 (9ZT10CC55) | FSSS-JB-3AB2 (72 WAYS) EL 20300: NEAR S12L | OIL GUN ENGAGE-LS EL 21793: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
254 | FSSS |  |  | FS- CBL-AB3-03 (9ZT10CC56) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3AB3 (72 WAYS) EL 20300: NEAR S12R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 145 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
255 | FSSS |  |  | FSSS-CBL-JB-3A B3-1 (9ZT10CC57) | FSSS-JB-3AB3 (72 WAYS) EL 20300: NEAR S12R | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
256 | FSSS |  |  | FSSS-CBL-JB-3A B3-2 (9ZT10CC58) | FSSS-JB-3AB3 (72 WAYS) EL 20300: NEAR S12R | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
257 | FSSS |  |  | FSSS-CBL-JB-3A B3-3 (9ZT10CC59) | FSSS-JB-3AB3 (72 WAYS) EL 20300: NEAR S12R | LIGHT OIL MAN ISO VALVE EL 21793: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
258 | FSSS |  |  | FSSS-CBL-JB-3A B3-4 (9ZT10CC60) | FSSS-JB-3AB3 (72 WAYS) EL 20300: NEAR S12R | ATOM. AIR MAN ISO VALVE EL 21793: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
259 | FSSS |  |  | FSSS-CBL-JB-3A B3-5 (9ZT10CC61) | FSSS-JB-3AB3 (72 WAYS) EL 20300: NEAR S12R | OIL GUN ENGAGE-LS EL 21793: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
260 | FSSS |  |  | FS- CBL-AB4-03 (9ZT10CC62) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3AB4 (72 WAYS) EL 20300: NEAR S9R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 145 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
261 | FSSS |  |  | FSSS-CBL-JB-3A B4-1 (9ZT10CC63) | FSSS-JB-3AB4 (72 WAYS) EL 20300: NEAR S9R | LIGHT OIL NOZZLE VALVE EL 21793: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
262 | FSSS |  |  | FSSS-CBL-JB-3A B4-2 (9ZT10CC64) | FSSS-JB-3AB4 (72 WAYS) EL 20300: NEAR S9R | ATOM. AIR NOZZLE VALVE EL 21793: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
263 | FSSS |  |  | FSSS-CBL-JB-3A B4-3 (9ZT10CC65) | FSSS-JB-3AB4 (72 WAYS) EL 20300: NEAR S9R | LIGHT OIL MAN ISO VALVE EL 21793: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
264 | FSSS |  |  | FSSS-CBL-JB-3A B4-4 (9ZT10CC66) | FSSS-JB-3AB4 (72 WAYS) EL 20300: NEAR S9R | ATOM. AIR MAN ISO VALVE EL 21793: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
265 | FSSS |  |  | FSSS-CBL-JB-3A B4-5 (9ZT10CC67) | FSSS-JB-3AB4 (72 WAYS) EL 20300: NEAR S9R | OIL GUN ENGAGE-LS EL 21793: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
266 | FSSS |  |  | FS- CBL-CD1-03 (9ZT10CC68) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3CD1 (72 WAYS) EL 23300: NEAR S9L | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 152 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-R4, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-02, BR18-02, BR19-03, ZZ99- |  | 0 | 0
267 | FSSS |  |  | FSSS-CBL-JB-3C D1-1 (9ZT10CC69) | FSSS-JB-3CD1 (72 WAYS) EL 23300: NEAR S9L | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
268 | FSSS |  |  | FSSS-CBL-JB-3C D1-2 (9ZT10CC70) | FSSS-JB-3CD1 (72 WAYS) EL 23300: NEAR S9L | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
269 | FSSS |  |  | FSSS-CBL-JB-3C D1-3 (9ZT10CC71) | FSSS-JB-3CD1 (72 WAYS) EL 23300: NEAR S9L | LIGHT OIL MAN ISO VALVE EL 24633: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
270 | FSSS |  |  | FSSS-CBL-JB-3C D1-4 (9ZT10CC72) | FSSS-JB-3CD1 (72 WAYS) EL 23300: NEAR S9L | ATOM. AIR MAN ISO VALVE EL 24633: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
271 | FSSS |  |  | FSSS-CBL-JB-3C D1-5 (9ZT10CC73) | FSSS-JB-3CD1 (72 WAYS) EL 23300: NEAR S9L | OIL GUN ENGAGE-LS EL 24633: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
272 | FSSS |  |  | FS- CBL-CD2-03 (9ZT10CC74) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3CD2 (72 WAYS) EL 23300: NEAR S12L | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 152 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, BR19-03, ZZ99- |  | 0 | 0
273 | FSSS |  |  | FSSS-CBL-JB-3C D2-1 (9ZT10CC75) | FSSS-JB-3CD2 (72 WAYS) EL 23300: NEAR S12L | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
274 | FSSS |  |  | FSSS-CBL-JB-3C D2-2 (9ZT10CC76) | FSSS-JB-3CD2 (72 WAYS) EL 23300: NEAR S12L | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
275 | FSSS |  |  | FSSS-CBL-JB-3C D2-3 (9ZT10CC77) | FSSS-JB-3CD2 (72 WAYS) EL 23300: NEAR S12L | LIGHT OIL MAN ISO VALVE EL 24633: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
276 | FSSS |  |  | FSSS-CBL-JB-3C D2-4 (9ZT10CC78) | FSSS-JB-3CD2 (72 WAYS) EL 23300: NEAR S12L | ATOM. AIR MAN ISO VALVE EL 24633: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
277 | FSSS |  |  | FSSS-CBL-JB-3C D2-5 (9ZT10CC79) | FSSS-JB-3CD2 (72 WAYS) EL 23300: NEAR S12L | OIL GUN ENGAGE-LS EL 24633: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
278 | FSSS |  |  | FS- CBL-CD3-03 (9ZT10CC80) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3CD3 (72 WAYS) EL 23300: NEAR S12R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 145 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
279 | FSSS |  |  | FSSS-CBL-JB-3C D3-1 (9ZT10CC81) | FSSS-JB-3CD3 (72 WAYS) EL 23300: NEAR S12R | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
280 | FSSS |  |  | FSSS-CBL-JB-3C D3-2 (9ZT10CC82) | FSSS-JB-3CD3 (72 WAYS) EL 23300: NEAR S12R | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
281 | FSSS |  |  | FSSS-CBL-JB-3C D3-3 (9ZT10CC83) | FSSS-JB-3CD3 (72 WAYS) EL 23300: NEAR S12R | LIGHT OIL MAN ISO VALVE EL 24633: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
282 | FSSS |  |  | FSSS-CBL-JB-3C D3-4 (9ZT10CC84) | FSSS-JB-3CD3 (72 WAYS) EL 23300: NEAR S12R | ATOM. AIR MAN ISO VALVE EL 24633: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
283 | FSSS |  |  | FSSS-CBL-JB-3C D3-5 (9ZT10CC85) | FSSS-JB-3CD3 (72 WAYS) EL 23300: NEAR S12R | OIL GUN ENGAGE-LS EL 24633: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
284 | FSSS |  |  | FS- CBL-CD4-03 (9ZT10CC86) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3CD4 (72 WAYS) EL 23300: NEAR S9R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 145 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, ZZ99- |  | 0 | 0
285 | FSSS |  |  | FSSS-CBL-JB-3C D4-1 (9ZT10CC87) | FSSS-JB-3CD4 (72 WAYS) EL 23300: NEAR S9R | LIGHT OIL NOZZLE VALVE EL 24633: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
286 | FSSS |  |  | FSSS-CBL-JB-3C D4-2 (9ZT10CC88) | FSSS-JB-3CD4 (72 WAYS) EL 23300: NEAR S9R | ATOM. AIR NOZZLE VALVE EL 24633: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
287 | FSSS |  |  | FSSS-CBL-JB-3C D4-3 (9ZT10CC89) | FSSS-JB-3CD4 (72 WAYS) EL 23300: NEAR S9R | LIGHT OIL MAN ISO VALVE EL 24633: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
288 | FSSS |  |  | FSSS-CBL-JB-3C D4-4 (9ZT10CC90) | FSSS-JB-3CD4 (72 WAYS) EL 23300: NEAR S9R | ATOM. AIR MAN ISO VALVE EL 24633: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
289 | FSSS |  |  | FSSS-CBL-JB-3C D4-5 (9ZT10CC91) | FSSS-JB-3CD4 (72 WAYS) EL 23300: NEAR S9R | OIL GUN ENGAGE-LS EL 24633: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
290 | FSSS |  |  | FS- CBL-EF1-03 (9ZT10CC92) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3EF1 (72 WAYS) EL 26300: NEAR S9L | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
291 | FSSS |  |  | FSSS-CBL-JB-3E F1-1 (9ZT10CC93) | FSSS-JB-3EF1 (72 WAYS) EL 26300: NEAR S9L | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
292 | FSSS |  |  | FSSS-CBL-JB-3E F1-2 (9ZT10CC94) | FSSS-JB-3EF1 (72 WAYS) EL 26300: NEAR S9L | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
293 | FSSS |  |  | FSSS-CBL-JB-3E F1-3 (9ZT10CC95) | FSSS-JB-3EF1 (72 WAYS) EL 26300: NEAR S9L | LIGHT OIL MAN ISO VALVE EL 27473: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
294 | FSSS |  |  | FSSS-CBL-JB-3E F1-4 (9ZT10CC96) | FSSS-JB-3EF1 (72 WAYS) EL 26300: NEAR S9L | ATOM. AIR MAN ISO VALVE EL 27473: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
295 | FSSS |  |  | FSSS-CBL-JB-3E F-5 (9ZT10CC97) | FSSS-JB-3EF1 (72 WAYS) EL 26300: NEAR S9L | OIL GUN ENGAGE-LS EL 27473: NEAR S9L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
296 | FSSS |  |  | FS- CBL-EF2-03 (9ZT10CC98) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3EF2 (72 WAYS) EL 26300: NEAR S12L | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
297 | FSSS |  |  | FSSS-CBL-JB-3E F2-1 (9ZT10CC99) | FSSS-JB-3EF2 (72 WAYS) EL 26300: NEAR S12L | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
298 | FSSS |  |  | FSSS-CBL-JB-3E F2-2 (9ZT10DC01) | FSSS-JB-3EF2 (72 WAYS) EL 26300: NEAR S12L | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S12L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
299 | FSSS |  |  | FSSS-CBL-JB-3E F2-3 (9ZT10DC02) | FSSS-JB-3EF2 (72 WAYS) EL 26300: NEAR S12L | LIGHT OIL MAN ISO VALVE EL 27473: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
300 | FSSS |  |  | FSSS-CBL-JB-3E F2-4 (9ZT10DC03) | FSSS-JB-3EF2 (72 WAYS) EL 26300: NEAR S12L | ATOM. AIR MAN ISO VALVE EL 27473: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
301 | FSSS |  |  | FSSS-CBL-JB-3E F2-5 (9ZT10DC04) | FSSS-JB-3EF2 (72 WAYS) EL 26300: NEAR S12L | OIL GUN ENGAGE-LS EL 27473: NEAR S12L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 12 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
302 | FSSS |  |  | FS- CBL-EF3-03 (9ZT10DC05) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3EF3 (72 WAYS) EL 26300: NEAR S12R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
303 | FSSS |  |  | FSSS-CBL-JB-3E F3-1 (9ZT10DC06) | FSSS-JB-3EF3 (72 WAYS) EL 26300: NEAR S12R | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
304 | FSSS |  |  | FSSS-CBL-JB-3E F3-2 (9ZT10DC07) | FSSS-JB-3EF3 (72 WAYS) EL 26300: NEAR S12R | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S12R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
305 | FSSS |  |  | FSSS-CBL-JB-3E F3-3 (9ZT10DC08) | FSSS-JB-3EF3 (72 WAYS) EL 26300: NEAR S12R | LIGHT OIL MAN ISO VALVE EL 27473: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
306 | FSSS |  |  | FSSS-CBL-JB-3E F3-4 (9ZT10DC09) | FSSS-JB-3EF3 (72 WAYS) EL 26300: NEAR S12R | ATOM. AIR MAN ISO VALVE EL 27473: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
307 | FSSS |  |  | FSSS-CBL-JB-3E F3-5 (9ZT10DC10) | FSSS-JB-3EF3 (72 WAYS) EL 26300: NEAR S12R | OIL GUN ENGAGE-LS EL 27473: NEAR S12R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
308 | FSSS |  |  | FS- CBL-EF4-03 (9ZT10DC11) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3EF4 (72 WAYS) EL 26300: NEAR S9R | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 125 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
309 | FSSS |  |  | FSSS-CBL-JB-3E F4-1 (9ZT10DC12) | FSSS-JB-3EF4 (72 WAYS) EL 26300: NEAR S9R | LIGHT OIL NOZZLE VALVE EL 27473: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
310 | FSSS |  |  | FSSS-CBL-JB-3E F4-2 (9ZT10DC13) | FSSS-JB-3EF4 (72 WAYS) EL 26300: NEAR S9R | ATOM. AIR NOZZLE VALVE EL 27473: NEAR S9R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
311 | FSSS |  |  | FSSS-CBL-JB-3E F4-3 (9ZT10DC14) | FSSS-JB-3EF4 (72 WAYS) EL 26300: NEAR S9R | LIGHT OIL MAN ISO VALVE EL 27473: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
312 | FSSS |  |  | FSSS-CBL-JB-3E F4-4 (9ZT10DC15) | FSSS-JB-3EF4 (72 WAYS) EL 26300: NEAR S9R | ATOM. AIR MAN ISO VALVE EL 27473: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
313 | FSSS |  |  | FSSS-CBL-JB-3E F4-5 (9ZT10DC16) | FSSS-JB-3EF4 (72 WAYS) EL 26300: NEAR S9R | OIL GUN ENGAGE-LS EL 27473: NEAR S9R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM OIL EL. LONV. ATOM. AIR NOZZLE | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
314 | FSSS |  |  | FS- CBL-A-01 (9ZT10DC17) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 237 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, BC16-02, ZZ99- |  | 0 | 0
315 | FSSS |  |  | FS- CBL-A-02 (9ZT10DC18) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 237 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, BC16-02, ZZ99- |  | 0 | 0
316 | FSSS |  |  | FS- CBL-A-03 (9ZT10DC19) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 237 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, BC16-02, ZZ99- |  | 0 | 0
317 | FSSS |  |  | FS- CBL-A-04 (9ZT10DC20) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
318 | FSSS |  |  | FS- CBL-A-05 (9ZT10DC21) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC01-03, LR08-03, MR07-03, MA08-03, ZZ99- |  | 0 | 0
319 | FSSS |  |  | FSSS-CBL-JB-5A -1 (9ZT10DC22) | FSSS-JB-5A (24 WAYS) EL 10300 NEAR MILL A | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL A | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
320 | FSSS |  |  | FSSS-CBL-JB-5A -2 (9ZT10DC23) | FSSS-JB-5A (24 WAYS) EL 10300 NEAR MILL A | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL A | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
321 | FSSS |  |  | FSSS-CBL-JB-5A -3 (9ZT10DC24) | FSSS-JB-5A (24 WAYS) EL 10300 NEAR MILL A | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL A | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
322 | FSSS |  |  | FS- CBL-B-01 (9ZT10DC25) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 228 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, ZZ99- |  | 0 | 0
323 | FSSS |  |  | FS- CBL-B-02 (9ZT10DC26) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 228 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, ZZ99- |  | 0 | 0
324 | FSSS |  |  | FS- CBL-B-03 (9ZT10DC27) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 228 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, ZZ99- |  | 0 | 0
325 | FSSS |  |  | FS- CBL-B-04 (9ZT10DC28) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
326 | FSSS |  |  | FS- CBL-B-05 (9ZT10DC29) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC01-03, LR08-03, MR07-03, MA08-03, ZZ99- |  | 0 | 0
327 | FSSS |  |  | FSSS-CBL-JB-5B -1 (9ZT10DC30) | FSSS-JB-5B (24 WAYS) EL 10300 NEAR MILL B | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL B | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
328 | FSSS |  |  | FSSS-CBL-JB-5B -2 (9ZT10DC31) | FSSS-JB-5B (24 WAYS) EL 10300 NEAR MILL B | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL B | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
329 | FSSS |  |  | FSSS-CBL-JB-5B -3 (9ZT10DC32) | FSSS-JB-5B (24 WAYS) EL 10300 NEAR MILL B | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL B | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
330 | FSSS |  |  | FS- CBL-C-01 (9ZT10DC33) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 232 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | 0 | 0
331 | FSSS |  |  | FS- CBL-C-02 (9ZT10DC34) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 232 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | 0 | 0
332 | FSSS |  |  | FS- CBL-C-03 (9ZT10DC35) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 232 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, CC80-02, CC24-02, CC66-03, CC67-03, CC68-03, CC41-01, CC85-02, CC86-03, CC88-03, CC92-02, LR05-02, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99- |  | 0 | 0
333 | FSSS |  |  | FS- CBL-C-04 (9ZT10DC36) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  | 0 | 0
334 | FSSS |  |  | FS- CBL-C-05 (9ZT10DC37) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC01-03, LR08-03, MR07-03, MA08-03, ZZ99- |  |  | 0
335 | FSSS |  |  | FSSS-CBL-JB-5C -1 (9ZT10DC38) | FSSS-JB-5C (24 WAYS) EL 10300 NEAR MILL C | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL C | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
336 | FSSS |  |  | FSSS-CBL-JB-5C -2 (9ZT10DC39) | FSSS-JB-5C (24 WAYS) EL 10300 NEAR MILL C | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL C | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
337 | FSSS |  |  | FSSS-CBL-JB-5C -3 (9ZT10DC40) | FSSS-JB-5C (24 WAYS) EL 10300 NEAR MILL C | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL C | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
338 | FSSS |  |  | FS- CBL-D-01 (9ZT10DC41) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 217 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
339 | FSSS |  |  | FS- CBL-D-02 (9ZT10DC42) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 217 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
340 | FSSS |  |  | FS- CBL-D-03 (9ZT10DC43) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 217 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
341 | FSSS |  |  | FS- CBL-D-04 (9ZT10DC44) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
342 | FSSS |  |  | FS- CBL-D-05 (9ZT10DC45) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC01-03, LR08-03, MR07-03, MA08-03, ZZ99- |  |  | 0
343 | FSSS |  |  | FSSS-CBL-JB-5D -1 (9ZT10DC46) | FSSS-JB-5D (24 WAYS) EL 10300 NEAR MILL D | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL D | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
344 | FSSS |  |  | FSSS-CBL-JB-5D -2 (9ZT10DC47) | FSSS-JB-5D (24 WAYS) EL 10300 NEAR MILL D | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL D | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
345 | FSSS |  |  | FSSS-CBL-JB-5D -3 (9ZT10DC48) | FSSS-JB-5D (24 WAYS) EL 10300 NEAR MILL D | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL D | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
346 | FSSS |  |  | FS- CBL-E-01 (9ZT10DC49) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 217 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
347 | FSSS |  |  | FS- CBL-E-02 (9ZT10DC50) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 217 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
348 | FSSS |  |  | FS- CBL-E-03 (9ZT10DC51) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 217 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
349 | FSSS |  |  | FS- CBL-E-04 (9ZT10DC52) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
350 | FSSS |  |  | FS- CBL-E-05 (9ZT10DC53) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC01-03, LR08-03, MR07-03, MA08-03, ZZ99- |  |  | 0
351 | FSSS |  |  | FSSS-CBL-JB-5E -1 (9ZT10DC54) | FSSS-JB-5E (24 WAYS) EL 10300 NEAR MILL E | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
352 | FSSS |  |  | FSSS-CBL-JB-5E -2 (9ZT10DC55) | FSSS-JB-5E (24 WAYS) EL 10300 NEAR MILL E | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
353 | FSSS |  |  | FSSS-CBL-JB-5E -3 (9ZT10DC56) | FSSS-JB-5E (24 WAYS) EL 10300 NEAR MILL E | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL E | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
354 | FSSS |  |  | FS- CBL-F-01 (9ZT10DC57) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 221 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC20-02, BC21-02, BC22-02, ZZ99- |  |  | 0
355 | FSSS |  |  | FS- CBL-F-02 (9ZT10DC58) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | 07C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 221 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC20-02, BC21-02, BC22-02, ZZ99- |  |  | 0
356 | FSSS |  |  | FS- CBL-F-03 (9ZT10DC59) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | 16C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 221 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC90-03, LR07-03, LV74-03, LV25-L4, LV75-03, LV77-03, LR10-R5, CR01-L2, QR03-L3, BQ20-L3, BQ19-L3, BQ06-02, BQ05-02, BQ04-02, BQ03-R1, BQ02-R1, QR01-02, BQ01-02, BR44-02, BD09-02, BD08-02, BR03-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC20-02, BC21-02, BC22-02, ZZ99- |  |  | 0
357 | FSSS |  |  | FS- CBL-F-04 (9ZT10DC60) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
358 | FSSS |  |  | FS- CBL-F-05 (9ZT10DC61) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | ZZ99- , CC01-03, LR08-03, MR07-03, MA08-03, ZZ99- |  |  | 0
359 | FSSS |  |  | FSSS-CBL-JB-5F -1 (9ZT10DC62) | FSSS-JB-5F (24 WAYS) EL 10300 NEAR MILL F | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
360 | FSSS |  |  | FSSS-CBL-JB-5F -2 (9ZT10DC63) | FSSS-JB-5F (24 WAYS) EL 10300 NEAR MILL F | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
361 | FSSS |  |  | FSSS-CBL-JB-5F -3 (9ZT10DC64) | FSSS-JB-5F (24 WAYS) EL 10300 NEAR MILL F | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL F | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION HAG. DISCH. GATE & | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
362 | FSSS |  |  | FS- CBL-A-06 (9ZT10DC65) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , CC01-04, LR08-04, MR07-04, MA08-04, ZZ99- |  |  | 0
363 | FSSS |  |  | FS- CBL-A-07 (9ZT10DC66) | PULVERISER MOTOR-A BREAKERHT SWITCHGEAR ROOM | FSSS CABINET (CJF14 TBA)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , MA08-04, MR07-04, LR08-04, CC01-04, ZZ99- |  |  | 0
364 | FSSS |  |  | FS- CBL-B-06 (9ZT10DC67) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-B BREAKERHT SWITCHGEAR ROOM | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , CC01-04, LR08-04, MR07-04, MA08-04, ZZ99- |  |  | 0
365 | FSSS |  |  | FS- CBL-B-07 (9ZT10DC68) | PULVERISER MOTOR-B BREAKERHT SWITCHGEAR ROOM | FSSS CABINET (CJF14 TBA)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , MA08-04, MR07-04, LR08-04, CC01-04, ZZ99- |  |  | 0
366 | FSSS |  |  | FS- CBL-C-06 (9ZT10DC69) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-C BREAKERHT SWITCHGEAR ROOM | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , CC01-04, LR08-04, MR07-04, MA08-04, ZZ99- |  |  | 0
367 | FSSS |  |  | FS- CBL-C-07 (9ZT10DC70) | PULVERISER MOTOR-C BREAKERHT SWITCHGEAR ROOM | FSSS CABINET (CJF19 TBA)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , MA08-04, MR07-04, LR08-04, CC01-04, ZZ99- |  |  | 0
368 | FSSS |  |  | FS- CBL-D-06 (9ZT10DC71) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-D BREAKERHT SWITCHGEAR ROOM | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , CC01-04, LR08-04, MR07-04, MA08-04, ZZ99- |  |  | 0
369 | FSSS |  |  | FS- CBL-D-07 (9ZT10DC72) | PULVERISER MOTOR-D BREAKERHT SWITCHGEAR ROOM | FSSS CABINET (CJF19 TBA)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , MA08-04, MR07-04, LR08-04, CC01-04, ZZ99- |  |  | 0
370 | FSSS |  |  | FS- CBL-E-06 (9ZT10DC73) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-E BREAKERHT SWITCHGEAR ROOM | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , CC01-04, LR08-04, MR07-04, MA08-04, ZZ99- |  |  | 0
371 | FSSS |  |  | FS- CBL-E-07 (9ZT10DC74) | PULVERISER MOTOR-E BREAKERHT SWITCHGEAR ROOM | FSSS CABINET (CJF24 TBA)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , MA08-04, MR07-04, LR08-04, CC01-04, ZZ99- |  |  | 0
372 | FSSS |  |  | FS- CBL-F-06 (9ZT10DC75) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PULVERISER MOTOR-E BREAKERHT SWITCHGEAR ROOM | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , CC01-04, LR08-04, MR07-04, MA08-04, ZZ99- |  |  | 0
373 | FSSS |  |  | FS- CBL-F-07 (9ZT10DC76) | PULVERISER MOTOR-F BREAKERHT SWITCHGEAR ROOM | FSSS CABINET (CJF24 TBA)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 86 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR BREAKER | PEM SCOPE CABLE | ZZ99- , MA08-04, MR07-04, LR08-04, CC01-04, ZZ99- |  |  | 0
374 | FSSS |  |  | FS- CBL-A-08 (9ZT10DC77) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-5A (24 WAYS) EL 10300 NEAR MILL A | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 249 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-05, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-L3, IC04-L3, IC05-L3, IC06-L3, IR07-02, IC50-02, IC51-02, IC52-02, BR16-03, BA01-03, BA02-03, BA03-03, BA04-03, BA10-03, BA11-03, BA12-03, BA13-03, BA14-04, BA15-04, BR39-03, BB12-03, ZZ99- |  |  | 0
375 | FSSS |  |  | FS- CBL-A-09 (9ZT10DC78) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2A (48 WAYS) EL 17000 NEAR FEEDER A | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 221 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BC01-03, BC02-03, BC03-03, BC29-03, BC30-03, BC31-03, BC11-03, BC14-03, BC15-03, BC16-03, ZZ99- |  |  | 0
376 | FSSS |  |  | FS- CBL-JB-1A- 01 (9ZT10DC79) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
377 | FSSS |  |  | FS- CBL-JB-1A- 02 (9ZT10DC80) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
378 | FSSS |  |  | FS- CBL-JB-1A- 03 (9ZT10DC81) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | PULVERISER SEAL AIR VALVE EL 17000 NEAR FEEDER A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
379 | FSSS |  |  | FS- CBL-JB-1A- 04 (9ZT10DC82) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | FEEDER SEAL AIR VALVE EL 17000 NEAR FEEDER A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
380 | FSSS |  |  | FS- CBL-JB-1A- 05 (9ZT10DC83) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
381 | FSSS |  |  | FS- CBL-JB-1A- 06 (9ZT10DC84) | FSSS-JB-1A (48 WAYS) EL 17000 NEAR FEEDER A | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL A | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
382 | FSSS |  |  | FS- CBL-JB-2A- 01 (9ZT10DC85) | FSSS-JB-2A (48 WAYS) EL 17000 NEAR FEEDER A | PULVERISER SEAL AIR VALVE EL 17000 NEAR FEEDER A | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
383 | FSSS |  |  | FS- CBL-JB-2A- 02 (9ZT10DC86) | FSSS-JB-2A (48 WAYS) EL 17000 NEAR FEEDER A | FEEDER SEAL AIR VALVE EL 17000 NEAR FEEDER A | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
384 | FSSS |  |  | FS- CBL-JB-2A- 03 (9ZT10DC87) | FSSS-JB-2A (48 WAYS) EL 17000 NEAR FEEDER A | FEEDER INLET GATE EL 17125 ; NEAR FEEDER A | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
385 | FSSS |  |  | FS- CBL-JB-2A- 04 (9ZT10DC88) | FSSS-JB-2A (48 WAYS) EL 17000 NEAR FEEDER A | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER A | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
386 | FSSS |  |  | FS- CBL-JB-2A- 05 (9ZT10DC89) | FSSS-JB-2A (48 WAYS) EL 17000 NEAR FEEDER A | BURNER OUTLET GATE (MCC) EL 22720 ; NEAR FEEDER A | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
387 | FSSS |  |  | FS- CBL-B-08 (9ZT10DC90) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-5B (24 WAYS) EL 10300 NEAR MILL B | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 242 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-04, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-L3, IC04-L3, IC05-L3, IC06-L3, IR07-04, IC50-04, IC51-04, IC52-04, BR16-03, BA01-03, BA02-03, BA03-03, BA04-03, BA10-03, BA11-03, BA12-03, BA13-03, BA14-04, BA15-04, BR39-03, BB12-03, ZZ99- |  |  | 0
388 | FSSS |  |  | FS- CBL-B-09 (9ZT10DC91) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2B (48 WAYS) EL 17000 NEAR FEEDER B | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 212 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BC01-03, BC02-03, BC03-03, BC29-03, BC30-03, BC31-03, BC11-03, BC14-03, BC15-03, ZZ99- |  |  | 0
389 | FSSS |  |  | FS- CBL-JB-1B- 01 (9ZT10DC92) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
390 | FSSS |  |  | FS- CBL-JB-1B- 02 (9ZT10DC93) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
391 | FSSS |  |  | FS- CBL-JB-1B- 03 (9ZT10DC94) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | PULVERISER SEAL AIR VALVE EL 17000 NEAR FEEDER B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
392 | FSSS |  |  | FS- CBL-JB-1B- 04 (9ZT10DC95) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | FEEDER SEAL AIR VALVE EL 17000 NEAR FEEDER B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
393 | FSSS |  |  | FS- CBL-JB-1B- 05 (9ZT10DC96) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
394 | FSSS |  |  | FS- CBL-JB-1B- 06 (9ZT10DC97) | FSSS-JB-1B (48 WAYS) EL 17000 NEAR FEEDER B | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL B | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
395 | FSSS |  |  | FS- CBL-JB-2B- 01 (9ZT10DC98) | FSSS-JB-2B (48 WAYS) EL 17000 NEAR FEEDER B | PULVERISER SEAL AIR VALVE EL 17750 : NEAR MILL C | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
396 | FSSS |  |  | FS- CBL-JB-2B- 02 (9ZT10DC99) | FSSS-JB-2B (48 WAYS) EL 17000 NEAR FEEDER B | FEEDER SEAL AIR VALVE EL 17750 : NEAR MILL D | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
397 | FSSS |  |  | FS- CBL-JB-2B- 03 (9ZT10EC01) | FSSS-JB-2B (48 WAYS) EL 17000 NEAR FEEDER B | FEEDER INLET GATE EL 17750 : NEAR MILL E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
398 | FSSS |  |  | FS- CBL-JB-2B- 04 (9ZT10EC02) | FSSS-JB-2B (48 WAYS) EL 17000 NEAR FEEDER B | FEEDER OUTLET GATE EL 17750 : NEAR MILL F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
399 | FSSS |  |  | FS- CBL-JB-2B- 05 (9ZT10EC03) | FSSS-JB-2B (48WAYS) EL 17000 NEAR FEEDER B | BURNER OUTLET GATE (MCC) EL 22720 ; NEAR FEEDER B | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
400 | FSSS |  |  | FS- CBL-C-08 (9ZT10EC04) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-5C EL 10300 NEAR MILL C | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 228 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-04, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-L3, IC04-L3, IC05-L3, IC06-L3, IR07-04, IC50-04, IC51-04, IC52-04, BR16-03, BA01-03, BA02-03, BA03-03, BA04-03, BA10-03, BA11-03, BA12-03, BA13-03, BA14-04, BA15-04, BR39-03, BB12-03, ZZ99- |  |  | 0
401 | FSSS |  |  | FS- CBL-C-09 (9ZT10EC05) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2C EL 17000 NEAR FEEDER C | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 204 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BC01-03, BC02-03, BC03-03, BC29-03, BC30-03, BC31-03, BC11-03, BC12-03, BC13-03, ZZ99- |  |  | 0
402 | FSSS |  |  | FS- CBL-JB-1C- 01 (9ZT10EC06) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
403 | FSSS |  |  | FS- CBL-JB-1C- 02 (9ZT10EC07) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
404 | FSSS |  |  | FS- CBL-JB-1C- 03 (9ZT10EC08) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | PULVERISER SEAL AIR VALVEPULVERISER SEAL AIR VALVE | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
405 | FSSS |  |  | FS- CBL-JB-1C- 04 (9ZT10EC09) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | FEEDER SEAL AIR VALVEFEEDER SEAL AIR VALVE | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
406 | FSSS |  |  | FS- CBL-JB-1C- 05 (9ZT10EC10) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
407 | FSSS |  |  | FS- CBL-JB-1C- 06 (9ZT10EC11) | FSSS-JB-1C (48 WAYS) EL 17000 NEAR FEEDER C | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL C | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
408 | FSSS |  |  | FS- CBL-JB-2C- 01 (9ZT10EC12) | FSSS-JB-2C (48 WAYS) EL 17000 NEAR FEEDER C | PULVERISER SEAL AIR VALVEPULVERISER SEAL AIR VALVE | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
409 | FSSS |  |  | FS- CBL-JB-2C- 02 (9ZT10EC13) | FSSS-JB-2C (48 WAYS) EL 17000 NEAR FEEDER C | FEEDER SEAL AIR VALVEFEEDER SEAL AIR VALVE | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
410 | FSSS |  |  | FS- CBL-JB-2C- 03 (9ZT10EC14) | FSSS-JB-2C (48 WAYS) EL 17000 NEAR FEEDER C | FEEDER INLET GATE EL 17125 ; NEAR FEEDER C | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
411 | FSSS |  |  | FS- CBL-JB-2C- 04 (9ZT10EC15) | FSSS-JB-2C (48 WAYS) EL 17000 NEAR FEEDER C | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER C | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
412 | FSSS |  |  | FS- CBL-JB-2C- 05 (9ZT10EC16) | FSSS-JB-2C (48 WAYS) EL 17000 NEAR FEEDER C | BURNER OUTLET GATE (MCC) EL 22720 ; NEAR FEEDER C | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
413 | FSSS |  |  | FS- CBL-D-08 (9ZT10EC17) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-5C (24 WAYS) EL 10300 NEAR MILL C | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 229 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-04, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-L3, IC04-L3, IC05-L3, IC06-L3, IR07-04, IC50-04, IC51-04, IC52-04, BR16-03, BA01-03, BA02-03, BA03-03, BA04-03, BA10-03, BA11-03, BA12-03, BA13-03, BA14-04, BA15-04, BR39-02, BB12-03, ZZ99- |  |  | 0
414 | FSSS |  |  | FS- CBL-D-09 (9ZT10EC18) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2D (48 WAYS) EL 17000 NEAR FEEDER D | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 202 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99- |  |  | 0
415 | FSSS |  |  | FS- CBL-JB-1D- 01 (9ZT10EC19) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
416 | FSSS |  |  | FS- CBL-JB-1D- 02 (9ZT10EC20) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
417 | FSSS |  |  | FS- CBL-JB-1D- 03 (9ZT10EC21) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | PULVERISER SEAL AIR VALVEPULVERISER SEAL AIR VALVE | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
418 | FSSS |  |  | FS- CBL-JB-1D- 04 (9ZT10EC22) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | FEEDER SEAL AIR VALVEFEEDER SEAL AIR VALVE | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
419 | FSSS |  |  | FS- CBL-JB-1D- 05 (9ZT10EC23) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
420 | FSSS |  |  | FS- CBL-JB-1D- 06 (9ZT10EC24) | FSSS-JB-1D (48 WAYS) EL 17000 NEAR FEEDER D | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL D | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
421 | FSSS |  |  | FS- CBL-JB-2D- 01 (9ZT10EC25) | FSSS-JB-2D (48 WAYS) EL 17000 NEAR FEEDER D | PULVERISER SEAL AIR VALVEPULVERISER SEAL AIR VALVE | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
422 | FSSS |  |  | FS- CBL-JB-2D- 02 (9ZT10EC26) | FSSS-JB-2D (48 WAYS) EL 17000 NEAR FEEDER D | FEEDER SEAL AIR VALVEFEEDER SEAL AIR VALVE | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
423 | FSSS |  |  | FS- CBL-JB-2D- 03 (9ZT10EC27) | FSSS-JB-2D (48 WAYS) EL 17000 NEAR FEEDER D | FEEDER INLET GATE EL 17125 ; NEAR FEEDER D | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
424 | FSSS |  |  | FS- CBL-JB-2D- 04 (9ZT10EC28) | FSSS-JB-2D (48 WAYS) EL 17000 NEAR FEEDER D | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER D | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
425 | FSSS |  |  | FS- CBL-JB-2D- 05 (9ZT10EC29) | FSSS-JB-2D (48 WAYS) EL 17000 NEAR FEEDER D | BURNER OUTLET GATE (MCC) EL 22720 ; NEAR FEEDER D | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
426 | FSSS |  |  | FS- CBL-E-08 (9ZT10EC30) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-5E (24 WAYS) EL 10300 NEAR MILL E | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 228 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-04, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-L3, IC04-L3, IC05-L3, IC06-L3, IR07-04, IC50-04, IC51-04, IC52-04, BR16-03, BA01-03, BA02-03, BA03-03, BA04-03, BA10-03, BA11-03, BA12-03, BA13-03, BA14-04, BA15-04, BR39-03, BB13-03, ZZ99- |  |  | 0
427 | FSSS |  |  | FS- CBL-E-09 (9ZT10EC31) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2E (48 WAYS) EL 17000 NEAR FEEDER E | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 208 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, ZZ99- |  |  | 0
428 | FSSS |  |  | FS- CBL-JB-1E- 01 (9ZT10EC32) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL E | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
429 | FSSS |  |  | FS- CBL-JB-1E- 02 (9ZT10EC33) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL E | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
430 | FSSS |  |  | FS- CBL-JB-1E- 03 (9ZT10EC34) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | PULVERISER SEAL AIR VALVE EL 17000 NEAR FEEDER E | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
431 | FSSS |  |  | FS- CBL-JB-1E- 04 (9ZT10EC35) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | FEEDER SEAL AIR VALVE EL 17000 NEAR FEEDER E | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
432 | FSSS |  |  | FS- CBL-JB-1E- 05 (9ZT10EC36) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER E | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
433 | FSSS |  |  | FS- CBL-JB-1E- 06 (9ZT10EC37) | FSSS-JB-1E (48 WAYS) EL 17000 NEAR FEEDER E | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL E | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
434 | FSSS |  |  | FS- CBL-JB-2E- 01 (9ZT10EC38) | FSSS-JB-2E (48 WAYS) EL 17000 NEAR FEEDER E | PULVERISER SEAL AIR VALVE EL 17000 NEAR FEEDER E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
435 | FSSS |  |  | FS- CBL-JB-2E- 02 (9ZT10EC39) | FSSS-JB-2E (48 WAYS) EL 17000 NEAR FEEDER E | FEEDER SEAL AIR VALVE EL 17000 NEAR FEEDER E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
436 | FSSS |  |  | FS- CBL-JB-2E- 03 (9ZT10EC40) | FSSS-JB-2E (48 WAYS) EL 17000 NEAR FEEDER E | FEEDER INLET GATE EL 17125 ; NEAR FEEDER E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
437 | FSSS |  |  | FS- CBL-JB-2E- 04 (9ZT10EC41) | FSSS-JB-2E (48 WAYS) EL 17000 NEAR FEEDER E | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
438 | FSSS |  |  | FS- CBL-JB-2E- 05 (9ZT10EC42) | FSSS-JB-2E ( 48 WAYS) EL 17000 NEAR FEEDER E | BURNER OUTLET GATE (MCC) EL 22720 ; NEAR FEEDER E | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
439 | FSSS |  |  | FS- CBL-F-08 (9ZT10EC43) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-5F (24 WAYS) EL 10300 NEAR MILL F | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 248 | [5 empty] | EL 10300 NEAR MILL F | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-04, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-L3, IC04-L3, IC05-L3, IC06-L3, IR07-04, IC50-04, IC51-04, IC52-04, BR16-03, BA01-03, BA02-03, BA03-03, BA04-03, BA10-03, BA11-03, BA12-03, BA13-03, BA14-04, BA15-04, BR39-03, BB13-03, ZZ99- |  |  | 0
440 | FSSS |  |  | FS- CBL-F-09 (9ZT10EC44) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-2F ( 48 WAYS) EL 17000 NEAR FEEDER F | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 222 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, CR01-R4, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, BC22-03, ZZ99- |  |  | 0
441 | FSSS |  |  | FS- CBL-JB-1F- 01 (9ZT10EC45) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | PULVERISER DISCHARGE VALVE TERMINATION BOX EL 10300 : BETWEEN M & N ROWS MILL F | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
442 | FSSS |  |  | FS- CBL-JB-1F- 02 (9ZT10EC46) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | HOT AIR GATE TERMINATION BOX EL 17750 : NEAR MILL F | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
443 | FSSS |  |  | FS- CBL-JB-1F- 03 (9ZT10EC47) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | PULVERISER SEAL AIR VALVE EL 17000 NEAR FEEDER F | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
444 | FSSS |  |  | FS- CBL-JB-1F- 04 (9ZT10EC48) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | FEEDER SEAL AIR VALVE EL 17000 NEAR FEEDER F | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
445 | FSSS |  |  | FS- CBL-JB-1F- 05 (9ZT10EC49) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER F | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
446 | FSSS |  |  | FS- CBL-JB-1F- 06 (9ZT10EC50) | FSSS-JB-1F ( 48 WAYS) EL 17000 NEAR FEEDER F | COLD AIR GATE TERMINATION BOX EL 17750 : NEAR MILL F | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
447 | FSSS |  |  | FS- CBL-JB-2F- 01 (9ZT10EC51) | FSSS-JB-2F ( 48 WAYS) EL 17000 NEAR FEEDER F | PULVERISER SEAL AIR VALVE EL 17000 NEAR FEEDER F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
448 | FSSS |  |  | FS- CBL-JB-2F- 02 (9ZT10EC52) | FSSS-JB-2F ( 48 WAYS) EL 17000 NEAR FEEDER F | FEEDER SEAL AIR VALVE EL 17000 NEAR FEEDER F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
449 | FSSS |  |  | FS- CBL-JB-2F- 03 (9ZT10EC53) | FSSS-JB-2F ( 48 WAYS) EL 17000 NEAR FEEDER F | FEEDER INLET GATE EL 17125 ; NEAR FEEDER F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
450 | FSSS |  |  | FS- CBL-JB-2F- 04 (9ZT10EC54) | FSSS-JB-2F ( 48 WAYS) EL 17000 NEAR FEEDER F | FEEDER OUTLET GATE EL 17125 ; NEAR FEEDER F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 10 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
451 | FSSS |  |  | FS- CBL-JB-2F- 05 (9ZT10EC55) | FSSS-JB-2F ( 48 WAYS) EL 17000 NEAR FEEDER F | BURNER OUTLET GATE (MCC) EL 22720 ; NEAR FEEDER F | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SEAL AIR & FEEDER SEAL AIR | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
452 | FSSS |  |  | FS- CBL-A-10 (9ZT10EC56) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3A (24 WAYS) EL 20300 NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 148 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-R4, IC01-R3, IC02-R3, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-04, ZZ99- |  |  | 0
453 | FSSS |  |  | FS- CBL-A-11 (9ZT10EC57) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
454 | FSSS |  |  | FS- CBL-JB-3A- 1 (9ZT10EC58) | FSSS-JB-3A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 21100 NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
455 | FSSS |  |  | FS- CBL-JB-3A- 2 (9ZT10EC59) | FSSS-JB-3A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 21100 NEAR S11L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
456 | FSSS |  |  | FS- CBL-JB-3A- 3 (9ZT10EC60) | FSSS-JB-3A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 21100 NEAR S11R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
457 | FSSS |  |  | FS- CBL-JB-3A- 4 (9ZT10EC61) | FSSS-JB-3A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 21100 NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
458 | FSSS |  |  | FS- CBL-B-10 (9ZT10EC62) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3B ( 24 WAYS) EL 20300 NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 150 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-04, LR10-R4, IC01-R3, IC02-R3, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-04, ZZ99- |  |  | 0
459 | FSSS |  |  | FS- CBL-B-11 (9ZT10EC63) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
460 | FSSS |  |  | FS- CBL-JB-3B- 1 (9ZT10EC64) | FSSS-JB-3B ( 24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 22500 NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
461 | FSSS |  |  | FS- CBL-JB-3B- 2 (9ZT10EC65) | FSSS-JB-3B (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 22500 NEAR S11L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
462 | FSSS |  |  | FS- CBL-JB-3B- 3 (9ZT10EC66) | FSSS-JB-3B (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 22500 NEAR S11R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
463 | FSSS |  |  | FS- CBL-JB-3B- 4 (9ZT10EC67) | FSSS-JB-3B (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 22500 NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
464 | FSSS |  |  | FS- CBL-C-10 (9ZT10EC68) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3C (24 WAYS) EL 23300 NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 153 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, IC01-R3, IC02-R3, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-04, BR19-03, ZZ99- |  |  | 0
465 | FSSS |  |  | FS- CBL-C-11 (9ZT10EC69) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
466 | FSSS |  |  | FS- CBL-JB-3C- 1 (9ZT10EC70) | FSSS-JB-3C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 23900 NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
467 | FSSS |  |  | FS- CBL-JB-3C- 2 (9ZT10EC71) | FSSS-JB-3C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 23900 NEAR S11L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
468 | FSSS |  |  | FS- CBL-JB-3C- 3 (9ZT10EC72) | FSSS-JB-3C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 23900 NEAR S11R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
469 | FSSS |  |  | FS- CBL-JB-3C- 4 (9ZT10EC73) | FSSS-JB-3C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 23900 NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
470 | FSSS |  |  | FS- CBL-D-10 (9ZT10EC74) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3D (24 WAYS) EL 23300 NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 153 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, IC01-R3, IC02-R3, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-04, BR19-03, ZZ99- |  |  | 0
471 | FSSS |  |  | FS- CBL-D-11 (9ZT10EC75) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
472 | FSSS |  |  | FS- CBL-JB-3D- 1 (9ZT10EC76) | FSSS-JB-3D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 25300 NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
473 | FSSS |  |  | FS- CBL-JB-3D- 2 (9ZT10EC77) | FSSS-JB-3D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 25300 NEAR S11L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
474 | FSSS |  |  | FS- CBL-JB-3D- 3 (9ZT10EC78) | FSSS-JB-3D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 25300 NEAR S11R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
475 | FSSS |  |  | FS- CBL-JB-3D- 4 (9ZT10EC79) | FSSS-JB-3D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 25300 NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
476 | FSSS |  |  | FS- CBL-E-10 (9ZT10EC80) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3E ( 24 WAYS) EL 26300 NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 132 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-04, BR19-03, BR20-03, ZZ99- |  |  | 0
477 | FSSS |  |  | FS- CBL-E-11 (9ZT10EC81) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
478 | FSSS |  |  | FS- CBL-JB-3E- 1 (9ZT10EC82) | FSSS-JB-3E ( 24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 26800 NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
479 | FSSS |  |  | FS- CBL-JB-3E- 2 (9ZT10EC83) | FSSS-JB-3E (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 26800 NEAR S11L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
480 | FSSS |  |  | FS- CBL-JB-3E- 3 (9ZT10EC84) | FSSS-JB-3E (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 26800 NEAR S11R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
481 | FSSS |  |  | FS- CBL-JB-3E- 4 (9ZT10EC85) | FSSS-JB-3E (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 26800 NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
482 | FSSS |  |  | FS- CBL-F-10 (9ZT10EC86) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FSSS-JB-3F (24 WAYS) EL 26300 NEAR S9L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 142 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-04, BR19-03, BR20-03, ZZ99- |  |  | 0
483 | FSSS |  |  | FS- CBL-F-11 (9ZT10EC87) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | RD FEEDER CABINETCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
484 | FSSS |  |  | FS- CBL-JB-3F- 1 (9ZT10EC88) | FSSS-JB-3F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 28200 NEAR S9L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
485 | FSSS |  |  | FS- CBL-JB-3F- 2 (9ZT10EC89) | FSSS-JB-3F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 28200 NEAR S11L | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
486 | FSSS |  |  | FS- CBL-JB-3F- 3 (9ZT10EC90) | FSSS-JB-3F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 28200 NEAR S11R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
487 | FSSS |  |  | FS- CBL-JB-3F- 4 (9ZT10EC91) | FSSS-JB-3F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 28200 NEAR S9R | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
488 | FSSS |  |  | FS- CBL-JB-4A- 1 (9ZT10EC92) | FSSS-JB-4A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 21100 NEAR S9L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
489 | FSSS |  |  | FS- CBL-JB-4A- 2 (9ZT10EC93) | FSSS-JB-4A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 21100 NEAR S11L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
490 | FSSS |  |  | FS- CBL-JB-4A- 3 (9ZT10EC94) | FSSS-JB-4A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 21100 NEAR S11R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
491 | FSSS |  |  | FS- CBL-JB-4A- 4 (9ZT10EC95) | FSSS-JB-4A (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 21100 NEAR S9R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
492 | FSSS |  |  | FS- CBL-JB-4B- 1 (9ZT10EC96) | FSSS-JB-4B (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 22500 NEAR S9L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
493 | FSSS |  |  | FS- CBL-JB-4B- 2 (9ZT10EC97) | FSSS-JB-4B (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 22500 NEAR S11L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
494 | FSSS |  |  | FS- CBL-JB-4B- 3 (9ZT10EC98) | FSSS-JB-4B (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 22500 NEAR S11R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
495 | FSSS |  |  | FS- CBL-JB-4B- 4 (9ZT10EC99) | FSSS-JB-4B (24 WAYS) EL 20300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 22500 NEAR S9R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
496 | FSSS |  |  | FS- CBL-JB-4C- 1 (9ZT10FC01) | FSSS-JB-4C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 23900 NEAR S9L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
497 | FSSS |  |  | FS- CBL-JB-4C- 2 (9ZT10FC02) | FSSS-JB-4C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 23900 NEAR S11L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
498 | FSSS |  |  | FS- CBL-JB-4C- 3 (9ZT10FC03) | FSSS-JB-4C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 23900 NEAR S11R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
499 | FSSS |  |  | FS- CBL-JB-4C- 4 (9ZT10FC04) | FSSS-JB-4C (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 23900 NEAR S9R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
500 | FSSS |  |  | FS- CBL-JB-4D- 1 (9ZT10FC05) | FSSS-JB-4D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 25300 NEAR S9L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
501 | FSSS |  |  | FS- CBL-JB-4D- 2 (9ZT10FC06) | FSSS-JB-4D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 25300 NEAR S11L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
502 | FSSS |  |  | FS- CBL-JB-4D- 3 (9ZT10FC07) | FSSS-JB-4D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 25300 NEAR S11R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
503 | FSSS |  |  | FS- CBL-JB-4D- 4 (9ZT10FC08) | FSSS-JB-4D (24 WAYS) EL 23300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 25300 NEAR S9R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 25 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
504 | FSSS |  |  | FS- CBL-JB-4E- 1 (9ZT10FC09) | FSSS-JB-4E (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 26800 NEAR S9L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
505 | FSSS |  |  | FS- CBL-JB-4E- 2 (9ZT10FC10) | FSSS-JB-4E (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 26800 NEAR S11L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
506 | FSSS |  |  | FS- CBL-JB-4E- 3 (9ZT10FC11) | FSSS-JB-4E (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 26800 NEAR S11R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
507 | FSSS |  |  | FS- CBL-JB-4E- 4 (9ZT10FC12) | FSSS-JB-4E (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 26800 NEAR S9R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
508 | FSSS |  |  | FS- CBL-JB-4F- 1 (9ZT10FC13) | FSSS-JB-4F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-1 EL 28200 NEAR S9L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
509 | FSSS |  |  | FS- CBL-JB-4F- 2 (9ZT10FC14) | FSSS-JB-4F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-2 EL 28200 NEAR S11L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 15 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
510 | FSSS |  |  | FS- CBL-JB-4F- 3 (9ZT10FC15) | FSSS-JB-4F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-3 EL 28200 NEAR S11R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
511 | FSSS |  |  | FS- CBL-JB-4F- 4 (9ZT10FC16) | FSSS-JB-4F (24 WAYS) EL 26300 NEAR S9L | BURNER ISOLATION GATE CORNER-4 EL 28200 NEAR S9R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 50 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL SECTION BURNER ISO. VALVE | TRICHY SCOPE CABLE | SITE ROUTING |  |  | 0
512 | FSSS |  |  | FS- CBL-A-12 (9ZT10FC17) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SA HDR/PULV BOWL DP TRANSMITTER) [FSSS-LIE-6]FEEDER FLOOR ; NEAR FEEDER A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 219 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL DP TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BC01-03, BC02-03, BC03-03, BC29-03, BC30-03, BC31-03, BC11-03, BC14-03, BC15-03, BC16-03, ZZ99- |  |  | 0
513 | FSSS |  |  | FS- CBL-B-12 (9ZT10FC18) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SA HDR/PULV BOWL DP TRANSMITTER) [FSSS-LIE-7]FEEDER FLOOR ; NEAR FEEDER B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 209 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL DP TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BC01-03, BC02-03, BC03-03, BC29-03, BC30-03, BC31-03, BC11-03, BC14-03, BC15-03, ZZ99- |  |  | 0
514 | FSSS |  |  | FS- CBL-C-12 (9ZT10FC19) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SA HDR/PULV BOWL DP TRANSMITTER) [FSSS-LIE-8]FEEDER FLOOR ; NEAR FEEDER C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 203 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL DP TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BC01-03, BC02-03, BC03-03, BC29-03, BC30-03, BC31-03, BC11-03, BC12-03, ZZ99- |  |  | 0
515 | FSSS |  |  | FS- CBL-D-12 (9ZT10FC20) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SA HDR/PULV BOWL DP TRANSMITTER) [FSSS-LIE-9]FEEDER FLOOR ; NEAR FEEDER D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 201 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL DP TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-04, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-R4, CR01-L3, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, ZZ99- |  |  | 0
516 | FSSS |  |  | FS- CBL-E-12 (9ZT10FC21) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SA HDR/PULV BOWL DP TRANSMITTER) [FSSS-LIE-10]FEEDER FLOOR ; NEAR FEEDER E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 210 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL DP TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, ZZ99- |  |  | 0
517 | FSSS |  |  | FS- CBL-F-12 (9ZT10FC22) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | LIE (SA HDR/PULV BOWL DP TRANSMITTER) [FSSS-LIE-11]FEEDER FLOOR ; NEAR FEEDER F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 218 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL DP TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R3, LV75-05, LV77-05, LR10-L5, CR01-R2, QR03-R3, BQ20-R3, BQ19-R3, BQ06-03, BQ05-03, BQ04-03, BQ03-R2, BQ02-R2, QR01-04, BQ01-04, BR44-04, BD09-04, BD08-04, BR03-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, BC22-03, ZZ99- |  |  | 0
518 | FSSS |  |  | FS- CBL-A-13 (9ZT10FC23) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FS OIL HEATER PS MCC MODUL ELTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 259 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | EDN SCOPE CABLE | ZZ99- , LV14-L4, LV13-R3, LV12-R3, LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IC07-R3, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IR13-02, IC30-03, IC31-03, ZZ99- |  |  | 0
519 | FSSS |  |  | FS- CBL-A-14 (9ZT10FC24) | FS OIL HEATER PS MCC MODUL ELTMCC | PLOS LUBE OIL TANK HEATERNEAR MILL A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 273 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | PEM SCOPE CABLE | ZZ99- , LV14-L4, LV13-R3, LV12-R3, LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IC07-R3, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IR14-02, IC35-03, IC36-03, ZZ99- |  |  | 0
520 | FSSS |  |  | FS- CBL-B-13 (9ZT10FC25) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FS OIL HEATER PS MCC MODUL ELTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 285 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | EDN SCOPE CABLE | ZZ99- , LV14-L4, LV13-R3, LV12-R3, LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IC07-R3, IR08-03, IC08-03, IC09-03, IC10-03, IC11-03, IC12-03, IC13-03, IR09-03, IC24-03, IC25-03, IC26-03, IR11-03, IC27-03, IC28-03, IR12-03, IC29-03, IC33-03, IC34-03, IC38-03, IC39-03, IC40-03, IR15-02, IC41-03, IC42-03, ZZ99- |  |  | 0
521 | FSSS |  |  | FS- CBL-B-14 (9ZT10FC26) | FS OIL HEATER PS MCC MODUL ELTMCC | PLOS LUBE OIL TANK HEATERNEAR MILL B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 298 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | PEM SCOPE CABLE | ZZ99- , LV14-L4, LV62-05, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, CC05-04, IR19-02, IM06-02, IM07-05, IM09-05, IM10-04, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IM88-02, IM89-02, IR35-02, IM90-02, IM91-02, IM93-02, ZZ99- |  |  | 0
522 | FSSS |  |  | FS- CBL-C-13 (9ZT10FC27) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FS OIL HEATER PS MCC MODUL ELTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 288 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | EDN SCOPE CABLE | ZZ99- , LV14-L4, LV13-L4, LV12-R3, LV11-L4, LV48-04, LV47-04, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, CC05-04, IR19-02, IM06-02, IM07-05, IM09-05, IM10-04, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IM85-03, IM86-03, IM87-03, IR34-02, IM97-02, IM98-02, IM99-02, ZZ99- |  |  | 0
523 | FSSS |  |  | FS- CBL-C-14 (9ZT10FC28) | FS OIL HEATER PS MCC MODUL ELTMCC | PLOS LUBE OIL TANK HEATERNEAR MILL C | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 272 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | PEM SCOPE CABLE | ZZ99- , LV14-L4, LV62-05, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC02-03, CC04-03, CC05-04, IR19-02, IM06-02, IM07-05, IM09-05, IM10-04, IM11-L7, IM12-L7, IM64-05, IM65-05, IM66-05, IM67-05, IM68-05, IM72-05, IM75-03, IR28-03, IM76-03, IM77-03, IM78-03, IR32-03, IM79-03, IM80-03, IR33-02, IM81-02, IM82-02, IM83-02, ZZ99- |  |  | 0
524 | FSSS |  |  | FS- CBL-D-13 (9ZT10FC29) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FS OIL HEATER PS MCC MODUL ELTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 83 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-L4, LV13-L4, LV14-L4, ZZ99- |  |  | 0
525 | FSSS |  |  | FS- CBL-D-14 (9ZT10FC30) | FS OIL HEATER PS MCC MODUL ELTMCC | PLOS LUBE OIL TANK HEATERNEAR MILL D | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 85 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | PEM SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, ZZ99- |  |  | 0
526 | FSSS |  |  | FS- CBL-E-13 (9ZT10FC31) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FS OIL HEATER PS MCC MODUL ELTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, ZZ99- |  |  | 0
527 | FSSS |  |  | FS- CBL-E-14 (9ZT10FC32) | FS OIL HEATER PS MCC MODUL ELTMCC | PLOS LUBE OIL TANK HEATERNEAR MILL E | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 85 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | PEM SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, ZZ99- |  |  | 0
528 | FSSS |  |  | FS- CBL-F-13 (9ZT10FC33) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | FS OIL HEATER PS MCC MODUL ELTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, ZZ99- |  |  | 0
529 | FSSS |  |  | FS- CBL-F-14 (9ZT10FC34) | FS OIL HEATER PS MCC MODUL ELTMCC | PLOS LUBE OIL TANK HEATERNEAR MILL F | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 85 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS ALARMS | PEM SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, ZZ99- |  |  | 0
530 | FSSS |  |  | FS- CBL-A-21 (9ZT10FC35) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
531 | FSSS |  |  | FS- CBL-A-22 (9ZT10FC36) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
532 | FSSS |  |  | FS- CBL-A-15 (9ZT10FC37) | FSSS PAN EL CONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLT MCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 60 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
533 | FSSS |  |  | FS- CBL-A-16 (9ZT10FC38) | FSSS PAN EL CONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLT MCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 60 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
534 | FSSS |  |  | FS- CBL-B-21 (9ZT10FC39) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
535 | FSSS |  |  | FS- CBL-B-22 (9ZT10FC40) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
536 | FSSS |  |  | FS- CBL-B-15 (9ZT10FC41) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
537 | FSSS |  |  | FS- CBL-B-16 (9ZT10FC42) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
538 | FSSS |  |  | FS- CBL-C-21 (9ZT10FC43) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
539 | FSSS |  |  | FS- CBL-C-22 (9ZT10FC44) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
540 | FSSS |  |  | FS- CBL-C-15 (9ZT10FC45) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
541 | FSSS |  |  | FS- CBL-C-16 (9ZT10FC46) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
542 | FSSS |  |  | FS- CBL-D-21 (9ZT10FC47) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
543 | FSSS |  |  | FS- CBL-D-22 (9ZT10FC48) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
544 | FSSS |  |  | FS- CBL-D-15 (9ZT10FC49) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
545 | FSSS |  |  | FS- CBL-D-16 (9ZT10FC50) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
546 | FSSS |  |  | FS- CBL-E-21 (9ZT10FC51) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
547 | FSSS |  |  | FS- CBL-E-22 (9ZT10FC52) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 88 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV28-L4, LV29-L4, LV30-L4, LV31-L4, LV61-05, LV19-L4, LV68-02, LV15-L4, ZZ99- |  |  | 0
548 | FSSS |  |  | FS- CBL-E-15 (9ZT10FC53) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
549 | FSSS |  |  | FS- CBL-E-16 (9ZT10FC54) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
550 | FSSS |  |  | FS- CBL-F-21 (9ZT10FC55) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 87 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-03, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
551 | FSSS |  |  | FS- CBL-F-22 (9ZT10FC56) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 88 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-03, LR08-03, LV73-03, LV81-L4, LV27-L4, LV42-02, LV23-L4, LV48-04, LV11-L4, LV12-R3, LV13-R3, LV14-R3, LV15-R3, ZZ99- |  |  | 0
552 | FSSS |  |  | FS- CBL-F-15 (9ZT10FC57) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS MAIN PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
553 | FSSS |  |  | FS- CBL-F-16 (9ZT10FC58) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS STANDBY PUMP STARTERLTMCC room | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 84 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS PUMP TRANSMITTER | EDN SCOPE CABLE | ZZ99- , CC01-04, LR08-04, LV73-04, LV39-R4, LV38-R4, LV37-R4, LV36-R4, LV35-R4, LV55-03, LV31-R4, LV61-06, LV19-R4, LV68-03, LV15-R4, ZZ99- |  |  | 0
554 | FSSS |  |  | FS- CBL-A-17 (9ZT10FC59) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-A MILL- JB-5A (60 WAYS) EL 0: NEAR MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 237 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IR13-03, ZZ99- |  |  | 0
555 | FSSS |  |  | FS- CBL-A-18 (9ZT10FC60) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-A MILL- JB-5A (60 WAYS) EL 0: NEAR MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 238 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IR13-03, ZZ99- |  |  | 0
556 | FSSS |  |  | FS- CBL-A-19 (9ZT10FC61) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-A MILL-JB-5A (60 WAYS) EL 0: NEAR MILL A | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 239 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IR13-03, ZZ99- |  |  | 0
557 | FSSS |  |  | FS- CBL-B-17 (9ZT10FC62) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-B MILL-JB-5B (60 WAYS) EL 0: NEAR MILL B | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 252 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IR14-03, ZZ99- |  |  | 0
558 | FSSS |  |  | FS- CBL-B-18 (9ZT10FC63) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-B MILL-JB-5B(60 WAYS) EL 0: NEAR MILL B | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 254 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IR14-03, ZZ99- |  |  | 0
559 | FSSS |  |  | FS- CBL-B-19 (9ZT10FC64) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-B MILL-JB-5B(60 WAYS) EL 0: NEAR MILL B | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 254 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IR14-03, ZZ99- |  |  | 0
560 | FSSS |  |  | FS- CBL-C-17 (9ZT10FC65) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-C MILL-JB-5C EL 0: NEAR MILL C | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 266 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IC38-04, IC39-04, IC40-04, IR15-03, ZZ99- |  |  | 0
561 | FSSS |  |  | FS- CBL-C-18 (9ZT10FC66) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-C MILL-JB-5C (60 WAYS) EL 0: NEAR MILL C | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 266 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IC38-04, IC39-04, IC40-04, IR15-03, ZZ99- |  |  | 0
562 | FSSS |  |  | FS- CBL-C-19 (9ZT10FC67) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-C MILL-JB-5C (60 WAYS) EL 0: NEAR MILL C | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 266 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IC38-04, IC39-04, IC40-04, IR15-03, ZZ99- |  |  | 0
563 | FSSS |  |  | FS- CBL-D-17 (9ZT10FC68) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-D MILL-JB-5D (60 WAYS) EL 0: NEAR MILL D | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 250 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IM88-03, IM89-03, IR35-03, ZZ99- |  |  | 0
564 | FSSS |  |  | FS- CBL-D-18 (9ZT10FC69) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-D MILL-JB-5D (60 WAYS) EL 0: NEAR MILL D | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 250 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IM88-03, IM89-03, IR35-03, ZZ99- |  |  | 0
565 | FSSS |  |  | FS- CBL-D-19 (9ZT10FC70) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-D MILL-JB-5D (60 WAYS) EL 0: NEAR MILL D | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 250 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IM88-03, IM89-03, IR35-03, ZZ99- |  |  | 0
566 | FSSS |  |  | FS- CBL-E-17 (9ZT10FC71) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-E MILL-JB-5E(60 WAYS) EL 0: NEAR MILL E | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 238 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IR34-03, ZZ99- |  |  | 0
567 | FSSS |  |  | FS- CBL-E-18 (9ZT10FC72) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-E MILL-JB-5E(60 WAYS) EL 0: NEAR MILL E | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 238 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IR34-03, ZZ99- |  |  | 0
568 | FSSS |  |  | FS- CBL-E-19 (9ZT10FC73) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-E MILL-JB-5E (60 WAYS) EL 0: NEAR MILL E | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 238 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IR34-03, ZZ99- |  |  | 0
569 | FSSS |  |  | FS- CBL-F-17 (9ZT10FC74) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-F MILL-JB-5F (60 WAYS) EL 0: NEAR MILL F | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 226 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IR33-03, ZZ99- |  |  | 0
570 | FSSS |  |  | FS- CBL-F-18 (9ZT10FC75) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-F MILL-JB-5F (60 WAYS) EL 0: NEAR MILL F | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 226 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-02, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IR33-03, ZZ99- |  |  | 0
571 | FSSS |  |  | FS- CBL-F-19 (9ZT10FC76) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | PLOS GAUGE PAN EL-F MILL-JB-5F (60 WAYS) EL 0: NEAR MILL F | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 226 | [5 empty] | FSSS INTERCONNECTION DIAGRAM PLOS GAUGE PANEL | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-02, CC63-02, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IR33-03, ZZ99- |  |  | 0
572 | FSSS |  |  | FS- CBL-A-20 (9ZT10FC77) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL A | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 240 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IR13-03, ZZ99- |  |  | 0
573 | FSSS |  |  | FS- CBL-MOTOR- A-01 (9ZT10FC78) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL A | MILL MOTOR A TERMINAL BOX (WINDING RTD WIRING)MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
574 | FSSS |  |  | FS- CBL-MOTOR- A-02 (9ZT10FC79) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL A | MILL MOTOR A TERMINAL BOX (WINDING RTD WIRING)MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
575 | FSSS |  |  | FS- CBL-MOTOR- A-03 (9ZT10FC80) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL A | MILL MOTOR A TERMINAL BOX (WINDING RTD WIRING)MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
576 | FSSS |  |  | FS- CBL-MOTOR- A-04 (9ZT10FC81) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL A | MILL MOTOR A TERMINAL BOX (WINDING RTD WIRING)MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
577 | FSSS |  |  | FS- CBL-B-20 (9ZT10FC82) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL B | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 254 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IR14-03, ZZ99- |  |  | 0
578 | FSSS |  |  | FS- CBL-MOTOR- B-01 (9ZT10FC83) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL B | MILL MOTOR B TERMINAL BOX (WINDING RTD WIRING)MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
579 | FSSS |  |  | FS- CBL-MOTOR- B-02 (9ZT10FC84) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL B | MILL MOTOR B TERMINAL BOX (WINDING RTD WIRING)MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
580 | FSSS |  |  | FS- CBL-MOTOR- B-03 (9ZT10FC85) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL B | MILL MOTOR B TERMINAL BOX (WINDING RTD WIRING)MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
581 | FSSS |  |  | FS- CBL-MOTOR- B-04 (9ZT10FC86) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL B | MILL MOTOR B TERMINAL BOX (WINDING RTD WIRING)MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
582 | FSSS |  |  | FS- CBL-C-20 (9ZT10FC87) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL C | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 266 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-04, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IC38-04, IC39-04, IC40-04, IR15-03, ZZ99- |  |  | 0
583 | FSSS |  |  | FS- CBL-MOTOR- C-01 (9ZT10FC88) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL C | MILL MOTOR C TERMINAL BOX (WINDING RTD WIRING)MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
584 | FSSS |  |  | FS- CBL-MOTOR- C-02 (9ZT10FC89) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL C | MILL MOTOR C TERMINAL BOX (WINDING RTD WIRING)MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
585 | FSSS |  |  | FS- CBL-MOTOR- C-03 (9ZT10FC90) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL C | MILL MOTOR C TERMINAL BOX (WINDING RTD WIRING)MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
586 | FSSS |  |  | FS- CBL-MOTOR- C-04 (9ZT10FC91) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL C | MILL MOTOR C TERMINAL BOX (WINDING RTD WIRING)MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
587 | FSSS |  |  | FS- CBL-D-20 (9ZT10FC92) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL D | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 249 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, CC80-03, CC23-04, CC21-03, CC64-04, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IM88-03, IM89-03, IR35-03, ZZ99- |  |  | 0
588 | FSSS |  |  | FS- CBL-MOTOR- D-01 (9ZT10FC93) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL D | MILL MOTOR D TERMINAL BOX (WINDING RTD WIRING)MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
589 | FSSS |  |  | FS- CBL-MOTOR- D-02 (9ZT10FC94) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL D | MILL MOTOR D TERMINAL BOX (WINDING RTD WIRING)MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
590 | FSSS |  |  | FS- CBL-MOTOR- D-03 (9ZT10FC95) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL D | MILL MOTOR D TERMINAL BOX (WINDING RTD WIRING)MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
591 | FSSS |  |  | FS- CBL-MOTOR- D-04 (9ZT10FC96) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL D | MILL MOTOR D TERMINAL BOX (WINDING RTD WIRING)MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
592 | FSSS |  |  | FS- CBL-E-20 (9ZT10FC97) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL E | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 237 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-02, CC80-03, CC23-04, CC21-03, CC64-04, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IR34-03, ZZ99- |  |  | 0
593 | FSSS |  |  | FS- CBL-MOTOR- E-01 (9ZT10FC98) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL E | MILL MOTOR E TERMINAL BOX (WINDING RTD WIRING)MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
594 | FSSS |  |  | FS- CBL-MOTOR- E-02 (9ZT10FC99) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL E | MILL MOTOR E TERMINAL BOX (WINDING RTD WIRING)MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
595 | FSSS |  |  | FS- CBL-MOTOR- E-03 (9ZT10GC01) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL E | MILL MOTOR E TERMINAL BOX (WINDING RTD WIRING)MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
596 | FSSS |  |  | FS- CBL-MOTOR- E-04 (9ZT10GC02) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL E | MILL MOTOR E TERMINAL BOX (WINDING RTD WIRING)MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
597 | FSSS |  |  | FS- CBL-F-20 (9ZT10GC03) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL F | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 224 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | TRICHY SCOPE CABLE | ZZ99- , CC90-04, CC80-03, CC23-04, CC21-03, CC64-04, CC63-04, CC62-04, CC04-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IR33-03, ZZ99- |  |  | 0
598 | FSSS |  |  | FS- CBL-MOTOR- F-01 (9ZT10GC04) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL F | MILL MOTOR F TERMINAL BOX (WINDING RTD WIRING)MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
599 | FSSS |  |  | FS- CBL-MOTOR- F-02 (9ZT10GC05) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL F | MILL MOTOR F TERMINAL BOX (WINDING RTD WIRING)MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
600 | FSSS |  |  | FS- CBL-MOTOR- F-03 (9ZT10GC06) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL F | MILL MOTOR F TERMINAL BOX (WINDING RTD WIRING)MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
601 | FSSS |  |  | FS- CBL-MOTOR- F-04 (9ZT10GC07) | ENCLOSURE BOX FOR MOUNTING MILL MOTOR BEARING & WINDING TEMP. ELEMENTNEAR MILL F | MILL MOTOR F TERMINAL BOX (WINDING RTD WIRING)MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL MOTOR TEMP. TRANSMITTER | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
602 | FSSS |  |  | FS- CBL-A-23 (9ZT10GC08) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL A | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 260 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IR13-03, IC30-04, IC31-04, ZZ99- |  |  | 0
603 | FSSS |  |  | FS- CBL-A-24 (9ZT10GC09) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTERNEAR MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 257 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IR13-03, IC30-04, IC31-04, ZZ99- |  |  | 0
604 | FSSS |  |  | FS- CBL-MILL-A -01 (9ZT10GC10) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL A | THRUST PAD RADIAL BRG TEMP. ELEMENT-1MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
605 | FSSS |  |  | FS- CBL-MILL-A -02 (9ZT10GC11) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL A | THRUST PAD RADIAL BRG TEMP. ELEMENT-2MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
606 | FSSS |  |  | FS- CBL-MILL-A -03 (9ZT10GC12) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL A | THRUST PAD RADIAL BRG TEMP. ELEMENT-3MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
607 | FSSS |  |  | FS- CBL-MILL-A -04 (9ZT10GC13) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL A | THRUST PAD RADIAL BRG TEMP. ELEMENT-4MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
608 | FSSS |  |  | FS- CBL-MILL-A -05 (9ZT10GC14) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL A | THRUST PAD RADIAL BRG TEMP. ELEMENT-5MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
609 | FSSS |  |  | FS- CBL-MILL-A -06 (9ZT10GC15) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL A | THRUST PAD RADIAL BRG TEMP. ELEMENT-6MILL A | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
610 | FSSS |  |  | FS- CBL-JBT/C- A-07 (9ZT10GC16) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL A | MILL -A OUTLET DUPLEX T/CMILL A | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
611 | FSSS |  |  | FS- CBL-JBT/C- A-08 (9ZT10GC17) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL A | MILL -A OUTLET DUPLEX T/CMILL A | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
612 | FSSS |  |  | FS- CBL-B-23 (9ZT10GC18) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL B | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 274 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IR14-03, IC35-04, IC36-04, ZZ99- |  |  | 0
613 | FSSS |  |  | FS- CBL-B-24 (9ZT10GC19) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTERNEAR MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 271 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R4, IC02-R4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IR14-03, IC35-04, IC36-04, ZZ99- |  |  | 0
614 | FSSS |  |  | FS- CBL-MILL-B -01 (9ZT10GC20) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL B | THRUST PAD RADIAL BRG TEMP. ELEMENT-1MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
615 | FSSS |  |  | FS- CBL-MILL-B -02 (9ZT10GC21) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL B | THRUST PAD RADIAL BRG TEMP. ELEMENT-2MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
616 | FSSS |  |  | FS- CBL-MILL-B -03 (9ZT10GC22) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL B | THRUST PAD RADIAL BRG TEMP. ELEMENT-3MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
617 | FSSS |  |  | FS- CBL-MILL-B -04 (9ZT10GC23) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL B | THRUST PAD RADIAL BRG TEMP. ELEMENT-4MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
618 | FSSS |  |  | FS- CBL-MILL-B -05 (9ZT10GC24) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL B | THRUST PAD RADIAL BRG TEMP. ELEMENT-5MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
619 | FSSS |  |  | FS- CBL-MILL-B -06 (9ZT10GC25) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL B | THRUST PAD RADIAL BRG TEMP. ELEMENT-6MILL B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
620 | FSSS |  |  | FS- CBL-JBT/C- B-07 (9ZT10GC26) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL B | MILL -B OUTLET DUPLEX T/CMILL B | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
621 | FSSS |  |  | FS- CBL-JBT/C- B-08 (9ZT10GC27) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL B | MILL -B OUTLET DUPLEX T/CMILL B | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
622 | FSSS |  |  | FS- CBL-C-23 (9ZT10GC28) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL C | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 284 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC90-04, LR07-04, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-R4, IC01-R6, IC02-R6, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IC38-04, IC39-04, IC40-04, IR15-03, IC41-04, IC42-04, ZZ99- |  |  | 0
623 | FSSS |  |  | FS- CBL-C-24 (9ZT10GC29) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTERNEAR MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 284 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC90-02, LR07-02, LV74-04, LV25-R4, LV75-05, LV77-05, LR10-L5, IC01-L4, IC02-L4, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IC07-R4, IR08-04, IC08-04, IC09-04, IC10-04, IC11-04, IC12-04, IC13-04, IR09-04, IC24-04, IC25-04, IC26-04, IR11-04, IC27-04, IC28-04, IR12-04, IC29-04, IC33-04, IC34-04, IC38-04, IC39-04, IC40-04, IR15-03, IC41-04, IC42-04, ZZ99- |  |  | 0
624 | FSSS |  |  | FS- CBL-MILL-C -01 (9ZT10GC30) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL C | THRUST PAD RADIAL BRG TEMP. ELEMENT-1MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
625 | FSSS |  |  | FS- CBL-MILL-C -02 (9ZT10GC31) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL C | THRUST PAD RADIAL BRG TEMP. ELEMENT-2MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
626 | FSSS |  |  | FS- CBL-MILL-C -03 (9ZT10GC32) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL C | THRUST PAD RADIAL BRG TEMP. ELEMENT-3MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
627 | FSSS |  |  | FS- CBL-MILL-C -04 (9ZT10GC33) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL C | THRUST PAD RADIAL BRG TEMP. ELEMENT-4MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
628 | FSSS |  |  | FS- CBL-MILL-C -05 (9ZT10GC34) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL C | THRUST PAD RADIAL BRG TEMP. ELEMENT-5MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
629 | FSSS |  |  | FS- CBL-MILL-C -06 (9ZT10GC35) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL C | THRUST PAD RADIAL BRG TEMP. ELEMENT-6MILL C | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
630 | FSSS |  |  | FS- CBL-JBT/C- C-07 (9ZT10GC36) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL C | MILL -C OUTLET DUPLEX T/CMILL C | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
631 | FSSS |  |  | FS- CBL-JBT/C- C-08 (9ZT10GC37) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL C | MILL -C OUTLET DUPLEX T/CMILL C | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
632 | FSSS |  |  | FS- CBL-D-23 (9ZT10GC38) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL D | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 230 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC53-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IM88-03, IM89-03, IR35-03, IM90-03, IM91-03, IM93-03, ZZ99- |  |  | 0
633 | FSSS |  |  | FS- CBL-D-24 (9ZT10GC39) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTERNEAR MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 230 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC53-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IM88-03, IM89-03, IR35-03, IM90-03, IM91-03, IM93-03, ZZ99- |  |  | 0
634 | FSSS |  |  | FS- CBL-MILL-D -01 (9ZT10GC40) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL D | THRUST PAD RADIAL BRG TEMP. ELEMENT-1MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
635 | FSSS |  |  | FS- CBL-MILL-D -02 (9ZT10GC41) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL D | THRUST PAD RADIAL BRG TEMP. ELEMENT-2MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
636 | FSSS |  |  | FS- CBL-MILL-D -03 (9ZT10GC42) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL D | THRUST PAD RADIAL BRG TEMP. ELEMENT-3MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
637 | FSSS |  |  | FS- CBL-MILL-D -04 (9ZT10GC43) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL D | THRUST PAD RADIAL BRG TEMP. ELEMENT-4MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
638 | FSSS |  |  | FS- CBL-MILL-D -05 (9ZT10GC44) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL D | THRUST PAD RADIAL BRG TEMP. ELEMENT-5MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
639 | FSSS |  |  | FS- CBL-MILL-D -06 (9ZT10GC45) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL D | THRUST PAD RADIAL BRG TEMP. ELEMENT-6MILL D | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
640 | FSSS |  |  | FS- CBL-JBT/C- D-07 (9ZT10GC46) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL D | MILL -D OUTLET DUPLEX T/CMILL D | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
641 | FSSS |  |  | FS- CBL-JBT/C- D-08 (9ZT10GC47) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL D | MILL -D OUTLET DUPLEX T/CMILL D | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
642 | FSSS |  |  | FS- CBL-E-23 (9ZT10GC48) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL E | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 219 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC53-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IR34-03, IM97-03, IM98-03, IM99-03, ZZ99- |  |  | 0
643 | FSSS |  |  | FS- CBL-E-24 (9ZT10GC49) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTERNEAR MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 219 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC53-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IM85-04, IM86-04, IM87-04, IR34-03, IM97-03, IM98-03, IM99-03, ZZ99- |  |  | 0
644 | FSSS |  |  | FS- CBL-MILL-E -01 (9ZT10GC50) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL E | THRUST PAD RADIAL BRG TEMP. ELEMENT-1MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
645 | FSSS |  |  | FS- CBL-MILL-E -02 (9ZT10GC51) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL E | THRUST PAD RADIAL BRG TEMP. ELEMENT-2MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
646 | FSSS |  |  | FS- CBL-MILL-E -03 (9ZT10GC52) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL E | THRUST PAD RADIAL BRG TEMP. ELEMENT-3MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
647 | FSSS |  |  | FS- CBL-MILL-E -04 (9ZT10GC53) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL E | THRUST PAD RADIAL BRG TEMP. ELEMENT-4MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
648 | FSSS |  |  | FS- CBL-MILL-E -05 (9ZT10GC54) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL E | THRUST PAD RADIAL BRG TEMP. ELEMENT-5MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
649 | FSSS |  |  | FS- CBL-MILL-E -06 (9ZT10GC55) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL E | THRUST PAD RADIAL BRG TEMP. ELEMENT-6MILL E | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
650 | FSSS |  |  | FS- CBL-JBT/C- E-07 (9ZT10GC56) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL E | MILL -E OUTLET DUPLEX T/CMILL E | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
651 | FSSS |  |  | FS- CBL-JBT/C- E-08 (9ZT10GC57) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL E | MILL -E OUTLET DUPLEX T/CMILL E | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
652 | FSSS |  |  | FS- CBL-F-23 (9ZT10GC58) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL F | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 204 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC53-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IR33-03, IM81-03, IM82-03, IM83-03, ZZ99- |  |  | 0
653 | FSSS |  |  | FS- CBL-F-24 (9ZT10GC59) | FSSS PAN ELCONTROL EQUIPMENT ROOM (CER) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTERNEAR MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 204 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | TRICHY SCOPE CABLE | ZZ99- , CC53-04, CC05-03, IR19-03, IM06-03, IM07-06, IM09-06, IM10-05, IM11-R7, IM12-R7, IM64-06, IM65-06, IM66-06, IM67-06, IM68-06, IM72-06, IM75-04, IR28-04, IM76-04, IM77-04, IM78-04, IR32-04, IM79-04, IM80-04, IR33-03, IM81-03, IM82-03, IM83-03, ZZ99- |  |  | 0
654 | FSSS |  |  | FS- CBL-MILL-F -01 (9ZT10GC60) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL F | THRUST PAD RADIAL BRG TEMP. ELEMENT-1MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
655 | FSSS |  |  | FS- CBL-MILL-F -02 (9ZT10GC61) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL F | THRUST PAD RADIAL BRG TEMP. ELEMENT-2MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
656 | FSSS |  |  | FS- CBL-MILL-F -03 (9ZT10GC62) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL F | THRUST PAD RADIAL BRG TEMP. ELEMENT-3MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
657 | FSSS |  |  | FS- CBL-MILL-F -04 (9ZT10GC63) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL F | THRUST PAD RADIAL BRG TEMP. ELEMENT-4MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
658 | FSSS |  |  | FS- CBL-MILL-F -05 (9ZT10GC64) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL F | THRUST PAD RADIAL BRG TEMP. ELEMENT-5MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
659 | FSSS |  |  | FS- CBL-MILL-F -06 (9ZT10GC65) | ENCLOSURE FOR MOUNTING MILL TEMP. ELEMENTNEAR MILL F | THRUST PAD RADIAL BRG TEMP. ELEMENT-6MILL F | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | HYD SCOPE CABLE | SITE ROUTING |  |  | 0
660 | FSSS |  |  | FS- CBL-JBT/C- F-07 (9ZT10GC66) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL F | MILL -F OUTLET DUPLEX T/CMILL F | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
661 | FSSS |  |  | FS- CBL-JBT/C- F-08 (9ZT10GC67) | JB FOR MOUNITNG MILL OUTLET TEMP. TRANSMITTER NEAR MILL F | MILL -F OUTLET DUPLEX T/CMILL F | 02C X 0.5 Compensating ( 0.6 kV ) | 20 | [5 empty] | FSSS INTERCONNECTION DIAGRAM MILL BEARING TEMP. TRANSMITTERS | EDN SCOPE CABLE | SITE ROUTING |  |  | 0
1 | GFC |  |  | GFCA-RCP-LCP-C C-001 (9ZT07AC01) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, BC16-02, ZZ99- |  |  | 0
2 | GFC |  |  | GFCA-RCP-LCP-C C-002 (9ZT07AC02) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, BC16-02, ZZ99- |  |  | 0
3 | GFC |  |  | GFCA-RCP-LCP-C C-003 (9ZT07AC03) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, BC16-02, ZZ99- |  |  | 0
4 | GFC |  |  | GFCB-RCP-LCP-C C-001 (9ZT07AC04) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 194 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, ZZ99- |  |  | 0
5 | GFC |  |  | GFCB-RCP-LCP-C C-002 (9ZT07AC05) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 194 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, ZZ99- |  |  | 0
6 | GFC |  |  | GFCB-RCP-LCP-C C-003 (9ZT07AC06) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 194 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, ZZ99- |  |  | 0
7 | GFC |  |  | GFCC-RCP-LCP-C C-001 (9ZT07AC07) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99- |  |  | 0
8 | GFC |  |  | GFCC-RCP-LCP-C C-002 (9ZT07AC08) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99- |  |  | 0
9 | GFC |  |  | GFCC-RCP-LCP-C C-003 (9ZT07AC09) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99- |  |  | 0
10 | GFC |  |  | GFCD-RCP-LCP-C C-001 (9ZT07AC10) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
11 | GFC |  |  | GFCD-RCP-LCP-C C-002 (9ZT07AC11) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
12 | GFC |  |  | GFCD-RCP-LCP-C C-003 (9ZT07AC12) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
13 | GFC |  |  | GFCE-RCP-LCP-C C-001 (9ZT07AC13) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
14 | GFC |  |  | GFCE-RCP-LCP-C C-002 (9ZT07AC14) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
15 | GFC |  |  | GFCE-RCP-LCP-C C-003 (9ZT07AC15) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99- |  |  | 0
16 | GFC |  |  | GFCF-RCP-LCP-C C-001 (9ZT07AC16) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 177 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC20-02, BC21-02, BC22-02, ZZ99- |  |  | 0
17 | GFC |  |  | GFCF-RCP-LCP-C C-002 (9ZT07AC17) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 19C X 1.5 PVC-Cu FRLS ( 1.1 kV ) | 177 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC20-02, BC21-02, BC22-02, ZZ99- |  |  | 0
18 | GFC |  |  | GFCF-RCP-LCP-C C-003 (9ZT07AC18) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 02C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 177 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC20-02, BC21-02, BC22-02, ZZ99- |  |  | 0
19 | GFC |  |  | GFCA-LCP-RCP-S C-001 (9ZT07AC19) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 195 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R6, IC02-R6, IR06-04, IC46-04, IC47-04, BR02-04, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, BC16-03, ZZ99- |  |  | 0
20 | GFC |  |  | GFCA-LCP-RCP-S C-002 (9ZT07AC20) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 194 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-L4, IC02-L4, IR06-04, IC46-04, IC47-04, BR02-04, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, BC16-03, ZZ99- |  |  | 0
21 | GFC |  |  | GFCA-LCP-RCP-S C-003 (9ZT07AC21) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 195 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, BC16-03, ZZ99- |  |  | 0
22 | GFC |  |  | GFCA-LCP-RCP-S C-004 (9ZT07AC22) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 195 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, BC16-03, ZZ99- |  |  | 0
23 | GFC |  |  | GFCA-RCP-LCP-P C-001 (9ZT07AP01) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 03C X 016 XLPE-Al FRLS ( 1.1 kV ) | 196 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R1, IC02-R1, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IR07-01, IC50-01, IC51-01, IC52-01, BR17-01, BC01-01, BC02-01, BC03-01, BC29-01, BC30-01, BC31-01, BC11-01, BC14-01, BC15-01, BC16-01, ZZ99- |  |  | 0
24 | GFC |  |  | GFCA-RCP-LCP-P C-002 (9ZT07AC23) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, BC16-02, ZZ99-
25 | GFC |  |  | GFCB-LCP-RCP-S C-001 (9ZT07AC24) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 191 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, ZZ99-
26 | GFC |  |  | GFCB-LCP-RCP-S C-002 (9ZT07AC25) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 191 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, ZZ99-
27 | GFC |  |  | GFCB-LCP-RCP-S C-003 (9ZT07AC26) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 141 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, ZZ99-
28 | GFC |  |  | GFCB-LCP-RCP-S C-004 (9ZT07AC27) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 191 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC14-03, BC15-03, ZZ99-
29 | GFC |  |  | GFCB-RCP-LCP-P C-001 (9ZT07AP02) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 03C X 016 XLPE-Al FRLS ( 1.1 kV ) | 193 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R2, IC02-R2, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IR07-01, IC50-01, IC51-01, IC52-01, BR17-01, BC01-01, BC02-01, BC03-01, BC29-01, BC30-01, BC31-01, BC11-01, BC14-01, BC15-01, ZZ99-
30 | GFC |  |  | GFCB-RCP-LCP-P C-002 (9ZT07AC28) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 194 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC14-02, BC15-02, ZZ99-
31 | GFC |  |  | GFCC-LCP-RCP-S C-001 (9ZT07AC29) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 174 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC12-03, BC13-03, ZZ99-
32 | GFC |  |  | GFCC-LCP-RCP-S C-002 (9ZT07AC30) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 174 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC12-03, BC13-03, ZZ99-
33 | GFC |  |  | GFCC-LCP-RCP-S C-003 (9ZT07AC31) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 174 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC12-03, BC13-03, ZZ99-
34 | GFC |  |  | GFCC-LCP-RCP-S C-004 (9ZT07AC32) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 174 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC09-03, BC10-03, BC11-03, BC12-03, BC13-03, ZZ99-
35 | GFC |  |  | GFCC-RCP-LCP-P C-001 (9ZT07AP03) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 03C X 016 XLPE-Al FRLS ( 1.1 kV ) | 176 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R2, IC02-R2, IC03-R1, IC04-R1, IC05-R1, IC06-R1, IR07-01, IC50-01, IC51-01, IC52-01, BR17-01, BC01-01, BC02-01, BC03-01, BC29-01, BC30-01, BC31-01, BC11-01, BC12-01, BC13-01, ZZ99-
36 | GFC |  |  | GFCC-RCP-LCP-P C-002 (9ZT07AC33) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER C | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 178 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BC01-02, BC02-02, BC03-02, BC29-02, BC30-02, BC31-02, BC11-02, BC12-02, BC13-02, ZZ99-
37 | GFC |  |  | GFCD-LCP-RCP-S C-001 (9ZT07AC34) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 157 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
38 | GFC |  |  | GFCD-LCP-RCP-S C-002 (9ZT07AC35) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 157 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
39 | GFC |  |  | GFCD-LCP-RCP-S C-003 (9ZT07AC36) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 157 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
40 | GFC |  |  | GFCD-LCP-RCP-S C-004 (9ZT07AC37) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 157 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
41 | GFC |  |  | GFCD-RCP-LCP-P C-001 (9ZT07AP04) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 03C X 016 XLPE-Al FRLS ( 1.1 kV ) | 156 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R2, IC02-R2, IR06-02, IC46-02, IC47-02, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC17-01, BC18-01, BC19-01, ZZ99-
42 | GFC |  |  | GFCD-RCP-LCP-P C-002 (9ZT07AC38) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER D | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 158 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99-
43 | GFC |  |  | GFCE-LCP-RCP-S C-001 (9ZT07AC39) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 172 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
44 | GFC |  |  | GFCE-LCP-RCP-S C-002 (9ZT07AC40) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 172 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
45 | GFC |  |  | GFCE-LCP-RCP-S C-003 (9ZT07AC41) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 172 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
46 | GFC |  |  | GFCE-LCP-RCP-S C-004 (9ZT07AC42) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 172 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC18-03, BC19-03, ZZ99-
47 | GFC |  |  | GFCE-RCP-LCP-P C-001 (9ZT07AP05) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 03C X 016 XLPE-Al FRLS ( 1.1 kV ) | 171 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R2, IC02-R2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC17-01, BC18-01, BC19-01, ZZ99-
48 | GFC |  |  | GFCE-RCP-LCP-P C-002 (9ZT07AC43) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER E | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC18-02, BC19-02, ZZ99-
49 | GFC |  |  | GFCF-LCP-RCP-S C-001 (9ZT07AC44) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 176 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, BC22-03, ZZ99-
50 | GFC |  |  | GFCF-LCP-RCP-S C-002 (9ZT07AC45) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 176 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, BC22-03, ZZ99-
51 | GFC |  |  | GFCF-LCP-RCP-S C-003 (9ZT07AC46) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 176 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, BC22-03, ZZ99-
52 | GFC |  |  | GFCF-LCP-RCP-S C-004 (9ZT07AC47) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 02P X 1.5 Paired Screened(O) ( 0.6 kV ) | 176 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BC25-03, BC24-03, BC23-03, BC06-03, BC07-03, BC08-03, BC17-03, BC20-03, BC21-03, BC22-03, ZZ99-
53 | GFC |  |  | GFCF-RCP-LCP-P C-001 (9ZT07AP06) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 03C X 016 XLPE-Al FRLS ( 1.1 kV ) | 175 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R2, IC02-R2, IR06-01, IC46-01, IC47-01, BR02-01, BC25-01, BC24-01, BC23-01, BC06-01, BC07-01, BC08-01, BC17-01, BC20-01, BC21-01, BC22-01, ZZ99-
54 | GFC |  |  | GFCF-RCP-LCP-P C-002 (9ZT07AC48) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | LOCAL CONTROL PANEL NEAR FEEDER F | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 177 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | ZZ99- , IC01-R5, IC02-R5, IR06-03, IC46-03, IC47-03, BR02-03, BC25-02, BC24-02, BC23-02, BC06-02, BC07-02, BC08-02, BC17-02, BC20-02, BC21-02, BC22-02, ZZ99-
55 | GFC |  |  | GFCA-RCP-DCS-0 01 (9ZT07AC49) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | SITE ROUTING
56 | GFC |  |  | GFCA-RCP-DCS-0 02 (9ZT07AC50) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | SITE ROUTING
57 | GFC |  |  | GFCB-RCP-DCS-0 01 (9ZT07AC51) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | SITE ROUTING
58 | GFC |  |  | GFCB-RCP-DCS-0 02 (9ZT07AC52) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | SITE ROUTING
59 | GFC |  |  | GFCC-RCP-DCS-0 01 (9ZT07AC53) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | SITE ROUTING
60 | GFC |  |  | GFCC-RCP-DCS-0 02 (9ZT07AC54) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | SITE ROUTING
61 | GFC |  |  | GFCD-RCP-DCS-0 01 (9ZT07AC55) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | SITE ROUTING
62 | GFC |  |  | GFCD-RCP-DCS-0 02 (9ZT07AC56) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | SITE ROUTING
63 | GFC |  |  | GFCE-RCP-DCS-0 01 (9ZT07AC57) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | SITE ROUTING
64 | GFC |  |  | GFCE-RCP-DCS-0 02 (9ZT07AC58) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | SITE ROUTING
65 | GFC |  |  | GFCF-RCP-DCS-0 01 (9ZT07AC59) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | SITE ROUTING
66 | GFC |  |  | GFCF-RCP-DCS-0 02 (9ZT07AC60) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | DCS PANELSCONTROL EQUIPMENT ROOM (CER) | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | SITE ROUTING
67 | GFC |  |  | GFCA-FSS-RCP-C C-001 (9ZT07AC61) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | SITE ROUTING
68 | GFC |  |  | GFCA-RCP-FSS-S C-001 (9ZT07AC62) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | SITE ROUTING
69 | GFC |  |  | GFCB-FSS-RCP-C C-001 (9ZT07AC63) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | SITE ROUTING
70 | GFC |  |  | GFCB-RCP-FSS-S C-001 (9ZT07AC64) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | SITE ROUTING
71 | GFC |  |  | GFCC-FSS-RCP-C C-001 (9ZT07AC65) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | SITE ROUTING
72 | GFC |  |  | GFCC-RCP-FSS-S C-001 (9ZT07AC66) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | SITE ROUTING
73 | GFC |  |  | GFCD-FSS-RCP-C C-001 (9ZT07AC67) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | SITE ROUTING
74 | GFC |  |  | GFCD-RCP-FSS-S C-001 (9ZT07AC68) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | SITE ROUTING
75 | GFC |  |  | GFCE-FSS-RCP-C C-001 (9ZT07AC69) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | SITE ROUTING
76 | GFC |  |  | GFCE-RCP-FSS-S C-001 (9ZT07AC70) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | SITE ROUTING
77 | GFC |  |  | GFCF-FSS-RCP-C C-001 (9ZT07AC71) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | SITE ROUTING
78 | GFC |  |  | GFCF-RCP-FSS-S C-001 (9ZT07AC72) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | FSSS PANELCONTROL EQUIPMENT ROOM (CER) | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | SITE ROUTING
79 | GFC |  |  | GFCA-RCP-SADC- SC-001 (9ZT07AC73) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | SADC (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF003)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | TRICHY SCOPE CABLE | SITE ROUTING
80 | GFC |  |  | GFCA-SC-001 (9ZT07AC74) | COMBUSTION CONTROL SYSTEM (4-20mA DEMAND SIGNAL) TAG NO: HFB10 CF004)CONTROL EQUIPMENT ROOM (CER) (DDCMIS) | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | PEM SCOPE CABLE | SITE ROUTING
81 | GFC |  |  | GFCA-SC-002 (9ZT07AC75) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF001)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | PEM SCOPE CABLE | SITE ROUTING
82 | GFC |  |  | GFCA-SC-003 (9ZT07AC76) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF002)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | PEM SCOPE CABLE | SITE ROUTING
83 | GFC |  |  | GFCA-PC-001 (9ZT07AC77) | PDB (240V AC, 1PH INCOMING POWER SUPPLY FOR PANEL ILLUMINATION)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
84 | GFC |  |  | GFCA-PC-002 (9ZT07AC78) | PDB (415V AC, 3PH 50Hz INCOMING SUPPLY)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV20-L4, LV21-L4, LV51-02, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
85 | GFC |  |  | GFCA-PC-003 (9ZT07AC79) | UPS PDB (240V AC, 1PH)UPS ACDB | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL A) | PEM SCOPE CABLE | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, ZZ99-
86 | GFC |  |  | GFCB-RCP-SADC- SC-001 (9ZT07AC80) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | SADC (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF003)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | TRICHY SCOPE CABLE | SITE ROUTING
87 | GFC |  |  | GFCB-SC-001 (9ZT07AC81) | COMBUSTION CONTROL SYSTEM (4-20mA DEMAND SIGNAL) TAG NO: HFB10 CF004)CONTROL EQUIPMENT ROOM (CER) (DDCMIS) | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | PEM SCOPE CABLE | SITE ROUTING
88 | GFC |  |  | GFCB-SC-002 (9ZT07AC82) | FEEDER ELECTRONICS PANELUNIT SERVICE ACDB MODULE | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF001)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | PEM SCOPE CABLE | SITE ROUTING
89 | GFC |  |  | GFCB-SC-003 (9ZT07AC83) | FEEDER ELECTRONICS PANELUPS ACDB | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF002)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | PEM SCOPE CABLE | SITE ROUTING
90 | GFC |  |  | GFCB-PC-001 (9ZT07AC84) | PDB (240V AC, 1PH INCOMING POWER SUPPLY FOR PANEL ILLUMINATION)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
91 | GFC |  |  | GFCB-PC-002 (9ZT07AC85) | PDB (415V AC, 3PH 50Hz INCOMING SUPPLY)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV20-L4, LV21-L4, LV51-02, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
92 | GFC |  |  | GFCB-PC-003 (9ZT07AC86) | UPS PDB (240V AC, 1PH)UPS ACDB | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL B) | PEM SCOPE CABLE | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, ZZ99-
93 | GFC |  |  | GFCC-RCP-SADC- SC-001 (9ZT07AC87) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | SADC (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF003)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | TRICHY SCOPE CABLE | SITE ROUTING
94 | GFC |  |  | GFCC-SC-001 (9ZT07AC88) | COMBUSTION CONTROL SYSTEM (4-20mA DEMAND SIGNAL) TAG NO: HFB10 CF004)CONTROL EQUIPMENT ROOM (CER) (DDCMIS) | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | PEM SCOPE CABLE | SITE ROUTING
95 | GFC |  |  | GFCC-SC-002 (9ZT07AC89) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF001)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | PEM SCOPE CABLE | SITE ROUTING
96 | GFC |  |  | GFCC-SC-003 (9ZT07AC90) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF002)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | PEM SCOPE CABLE | SITE ROUTING
97 | GFC |  |  | GFCC-PC-001 (9ZT07AC91) | PDB (240V AC, 1PH INCOMING POWER SUPPLY FOR PANEL ILLUMINATION)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
98 | GFC |  |  | GFCC-PC-002 (9ZT07AC92) | PDB (415V AC, 3PH 50Hz INCOMING SUPPLY)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV20-L4, LV21-L4, LV51-02, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
99 | GFC |  |  | GFCC-PC-003 (9ZT07AC93) | UPS PDB (240V AC, 1PH)UPS ACDB | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL C) | PEM SCOPE CABLE | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, ZZ99-
100 | GFC |  |  | GFCD-RCP-SADC- SC-001 (9ZT07AC94) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | SADC (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF003)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | TRICHY SCOPE CABLE | SITE ROUTING
101 | GFC |  |  | GFCD-SC-001 (9ZT07AC95) | COMBUSTION CONTROL SYSTEM (4-20mA DEMAND SIGNAL) TAG NO: HFB10 CF004)CONTROL EQUIPMENT ROOM (CER) (DDCMIS) | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | PEM SCOPE CABLE | SITE ROUTING
102 | GFC |  |  | GFCD-SC-002 (9ZT07AC96) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF001)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | PEM SCOPE CABLE | SITE ROUTING
103 | GFC |  |  | GFCD-SC-003 (9ZT07AC97) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF002)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | PEM SCOPE CABLE | SITE ROUTING
104 | GFC |  |  | GFCD-PC-001 (9ZT07AC98) | PDB (240V AC, 1PH INCOMING POWER SUPPLY FOR PANEL ILLUMINATION)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
105 | GFC |  |  | GFCD-PC-002 (9ZT07AC99) | PDB (415V AC, 3PH 50Hz INCOMING SUPPLY)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 100 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV20-L4, LV21-L4, LV51-02, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
106 | GFC |  |  | GFCD-PC-003 (9ZT07BC01) | UPS PDB (240V AC, 1PH)UPS ACDB | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL D) | PEM SCOPE CABLE | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, ZZ99-
107 | GFC |  |  | GFCE-RCP-SADC- SC-001 (9ZT07BC02) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | SADC (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF003)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | TRICHY SCOPE CABLE | SITE ROUTING
108 | GFC |  |  | GFCE-SC-001 (9ZT07BC03) | COMBUSTION CONTROL SYSTEM (4-20mA DEMAND SIGNAL) TAG NO: HFB10 CF004)CONTROL EQUIPMENT ROOM (CER) (DDCMIS) | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | PEM SCOPE CABLE | SITE ROUTING
109 | GFC |  |  | GFCE-SC-002 (9ZT07BC04) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF001)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | PEM SCOPE CABLE | SITE ROUTING
110 | GFC |  |  | GFCE-SC-003 (9ZT07BC05) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF002)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | PEM SCOPE CABLE | SITE ROUTING
111 | GFC |  |  | GFCE-PC-001 (9ZT07BC06) | PDB (240V AC, 1PH INCOMING POWER SUPPLY FOR PANEL ILLUMINATION)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
112 | GFC |  |  | GFCE-PC-002 (9ZT07BC07) | PDB (415V AC, 3PH 50Hz INCOMING SUPPLY)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
113 | GFC |  |  | GFCE-PC-003 (9ZT07BC08) | UPS PDB (240V AC, 1PH)UPS ACDB | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL E) | PEM SCOPE CABLE | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, ZZ99-
114 | GFC |  |  | GFCF-RCP-SADC- SC-001 (9ZT07BC09) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | SADC (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF003)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | TRICHY SCOPE CABLE | SITE ROUTING
115 | GFC |  |  | GFCF-SC-001 (9ZT07BC10) | COMBUSTION CONTROL SYSTEM (4-20mA DEMAND SIGNAL) TAG NO: HFB10 CF004)CONTROL EQUIPMENT ROOM (CER) (DDCMIS) | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 50 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | PEM SCOPE CABLE | SITE ROUTING
116 | GFC |  |  | GFCF-SC-002 (9ZT07BC11) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF001)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | PEM SCOPE CABLE | SITE ROUTING
117 | GFC |  |  | GFCF-SC-003 (9ZT07BC12) | REMOTE CONTROL PANEL CONTROL EQUIPMENT ROOM (CER) | COMBUSTION CONTROL SYSTEM (4-20mA RATE FEEDBACK SIGNAL) TAG NO: HFB10 CF002)CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(I) ( 225 V ) | 35 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | PEM SCOPE CABLE | SITE ROUTING
118 | GFC |  |  | GFCF-PC-001 (9ZT07BC13) | PDB (240V AC, 1PH INCOMING POWER SUPPLY FOR PANEL ILLUMINATION)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 101 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | PEM SCOPE CABLE | ZZ99- , LV19-L4, LV61-05, LV31-L4, LV30-L4, LV29-L4, LV28-L4, LV27-L4, LV81-L4, LV73-03, LR08-03, CC01-03, CC72-03, CC12-03, CC13-03, CC22-03, CC23-03, CC24-02, CC25-02, CC57-03, ZZ99-
119 | GFC |  |  | GFCF-PC-002 (9ZT07BC14) | PDB (415V AC, 3PH 50Hz INCOMING SUPPLY)UNIT SERVICE ACDB MODULE | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | PEM SCOPE CABLE | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, ZZ99-
120 | GFC |  |  | GFCF-PC-003 (9ZT07BC15) | UPS PDB (240V AC, 1PH)UPS ACDB | REMOTE CONTROL PANELCONTROL EQUIPMENT ROOM (CER) | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 38 | [5 empty] | GRAVIMETRIC FEEDER INTERCONNECTION DIAGRAM (MILL F) | PEM SCOPE CABLE | ZZ99- , CC16-02, CC55-03, CC56-03, CC57-03, ZZ99-
1 | GFC |  |  | MSG-CBL-01 (9ZT04AC01) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | LDO ISO VALVE BEF FCV LO-23A EL 20300: NEAR S3L | 04P X 0.5 Paired Screened (O) ( 0.6 kV ) | 106 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM LDO ISOLATION VALVES | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CC89-04, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BD10-03, ZZ99-
2 | GFC |  |  | MSG-CBL-02 (9ZT04AC02) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | LDO BYPASS VALVE BEF FCV LO-23B EL 20300: NEAR S3L | 04P X 0.5 Paired Screened (O) ( 0.6 kV ) | 106 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM LDO ISOLATION VALVES | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CC89-04, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BD10-03, ZZ99-
3 | GFC |  |  | MSG-CBL-03 (9ZT04AC03) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | LDO DO PUMP (BOILER AREA) LDO PUMP HOUSE | 08P X 0.5 Paired Screened (O) ( 0.6 kV ) | 120 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM LDO DO PUMP | TRICHY SCOPE CABLE | SITE ROUTING
4 | GFC |  |  | MSG-CBL-04 (9ZT04AC04) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | MSGCIC-JB-1 (24 WAYS) EL 20300: NEAR S2L | 08P X 0.5 Paired Screened (O) ( 0.6 kV ) | 106 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM - LDO SCANNER AIR DP, DO TANK | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CC89-04, CC92-04, LR05-04, LV79-05, LR10-L5, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BD10-03, ZZ99-
5 | GFC |  |  | MSG-CBL-JB-1-0 1 (9ZT04AC05) | MSGCIC-JB-1 (24 WAYS) EL 20300: NEAR S2L | LDO SUPPLY DP TRANSMITTER EL 20300: NEAR S3L | 04P X 0.5 Paired Screened (O) ( 0.6 kV ) | 12 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM - LDO SCANNER AIR DP, DO TANK | TRICHY SCOPE CABLE | SITE ROUTING
6 | GFC |  |  | MSG-CBL-JB-1-0 2 (9ZT04AC06) | MSGCIC-JB-1 (24 WAYS) EL 20300: NEAR S2L | LDO DO LEVEL TRANSMITTER EL 20300: NEAR S3L | 04P X 0.5 Paired Screened (O) ( 0.6 kV ) | 12 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM - LDO SCANNER AIR DP, DO TANK | TRICHY SCOPE CABLE | SITE ROUTING
1 | TGIPL |  |  | CCA5001 (9ZB07AC01) | CCA51 | CVP09 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
2 | TGIPL |  |  | CCA5002 (9ZB07AC02) | CCA51 | CVP12 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
3 | TGIPL |  |  | CCA5003 (9ZB07AC03) | CCA51 | CVP13 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
4 | TGIPL |  |  | CCA5004 (9ZB07AC04) | CCA51 | CVP08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
5 | TGIPL |  |  | CCA5005 (9ZB07AC05) | CCA51 | CJJ08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
6 | TGIPL |  |  | CCA5007 (9ZB07AC06) | CCA51 | CVP03 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
7 | TGIPL |  |  | CCA5009 (9ZB07AC07) | CCA51 | CJJ08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
8 | TGIPL |  |  | CCA5010 (9ZB07AC08) | CCA51 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
9 | TGIPL |  |  | CCA5011 (9ZB07AC09) | CCA51 | CCA53 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
10 | TGIPL |  |  | CCA5012 (9ZB07AC10) | CCA53 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
11 | TGIPL |  |  | CCA5013 (9ZB07AC11) | CCA53 | CJJ56 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
12 | TGIPL |  |  | CCA5016 (9ZB07AC12) | CCA53 | CJJ51 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
13 | TGIPL |  |  | CCA5017 (9ZB07AC13) | CCA53 | CCA56 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
14 | TGIPL |  |  | CCA5018 (9ZB07AC14) | CCA55 | CVP11 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
15 | TGIPL |  |  | CCA5019 (9ZB07AC15) | CCA55 | CVP12 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
16 | TGIPL |  |  | CCA5020 (9ZB07AC16) | CCA55 | CVP11 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
17 | TGIPL |  |  | CCA5022 (9ZB07AC17) | CCA56 | CXW01B | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
18 | TGIPL |  |  | CCA5023 (9ZB07AC18) | CCA56 | CXW01B | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
19 | TGIPL |  |  | CCA5025 (9ZB07AC19) | CCA56 | CXW01B | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
20 | TGIPL |  |  | CCA5026 (9ZB07AC20) | CCA56 | CXW01B | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
21 | TGIPL |  |  | CCA5027 (9ZB07AC21) | CCA56 | CXW01B | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
22 | TGIPL |  |  | CCA5028 (9ZB07AC22) | CCA56 | CXW01B | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
23 | TGIPL |  |  | CCA5032 (9ZB07AC23) | CCA56 | CXW01B | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
24 | TGIPL |  |  | CCA5033 (9ZB07AC24) | CCA56 | CCA51 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
25 | TGIPL |  |  | CJJ5044 (9ZB07AC25) | CJJ51 | CJJ08 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
26 | TGIPL |  |  | CJJ5045 (9ZB07AC26) | CJJ51 | CJJ08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
27 | TGIPL |  |  | CJJ5046 (9ZB07AC27) | CJJ51 | CJJ08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
28 | TGIPL |  |  | CJJ5047 (9ZB07AC28) | CJJ51 | CJJ08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
29 | TGIPL |  |  | CJJ5048 (9ZB07AC29) | CJJ51 | CJJ55 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
30 | TGIPL |  |  | CJJ5049 (9ZB07AC30) | CJJ51 | CVP08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
31 | TGIPL |  |  | CJJ5050 (9ZB07AC31) | CJJ51 | CVP08 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
32 | TGIPL |  |  | CJJ5051 (9ZB07AC32) | CJJ51 | CVP08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
33 | TGIPL |  |  | CJJ5052 (9ZB07AC33) | CJJ51 | CVP08 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
34 | TGIPL |  |  | CJJ5053 (9ZB07AC34) | CJJ51 | CVP08 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
35 | TGIPL |  |  | CJJ5054 (9ZB07AC35) | CJJ51 | CJJ91 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
36 | TGIPL |  |  | CJJ5055 (9ZB07AC36) | CJJ51 | CJJ91 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
37 | TGIPL |  |  | CJJ5056 (9ZB07AC37) | CJJ51 | CJJ91 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
38 | TGIPL |  |  | CJJ5057 (9ZB07AC38) | CJJ51 | CJJ91 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
39 | TGIPL |  |  | CJJ5058 (9ZB07AC39) | CJJ51 | CJJ91 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
40 | TGIPL |  |  | CJJ5059 (9ZB07AC40) | CJJ51 | CVP08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
41 | TGIPL |  |  | CJJ5060 (9ZB07AC41) | CJJ51 | CVP08 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
42 | TGIPL |  |  | CJJ5061 (9ZB07AC42) | CJJ51 | CVP08 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
43 | TGIPL |  |  | CJJ5062 (9ZB07AC43) | CJJ51 | CVP08 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
44 | TGIPL |  |  | CJJ5063 (9ZB07AC44) | CJJ53 | CCA55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
45 | TGIPL |  |  | CJJ5064 (9ZB07AC45) | CJJ53 | CJJ55 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
46 | TGIPL |  |  | CJJ5065 (9ZB07AC46) | CJJ53 | CJJ08 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
47 | TGIPL |  |  | CJJ5066 (9ZB07AC47) | CJJ53 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
48 | TGIPL |  |  | CJJ5067 (9ZB07AC48) | CJJ53 | CJJ08 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
49 | TGIPL |  |  | CJJ5068 (9ZB07AC49) | CJJ55 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
50 | TGIPL |  |  | CJJ5069 (9ZB07AC50) | CJJ55 | CJF04 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
51 | TGIPL |  |  | CJJ5071 (9ZB07AC51) | CJJ56 | CJJ55 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
52 | TGIPL |  |  | CJJ5073 (9ZB07AC52) | CJJ56 | CJJ91 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
53 | TGIPL |  |  | CJJ5074 (9ZB07AC53) | CJJ56 | CJJ91 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
54 | TGIPL |  |  | CJJ5075 (9ZB07AC54) | CJJ61 | CCA60 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
55 | TGIPL |  |  | CJJ5076 (9ZB07AC55) | CJJ61 | CJJ55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
56 | TGIPL |  |  | CJJ5077 (9ZB07AC56) | CJJ61 | CJJ56 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
57 | TGIPL |  |  | CJJ5078 (9ZB07AC57) | CJJ61 | CCA60 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 35 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
58 | TGIPL |  |  | CCA4001 (9ZB07AC58) | CCA51 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
59 | TGIPL |  |  | CCA4002 (9ZB07AC59) | CCA53 | CWD01 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
60 | TGIPL |  |  | CCA4003 (9ZB07AC60) | CCA53 | CWD01 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
61 | TGIPL |  |  | CCA4004 (9ZB07AC61) | CCA53 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
62 | TGIPL |  |  | CCA4005 (9ZB07AC62) | CCA55 | CWD01 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
63 | TGIPL |  |  | CCA4006 (9ZB07AC63) | CCA56 | CWD01 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
64 | TGIPL |  |  | CJJ4007 (9ZB07AC64) | CJJ51 | CWD01 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
65 | TGIPL |  |  | CJJ4008 (9ZB07AC65) | CJJ51 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
66 | TGIPL |  |  | CJJ4009 (9ZB07AC66) | CJJ55 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
67 | TGIPL |  |  | CJJ4010 (9ZB07AC67) | CJJ56 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
68 | TGIPL |  |  | CJJ4011 (9ZB07AC68) | CJJ55 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
69 | TGIPL |  |  | CJJ4012 (9ZB07AC69) | CJJ56 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
70 | TGIPL |  |  | CCA4013 (9ZB07AC70) | CCA55 | CWD01 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
71 | TGIPL |  |  | CCA4014 (9ZB07AC71) | CCA56 | CWD01 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 40 | [5 empty] | FRLS PVC | HARDWIRED EXCHANGE | SITE ROUTING
1 | TGICD |  |  | CCA3002 (9ZB09AC01) | MYA01GE001A | CCA51 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
2 | TGICD |  |  | CCA3003 (9ZB09AC02) | LBC00GB001 | CCA51 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
3 | TGICD |  |  | CCA3004 (9ZB09AC03) | MAA00GB001 | CCA51 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
4 | TGICD |  |  | CCA3006 (9ZB09AC04) | MAB00GB001 | CCA51 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
5 | TGICD |  |  | CCA3008 (9ZB09AC05) | MYA01GB001A | CCA51 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
6 | TGICD |  |  | CCA3009 (9ZB09AC06) | MYA01GB001A | CCA51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
7 | TGICD |  |  | CCA3010 (9ZB09AC07) | MYA01GB001A | CCA51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
8 | TGICD |  |  | CCA3011 (9ZB09AC08) | MYA01GB001A | CCA51 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
9 | TGICD |  |  | CCA3012 (9ZB09AC09) | MYA01GB001C | CCA51 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
10 | TGICD |  |  | CCA3013 (9ZB09AC10) | MYA01GB001A | CCA51 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
11 | TGICD |  |  | CCA3015 (9ZB09AC11) | MYA01GB001D | CCA51 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
12 | TGICD |  |  | CCA3017 (9ZB09AC12) | MAX00GE002 | CCA53 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
13 | TGICD |  |  | CCA3018 (9ZB09AC13) | MAX00GE002 | CCA53 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
14 | TGICD |  |  | CCA3019 (9ZB09AC14) | MAV00GB001 | CCA53 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
15 | TGICD |  |  | CCA3020 (9ZB09AC15) | MAX00GB004 | CCA53 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
16 | TGICD |  |  | CCA3022 (9ZB09AC16) | MAV00GC002 | CCA53 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
17 | TGICD |  |  | CCA3024 (9ZB09AC17) | MAV00GC002 | CCA53 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
18 | TGICD |  |  | CCA3025 (9ZB09AC18) | MAV00GB001 | CCA53 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
19 | TGICD |  |  | CCA3028 (9ZB09AC19) | MAX00GB003 | CCA53 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
20 | TGICD |  |  | CCA3030 (9ZB09AC20) | MAV00GB002 | CCA53 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
21 | TGICD |  |  | CCA3031 (9ZB09AC21) | MYA00GU003 | CCA53 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
22 | TGICD |  |  | CCA3032 (9ZB09AC22) | MAV00GB001 | CCA53 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
23 | TGICD |  |  | CCA3033 (9ZB09AC23) | MAV00GB001 | CCA53 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
24 | TGICD |  |  | CCA3034 (9ZB09AC24) | MYA00GU003 | CCA53 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
25 | TGICD |  |  | CCA3035 (9ZB09AC25) | MAA00GU112 | CCA53 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
26 | TGICD |  |  | CCA3036 (9ZB09AC26) | MAB00GU111 | CCA53 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
27 | TGICD |  |  | CCA3037 (9ZB09AC27) | MAY00GC001 | CCA55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
28 | TGICD |  |  | CCA3038 (9ZB09AC28) | MYA00GU003 | CCA55 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
29 | TGICD |  |  | CCA3039 (9ZB09AC29) | MKC01GC001A | CCA56 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
30 | TGICD |  |  | CCA3040 (9ZB09AC30) | MKA11GU021OUT | CCA56 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
31 | TGICD |  |  | CCA3043 (9ZB09AC31) | MKA11GU022OUT | CCA56 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
32 | TGICD |  |  | CCA3045 (9ZB09AC32) | MKA11GU023OUT | CCA56 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
33 | TGICD |  |  | CCA3046 (9ZB09AC33) | MKA11GU023OUT | CCA56 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
34 | TGICD |  |  | CCA3047 (9ZB09AC34) | MKY00GF003 | CCA56 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
35 | TGICD |  |  | CCA3048 (9ZB09AC35) | MKY00GF003 | CCA56 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
36 | TGICD |  |  | CCA3049 (9ZB09AC36) | MKY00GF003 | CCA56 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
37 | TGICD |  |  | CCA3052 (9ZB09AC37) | MKY00GU002 | CCA56 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
38 | TGICD |  |  | CCA3054 (9ZB09AC38) | MKY00GU114OUT | CCA56 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
39 | TGICD |  |  | CCA3057 (9ZB09AC39) | MKY00GU114OUT | CCA56 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
40 | TGICD |  |  | CCA3058 (9ZB09AC40) | PGB00GU001 | CCA56 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
41 | TGICD |  |  | CCA3059 (9ZB09AC41) | PGB00GU002 | CCA56 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
42 | TGICD |  |  | CCA3061 (9ZB09AC42) | MKY00GU004 | CCA56 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
43 | TGICD |  |  | CCA3062 (9ZB09AC43) | MKY00GU004 | CCA56 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
44 | TGICD |  |  | CJJ3063 (9ZB09AC44) | MYA01GE001A | CJJ08 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
45 | TGICD |  |  | CJJ3064 (9ZB09AC45) | MAD11GC001A | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
46 | TGICD |  |  | CJJ3065 (9ZB09AC46) | MAD11GC001B | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
47 | TGICD |  |  | CJJ3066 (9ZB09AC47) | MAD11GC001A | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
48 | TGICD |  |  | CJJ3067 (9ZB09AC48) | MYA01GB001D | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
49 | TGICD |  |  | CJJ3068 (9ZB09AC49) | MYA01GC001A | CJJ51 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
50 | TGICD |  |  | CJJ3071 (9ZB09AC50) | MYA01GC001A | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
51 | TGICD |  |  | CJJ3072 (9ZB09AC51) | MYA01GC001A | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
52 | TGICD |  |  | CJJ3073 (9ZB09AC52) | MAY00GU112 | CJJ51 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
53 | TGICD |  |  | CJJ3076 (9ZB09AC53) | MAB00GU112 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
54 | TGICD |  |  | CJJ3077 (9ZB09AC54) | MAA00GU112 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
55 | TGICD |  |  | CJJ3078 (9ZB09AC55) | MAB00GU111 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
56 | TGICD |  |  | CJJ3079 (9ZB09AC56) | LBA00GU111 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
57 | TGICD |  |  | CJJ3080 (9ZB09AC57) | LBY00GU111 | CJJ51 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
58 | TGICD |  |  | CJJ3082 (9ZB09AC58) | MAY00GU111 | CJJ51 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
59 | TGICD |  |  | CJJ3084 (9ZB09AC59) | MAY00GU112 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
60 | TGICD |  |  | CJJ3085 (9ZB09AC60) | MAY00GU001 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
61 | TGICD |  |  | CJJ3086 (9ZB09AC61) | LBY00GC001 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
62 | TGICD |  |  | CJJ3087 (9ZB09AC62) | LBY00GC001 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
63 | TGICD |  |  | CJJ3088 (9ZB09AC63) | MYA00GC001 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
64 | TGICD |  |  | CJJ3089 (9ZB09AC64) | LBS00GC001 | CJJ51 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
65 | TGICD |  |  | CJJ3091 (9ZB09AC65) | MAB00GU112 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
66 | TGICD |  |  | CJJ3092 (9ZB09AC66) | LBY00GC001 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
67 | TGICD |  |  | CJJ3093 (9ZB09AC67) | MYA00GC001 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
68 | TGICD |  |  | CJJ3094 (9ZB09AC68) | MAA00GU113 | CJJ51 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
69 | TGICD |  |  | CJJ3095 (9ZB09AC69) | MAL00GU111 | CJJ51 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
70 | TGICD |  |  | CJJ3097 (9ZB09AC70) | MAL00GU112 | CJJ51 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
71 | TGICD |  |  | CJJ3101 (9ZB09AC71) | LBS00GU111 | CJJ51 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
72 | TGICD |  |  | CJJ3102 (9ZB09AC72) | MAY00GC003 | CJJ51 | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
73 | TGICD |  |  | CJJ3104 (9ZB09AC73) | MAY00GC003 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
74 | TGICD |  |  | CJJ3105 (9ZB09AC74) | MYA00GC001 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
75 | TGICD |  |  | CJJ3107 (9ZB09AC75) | LBS00GC002 | CJJ51 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
76 | TGICD |  |  | CJJ3109 (9ZB09AC76) | LBS00GC001 | CJJ51 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
77 | TGICD |  |  | CJJ3110 (9ZB09AC77) | MAV00GU001 | CJJ51 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
78 | TGICD |  |  | CJJ3114 (9ZB09AC78) | LBY00GC001 | CJJ53 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
79 | TGICD |  |  | CJJ3115 (9ZB09AC79) | MAB00GU111 | CJJ53 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
80 | TGICD |  |  | CJJ3116 (9ZB09AC80) | MAN00GB002 | CJJ53 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
81 | TGICD |  |  | CJJ3119 (9ZB09AC81) | MYA00GC001 | CJJ53 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
82 | TGICD |  |  | CJJ3120 (9ZB09AC82) | MYA00GC002 | CJJ53 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
83 | TGICD |  |  | CJJ3121 (9ZB09AC83) | MAW00GF001 | CJJ53 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
84 | TGICD |  |  | CJJ3128 (9ZB09AC84) | MAY00GC001 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
85 | TGICD |  |  | CJJ3129 (9ZB09AC85) | MAY00GC001 | CJJ55 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
86 | TGICD |  |  | CJJ3130 (9ZB09AC86) | MAV00GB002 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
87 | TGICD |  |  | CJJ3131 (9ZB09AC87) | MAY00GC001 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
88 | TGICD |  |  | CJJ3132 (9ZB09AC88) | MAY00GC001 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
89 | TGICD |  |  | CJJ3133 (9ZB09AC89) | MAV00GB002 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
90 | TGICD |  |  | CJJ3134 (9ZB09AC90) | MAV00GB002 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
91 | TGICD |  |  | CJJ3135 (9ZB09AC91) | MAA00GU113 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
92 | TGICD |  |  | CJJ3136 (9ZB09AC92) | LBA00GU111 | CJJ55 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
93 | TGICD |  |  | CJJ3137 (9ZB09AC93) | MAA00GU113 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
94 | TGICD |  |  | CJJ3138 (9ZB09AC94) | MAA00GU113 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
95 | TGICD |  |  | CJJ3139 (9ZB09AC95) | MAD00GU113 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
96 | TGICD |  |  | CJJ3140 (9ZB09AC96) | MAD00GU113 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
97 | TGICD |  |  | CJJ3141 (9ZB09AC97) | MAD01GU113 | CJJ55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
98 | TGICD |  |  | CJJ3142 (9ZB09AC98) | MAD00GU111 | CJJ55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
99 | TGICD |  |  | CJJ3143 (9ZB09AC99) | MAD01GU111 | CJJ55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
100 | TGICD |  |  | CJJ3148 (9ZB09BC01) | MAD00GU110 | CJJ55 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
101 | TGICD |  |  | CJJ3150 (9ZB09BC02) | MAD00GU110 | CJJ55 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
102 | TGICD |  |  | CJJ3151 (9ZB09BC03) | MAD01GU110 | CJJ55 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
103 | TGICD |  |  | CJJ3152 (9ZB09BC04) | MAD00GU112 | CJJ55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
104 | TGICD |  |  | CJJ3153 (9ZB09BC05) | MAD01GU112 | CJJ55 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
105 | TGICD |  |  | CJJ3157 (9ZB09BC06) | MAD00GU113 | CJJ55 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
106 | TGICD |  |  | CJJ3161 (9ZB09BC07) | MKY00GU115OUT | CJJ55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
107 | TGICD |  |  | CJJ3164 (9ZB09BC08) | MKY00GU115OUT | CJJ55 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
108 | TGICD |  |  | CJJ3167 (9ZB09BC09) | MYA01GE001A | CJJ55 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
109 | TGICD |  |  | CJJ3168 (9ZB09BC10) | MKA11GU022OUT | CJJ56 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
110 | TGICD |  |  | CJJ3171 (9ZB09BC11) | MAY00GU111 | CJJ56 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
111 | TGICD |  |  | CJJ3172 (9ZB09BC12) | MKA11GU023OUT | CJJ56 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
112 | TGICD |  |  | CJJ3173 (9ZB09BC13) | MKA11GU023OUT | CJJ56 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
113 | TGICD |  |  | CJJ3174 (9ZB09BC14) | MYA01GE001A | CJJ56 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
114 | TGICD |  |  | CJJ3175 (9ZB09BC15) | MAA00GB001 | CJJ61 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
115 | TGICD |  |  | CJJ3178 (9ZB09BC16) | MAB00GB001 | CJJ61 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
116 | TGICD |  |  | CJJ3181 (9ZB09BC17) | MAX00GB001 | CJJ61 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
117 | TGICD |  |  | CJJ3182 (9ZB09BC18) | MAY00GC003 | CJJ61 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
118 | TGICD |  |  | CJJ3184 (9ZB09BC19) | MYA01GB001A | CJJ61 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
119 | TGICD |  |  | CJJ3185 (9ZB09BC20) | MYA01GB001B | CJJ61 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
120 | TGICD |  |  | CJJ3187 (9ZB09BC21) | MYA01GB001A | CJJ61 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
121 | TGICD |  |  | CJJ3188 (9ZB09BC22) | MYA01GB001C | CJJ61 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
122 | TGICD |  |  | CJJ3189 (9ZB09BC23) | MAY00GC003 | CJJ61 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
123 | TGICD |  |  | CJJ3190 (9ZB09BC24) | MYA01GB001A | CJJ61 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
124 | TGICD |  |  | CJJ3193 (9ZB09BC25) | MYA01GB001A | CJJ61 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
125 | TGICD |  |  | CJJ3194 (9ZB09BC26) | MYA01GB001B | CJJ61 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
126 | TGICD |  |  | CJJ3197 (9ZB09BC27) | MAA00GB001 | CJJ61 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
127 | TGICD |  |  | CJJ3198 (9ZB09BC28) | MAX00GB002 | CJJ61 | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
128 | TGICD |  |  | CJJ3202 (9ZB09BC29) | MAB00GB001 | CJJ61 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
129 | TGICD |  |  | CJJ3203 (9ZB09BC30) | MYA01GB001B | CJJ61 | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
130 | TGICD |  |  | CJJ3204 (9ZB09BC31) | MAX00GB001 | CJJ61 | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
131 | TGICD |  |  | CJJ3205 (9ZB09BC32) | MAX00GB002 | CJJ61 | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
132 | TGICD |  |  | CJJ3209A (9ZB09BC33) | MYA01GE001A | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
133 | TGICD |  |  | CJJ3209B (9ZB09BC34) | MYA01GE001A | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
134 | TGICD |  |  | CJJ3209C (9ZB09BC35) | MYA01GE001A | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
135 | TGICD |  |  | CJJ3210A (9ZB09BC36) | MAX00GE001 | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
136 | TGICD |  |  | CJJ3210B (9ZB09BC37) | MAX00GE001 | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
137 | TGICD |  |  | CJJ3210C (9ZB09BC38) | MAX00GE001 | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
138 | TGICD |  |  | CJJ3210D (9ZB09BC39) | MAX00GE001 | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
139 | TGICD |  |  | CJJ3211 (9ZB09BC40) | MYA01GB001C | CJJ61 | 04C X 2.5 PVC-Cu(A) FRLS ( 1.1 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
140 | TGICD |  |  | CJJ3212 (9ZB09BC41) | MAD00GC017 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
141 | TGICD |  |  | CJJ3213A (9ZB09BC42) | MAD00GC015 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
142 | TGICD |  |  | CJJ3213B (9ZB09BC43) | MAD00GC016 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
143 | TGICD |  |  | CJJ3214 (9ZB09BC44) | MAD00GC017 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
144 | TGICD |  |  | CJJ3215A (9ZB09BC45) | MAD00GC020 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
145 | TGICD |  |  | CJJ3215B (9ZB09BC46) | MAD00GC020 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
146 | TGICD |  |  | CJJ3216A (9ZB09BC47) | MAD00GC018 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
147 | TGICD |  |  | CJJ3216B (9ZB09BC48) | MAD00GC019 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
148 | TGICD |  |  | CJJ3216C (9ZB09BC49) | MAD00GC019 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
149 | TGICD |  |  | CJJ3217A (9ZB09BC50) | MAD00GC011 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
150 | TGICD |  |  | CJJ3217B (9ZB09BC51) | MAD00GC011 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
151 | TGICD |  |  | CJJ3218A (9ZB09BC52) | MAD00GC012 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
152 | TGICD |  |  | CJJ3218B (9ZB09BC53) | MAD00GC012 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
153 | TGICD |  |  | CJJ3219A (9ZB09BC54) | MAD00GC013 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
154 | TGICD |  |  | CJJ3219B (9ZB09BC55) | MAD00GC013 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
155 | TGICD |  |  | CJJ3220A (9ZB09BC56) | MAD00GC014 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
156 | TGICD |  |  | CJJ3220B (9ZB09BC57) | MAD00GC014 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
157 | TGICD |  |  | CJJ3221 (9ZB09BC58) | MAD00GC015 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
158 | TGICD |  |  | CJJ3222 (9ZB09BC59) | MAD00GC017 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
159 | TGICD |  |  | CJJ3223 (9ZB09BC60) | MAD00GC017 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
160 | TGICD |  |  | CJJ3224A (9ZB09BC61) | MKD00GC011 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
161 | TGICD |  |  | CJJ3224B (9ZB09BC62) | MKD00GC011 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
162 | TGICD |  |  | CJJ3225A (9ZB09BC63) | MKD00GC012 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
163 | TGICD |  |  | CJJ3225B (9ZB09BC64) | MKD00GC012 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
164 | TGICD |  |  | CJJ3226A (9ZB09BC65) | MKD00GC013 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
165 | TGICD |  |  | CJJ3226B (9ZB09BC66) | MKD00GC013 | CJJ91 | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
166 | TGICD |  |  | CXW3227 (9ZB09BC67) | MKY00GF005 | CXW01B | 12P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
167 | TGICD |  |  | CXW3254 (9ZB09BC68) | MKY00GF001 | CXW01B | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
168 | TGICD |  |  | CXW3260 (9ZB09BC69) | MKY00GF003 | CXW01B | 08P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
169 | TGICD |  |  | CXW3268 (9ZB09BC70) | MKY00GF003 | CXW01B | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 120 | [5 empty] | SIGNAL ACQUSITION | FRLS PVC | SITE ROUTING
1 | ERVFTP |  |  | FTP-CBL-01 (9ZT05AC01) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | FTP STARTER BOX-1 EL 41100: NEAR S10L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 135 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BJ05-03, ZZ99-
2 | ERVFTP |  |  | FTP-CBL-02 (9ZT05AC02) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | FTP STARTER BOX-1 EL 41100: NEAR S10L | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 136 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BJ05-03, ZZ99-
3 | ERVFTP |  |  | FTP-CBL-03 (9ZT05AC03) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | FTP STARTER BOX-1 EL 41100: NEAR S10L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 136 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BJ05-03, ZZ99-
4 | ERVFTP |  |  | FTP-CBL-07 (9ZT05AC04) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | TEMP. TRANSMITTER EL 42420 ; NEAR S10L | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 136 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BJ05-03, ZZ99-
5 | ERVFTP |  |  | FTP-CBL-08 (9ZT05AC05) | TEMP. TRANSMITTER EL 42420 ; NEAR S10L | FTP-1 THERMOCOUPLE EL 42420 ; FURNACE LEFT SIDE WALL | 02C X 0.5 Compensating ( 1.1 kV ) | 43 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BJ05-03, BJ06-03, ZZ99-
6 | ERVFTP |  |  | FTP-CBL-04 (9ZT05AC06) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | FTP STARTER BOX-2 EL 41100: NEAR S10R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 108 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BJ01-03, ZZ99-
7 | ERVFTP |  |  | FTP-CBL-05 (9ZT05AC07) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | FTP STARTER BOX-2 EL 41100: NEAR S10R | 08P X 0.5 Paired Screened(O) ( 0.6 kV ) | 108 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BJ01-03, ZZ99-
8 | ERVFTP |  |  | FTP-CBL-06 (9ZT05AC08) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | FTP STARTER BOX-2 EL 41100: NEAR S10R | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 108 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BJ01-03, ZZ99-
9 | ERVFTP |  |  | FTP-CBL-09 (9ZT05AC09) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | TEMP. TRANSMITTER EL 42420 ; NEAR S10R | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 108 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BJ01-03, ZZ99-
10 | ERVFTP |  |  | FTP-CBL-10 (9ZT05AC10) | TEMP. TRANSMITTER EL 42420 ; NEAR S10R | FTP-2 THERMOCOUPLE EL 42420 ; FURNACE RIGHT SIDE WALL | 02C X 0.5 Compensating ( 1.1 kV ) | 43 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BJ01-03, BJ02-03, ZZ99-
11 | ERVFTP |  |  | ERV-CBL-01 (9ZT05AC11) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | SH ERV ISOLATION VALVE -LEFT EL 56520: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 152 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R4, IC04-R4, IC05-R4, IC06-R4, IR07-04, IC50-04, IC51-04, IC52-04, BR17-02, BR18-04, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, ZZ99-
12 | ERVFTP |  |  | ERV-CBL-02 (9ZT05AC12) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | SH ERV ISOLATION BY PASS VALVE -LEFT EL 56520: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 152 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, ZZ99-
13 | ERVFTP |  |  | ERV-CBL-03 (9ZT05AC13) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | SH ERV ISOLATION VALVE -RIGHT EL 56520: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 137 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, BO07-03, ZZ99-
14 | ERVFTP |  |  | ERV-CBL-04 (9ZT05AC14) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | SH ERV ISOLATION BY PASS VALVE -RIGHT EL 56520: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 137 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, BO07-03, ZZ99-
15 | ERVFTP |  |  | ERV-CBL-05 (9ZT05AC15) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | SH ERV ISOLATION VALVE -RIGHT EL 56520: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 136 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, BO07-03, ZZ99-
16 | ERVFTP |  |  | ERV-CBL-06 (9ZT05AC16) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | SH ERV ISOLATION BY PASS VALVE -RIGHT EL 56520: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 136 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, BO07-03, ZZ99-
17 | ERVFTP |  |  | ERV-CBL-07 (9ZT05AC17) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | RH ERV ISOLATION VALVE -LEFT EL 58120: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 155 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, BR70-03, ZZ99-
18 | ERVFTP |  |  | ERV-CBL-08 (9ZT05AC18) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | RH ERV ISOLATION BY PASS VALVE -LEFT EL 58120: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 155 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, BR70-03, ZZ99-
19 | ERVFTP |  |  | ERV-CBL-09 (9ZT05AC19) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | RH ERV ISOLATION VALVE -RIGHT EL 58120: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 131 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BR71-03, BR69-03, ZZ99-
20 | ERVFTP |  |  | ERV-CBL-10 (9ZT05AC20) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | RH ERV ISOLATION BY PASS VALVE -RIGHT EL 58120: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 131 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-04, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BR71-03, BR69-03, ZZ99-
21 | ERVFTP |  |  | ERV-CBL-19 (9ZT05AC21) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | ERV-JB-01 (24 WAYS) EL 56850: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 151 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-04, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, ZZ99-
22 | ERVFTP |  |  | ERV-CBL-JB-01- 1 (9ZT05AC22) | ERV-JB-01 (24 WAYS)EL 56850: NEAR S10L | RH ERV (LEFT) (LBB50 AA705) EL 58120: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO01-03, BR70-03, ZZ99-
23 | ERVFTP |  |  | ERV-CBL-JB-01- 2 (9ZT05AC23) | ERV-JB-01 (24 WAYS)EL 56850: NEAR S10L | RH ERV (RIGHT) (LBB50 AA706) EL 58120: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 76 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO01-03, BR30-03, BP03-02, BP04-02, BP05-02, BP06-02, BR15-03, BO05-03, BR71-03, BR69-03, ZZ99-
24 | ERVFTP |  |  | ERV-CBL-20 (9ZT05AC24) | MSGCIC CABINET CONTROL EQUIPMENT ROOM (CER) | ERV-JB-02 (24 WAYS) EL 56850: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 151 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , CC71-07, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, BR20-03, BR21-03, BR22-05, BR23-05, BR24-05, BR25-03, BR26-03, BR27-03, BR28-03, BR29-03, BO01-03, ZZ99-
25 | ERVFTP |  |  | ERV-CBL-JB-02- 1 (9ZT05AC25) | ERV-JB-02 (36 WAYS)EL 55950: NEAR S4R | SH ERV (LEFT) (LBA25 AA702) EL 56520: NEAR S10L | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 85 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BN04-03, BN03-03, BR14-03, BR15-03, BP06-02, BP05-02, BP04-02, BP03-02, BR30-03, BO01-03, ZZ99-
26 | ERVFTP |  |  | ERV-CBL-JB-02- 2 (9ZT05AC26) | ERV-JB-02 (36 WAYS)EL 55950: NEAR S4R | SH ERV (RIGHT) (LBA25 AA704) EL 56520: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 65 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BN04-03, BN03-03, BR14-03, BO05-03, BO06-03, BO07-03, ZZ99-
27 | ERVFTP |  |  | ERV-CBL-JB-02- 3 (9ZT05AC27) | ERV-JB-02 (36 WAYS)EL 55950: NEAR S4R | SH ERV (RIGHT) (LBA25 AA705) EL 56520: NEAR S4R | 04P X 0.5 Paired Screened(O) ( 0.6 kV ) | 66 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BN04-03, BN03-03, BR14-03, BO05-03, BR71-03, BR69-03, BO07-03, ZZ99-
28 | ERVFTP |  |  | ERV-CBL-21 (9ZT05AC28) | 220V DC PDB DC PDB | MSGCIC CONTROL (MS ERV -LEFT) LBA25 AA702PART OF MSGCIC CONTROL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | PEM SCOPE CABLE | LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, BR21-04, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP02-02, ZZ99-
29 | ERVFTP |  |  | ERV-CBL-22 (9ZT05AC29) | MSGCIC CONTROL (MS ERV-LEFT) LBA25 AA702PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -LEFT) LBA25 AA702 EL 56850: NEAR S10L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP01-02, BR70-02, BO01-02, ZZ99-
30 | ERVFTP |  |  | ERV-CBL-23 (9ZT05AC30) | MSGCIC CONTROL (MS ERV-LEFT) LBA25 AA702PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -LEFT) LBA25 AA702 EL 56850: NEAR S10L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP01-02, BR70-02, BO01-02, ZZ99-
31 | ERVFTP |  |  | ERV-CBL-24 (9ZT05AC31) | ERV CONTROLLER (MS ERV -LEFT) LBA25 AA702EL 56850: NEAR S10L | ERV SOV (MS ERV -LEFT) LBA25 AA702 EL 56520: NEAR S10L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 21 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | BO01-02, ZZ99-
32 | ERVFTP |  |  | ERV-CBL-25 (9ZT05AC32) | ERV SOV (MS ERV -LEFT) LBA25 AA702EL 56520: NEAR S10L | MSGCIC CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 151 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BR21-03, BR20-03, BR19-03, BR18-02, BR17-02, IC52-02, IC51-02, IC50-02, IR07-02, IC06-R2, IC05-R2, IC04-R2, IC03-R2, IC02-R3, IC01-R3, CR01-R2, CC71-07, ZZ99-
33 | ERVFTP |  |  | ERV-CBL-26 (9ZT05AC33) | 220V DC PDB DC PDB | MSGCIC CONTROL (MS ERV -RIGHT) LBA25 AA704PART OF MSGCIC CONTROL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | PEM SCOPE CABLE | LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-01, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BP08-02, ZZ99-
34 | ERVFTP |  |  | ERV-CBL-27 (9ZT05AC34) | MSGCIC CONTROL (MS ERV-RIGHT) LBA25 AA704PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -RIGHT) LBA25 AA704 EL 56850: NEAR S4R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP07-02, BR69-02, BO07-02, ZZ99-
35 | ERVFTP |  |  | ERV-CBL-28 (9ZT05AC35) | MSGCIC CONTROL (MS ERV-RIGHT) LBA25 AA704PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -RIGHT) LBA25 AA704 EL 56850: NEAR S4R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP07-02, BR69-02, BO07-02, ZZ99-
36 | ERVFTP |  |  | ERV-CBL-29 (9ZT05AC36) | ERV CONTROLLER (MS ERV -RIGHT) LBA25 AA704EL 56850: NEAR S4R | ERV SOV (MS ERV -RIGHT) LBA25 AA704 EL 56520: NEAR S10R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 39 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO07-02, BO06-02, BO05-02, ZZ99-
37 | ERVFTP |  |  | ERV-CBL-30 (9ZT05AC37) | ERV SOV (MS ERV -RIGHT) LBA25 AA704EL 56520: NEAR S4R | MSGCIC CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 136 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO07-03, BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R3, IC01-R3, CR01-R2, CC71-07, ZZ99-
38 | ERVFTP |  |  | ERV-CBL-31 (9ZT05AC38) | 220V DC PDB DC PDB | MSGCIC CONTROL (MS ERV-RIGHT) LBA25 AA705PART OF MSGCIC CONTROL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | PEM SCOPE CABLE | LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-01, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BP08-02, ZZ99-
39 | ERVFTP |  |  | ERV-CBL-32 (9ZT05AC39) | MSGCIC CONTROL (MS ERV-RIGHT) LBA25 AA705PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV-RIGHT) LBA25 AA705 EL 56850: NEAR S4R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP07-02, BR69-02, BO07-02, ZZ99-
40 | ERVFTP |  |  | ERV-CBL-33 (9ZT05AC40) | MSGCIC CONTROL (MS ERV-RIGHT) LBA25 AA705PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV-RIGHT) LBA25 AA705 EL 56850: NEAR S4R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP07-02, BR69-02, BO07-02, ZZ99-
41 | ERVFTP |  |  | ERV-CBL-34 (9ZT05AC41) | ERV CONTROLLER (MS ERV-RIGHT) LBA25 AA705EL 56850: NEAR S4R | ERV SOV (MS ERV-RIGHT) LBA25 AA705 EL 56520: NEAR S10R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 39 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO07-02, BO06-02, BO05-02, ZZ99-
42 | ERVFTP |  |  | ERV-CBL-35 (9ZT05AC42) | ERV SOV (MS ERV-RIGHT) LBA25 AA705EL 56520: NEAR S4R | MSGCIC CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 136 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO07-03, BO06-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R3, IC01-R3, CR01-R2, CC71-07, ZZ99-
43 | ERVFTP |  |  | ERV-CBL-36 (9ZT05AC43) | 220V DC PDB DC PDB | MSGCIC CONTROL (MS ERV -LEFT) LBA25 AA702PART OF MSGCIC CONTROL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 168 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | PEM SCOPE CABLE | LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BR20-04, BR21-04, BR22-04, BR23-04, BR24-04, BR25-02, BR26-02, BR27-02, BR28-02, BR29-02, BO01-02, BR70-02, BP02-02, ZZ99-
44 | ERVFTP |  |  | ERV-CBL-37 (9ZT05AC44) | MSGCIC CONTROL (RH ERV-LEFT) LBB50 AA705PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -LEFT) LBA25 AA702 EL 56850: NEAR S10L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP01-02, BR70-02, BO01-02, ZZ99-
45 | ERVFTP |  |  | ERV-CBL-38 (9ZT05AC45) | MSGCIC CONTROL (RH ERV-LEFT) LBB50 AA705PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -LEFT) LBA25 AA702 EL 56850: NEAR S10L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 35 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP01-02, BR70-02, BO01-02, ZZ99-
46 | ERVFTP |  |  | ERV-CBL-39 (9ZT05AC46) | ERV CONTROLLER (RH ERV-LEFT) LBB50 AA705EL 56850: NEAR S10L | ERV SOV (MS ERV -LEFT) LBA25 AA702 EL 58120: NEAR S10L | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO01-02, BR70-02, ZZ99-
47 | ERVFTP |  |  | ERV-CBL-40 (9ZT05AC47) | ERV SOV (RH ERV -LEFT) LBB50 AA705EL 58120: NEAR S10L | MSGCIC CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 155 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BR70-03, BO01-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BR21-03, BR20-03, BR19-03, BR18-02, BR17-02, IC52-02, IC51-02, IC50-02, IR07-02, IC06-R2, IC05-R2, IC04-R2, IC03-R2, IC02-R3, IC01-R3, CR01-R2, CC71-07, ZZ99-
48 | ERVFTP |  |  | ERV-CBL-41 (9ZT05AC48) | 220V DC PDB DC PDB | MSGCIC CONTROL (MS ERV -RIGHT) LBA25 AA704 PART OF MSGCIC CONTROL | 02C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 143 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | PEM SCOPE CABLE | LV11-L4, LV10-L4, LV44-03, LV76-04, LV79-03, LR10-R5, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-01, BR03-03, BR04-04, BR05-04, BR06-04, BR07-04, BR08-04, BR09-04, BR10-02, BR11-02, BR12-02, BR13-02, BR14-02, BO05-02, BR71-02, BP08-02, ZZ99-
49 | ERVFTP |  |  | ERV-CBL-42 (9ZT05AC49) | MSGCIC CONTROL (RH ERV-RIGHT) LBB50 AA706PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -RIGHT) LBA25 AA704 EL 56850: NEAR S4R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP07-02, BR69-02, BO07-02, ZZ99-
50 | ERVFTP |  |  | ERV-CBL-43 (9ZT05AC50) | MSGCIC CONTROL (RH ERV-RIGHT) LBB50 AA706PART OF MSGCIC CONTROL | ERV CONTROLLER (MS ERV -RIGHT) LBA25 AA704 EL 56850: NEAR S4R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 30 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BP07-02, BR69-02, BO07-02, ZZ99-
51 | ERVFTP |  |  | ERV-CBL-44 (9ZT05AC51) | ERV CONTROLLER (RH ERV-RIGHT) LBB50 AA706EL 56850: NEAR S4R | ERV SOV (MS ERV -RIGHT) LBA25 AA704 EL 58120: NEAR S4R | 03C X 2.5 PVC-Cu FRLS ( 1.1 kV ) | 21 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BO07-02, BR69-02, ZZ99-
52 | ERVFTP |  |  | ERV-CBL-45 (9ZT05AC52) | ERV SOV (RH ERV -RIGHT) LBB50 AA706EL 58120: NEAR S4R | MSGCIC CONTROL EQUIPMENT ROOM (CER) | 02P X 0.5 Paired Screened(O) ( 0.6 kV ) | 132 | [5 empty] | MSGCIC INTERCONNECTION DIAGRAM FOR ERV & FTP | TRICHY SCOPE CABLE | ZZ99- , BR69-03, BR71-03, BO05-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R3, IC01-R3, CR01-R2, CC71-06, ZZ99-
1 | EWLI |  |  | EWLI-CBL-1 (9ZT02AC01) | PRESSURE VESSEL (16 PORT) PROBE EL 56850 ; NEAR S9L | ASCERTOR CABINET (LEFT) INDICATION SYSTEM EL 56850 ; NEAR S9L | 10P X 0.5 Paired Screened ( 0.6 kV ) | 12 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR30-03, ZZ99-
2 | EWLI |  |  | EWLI-CBL-2 (9ZT02AC02) | PRESSURE VESSEL (16 PORT) PROBE EL 56850 ; NEAR S9L | ASCERTOR CABINET (LEFT) INDICATION SYSTEM EL 56850 ; NEAR S9L | 10P X 0.5 Paired Screened ( 0.6 kV ) | 12 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR30-03, ZZ99-
3 | EWLI |  |  | EWLI-CBL-3 (9ZT02AC03) | ASCERTOR CABINET EL 56850 ; NEAR S9L | UCB DISPLAY (LEFT) CONTROL ROOM | 16P X 0.5 Paired Screened ( 0.6 kV ) | 143 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR30-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R3, IC01-R3, LR10-L5, LV79-05, LR05-04, CC92-04, ZZ99-
4 | EWLI |  |  | EWLI-CBL-4 (9ZT02AC04) | ASCERTOR CABINET EL 56850 ; NEAR S9L | OP. FLOOR DISPLAY (LEFT) EL 26300 ; NEAR S19 | 16P X 0.5 Paired Screened ( 0.6 kV ) | 84 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR30-03, BR29-03, BR28-03, BR27-03, BR26-03, BR25-03, BR24-05, BR23-05, BR22-05, BG01-01, BG02-01, BG03-01, BR48-03, BF01-03, ZZ99-
5 | EWLI |  |  | EWLI-CBL-5 (9ZT02AC05) | PRESSURE VESSEL (16 PORT) PROBE EL 56850 ; NEAR S9R | ASCERTOR CABINET (RIGHT) INDICATION SYSTEM EL 56850 ; NEAR S9R | 10P X 0.5 Paired Screened ( 0.6 kV ) | 12 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR15-03, ZZ99-
6 | EWLI |  |  | EWLI-CBL-6 (9ZT02AC06) | PRESSURE VESSEL (16 PORT) PROBE EL 56850 ; NEAR S9R | ASCERTOR CABINET (RIGHT) INDICATION SYSTEM EL 56850 ; NEAR S9R | 10P X 0.5 Paired Screened ( 0.6 kV ) | 12 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR15-03, ZZ99-
7 | EWLI |  |  | EWLI-CBL-7 (9ZT02AC07) | ASCERTOR CABINET EL 56850 ; NEAR S9R | UCB DISPLAY (RIGHT) CONTROL ROOM | 16P X 0.5 Paired Screened ( 0.6 kV ) | 120 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR15-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BR06-05, BR05-05, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R3, IC01-R3, LR10-L5, LV77-05, LR06-04, CC91-02, ZZ99-
8 | EWLI |  |  | EWLI-CBL-8 (9ZT02AC08) | ASCERTOR CABINET EL 56850 ; NEAR S9R | OP. FLOOR DISPLAY (RIGHT) EL 26300 ; NEAR S19 | 16P X 0.5 Paired Screened ( 0.6 kV ) | 107 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR15-03, BR14-03, BR13-03, BR12-03, BR11-03, BR10-03, BR09-05, BR08-05, BR07-05, BG23-03, BG24-03, BG22-03, BG01-01, BG02-01, BG03-01, BR48-03, BF01-03, ZZ99-
9 | EWLI |  |  | EWLI-CBL-9 (9ZT02AC09) | PRESSURE VESSEL (8 PORT) PROBE EL 56850 ; NEAR S9L | ASCERTOR CABINET (LEFT) VALIDATION SYSTEM EL 56850 ; NEAR S9L | 10P X 0.5 Paired Screened ( 0.6 kV ) | 12 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR30-03, ZZ99-
10 | EWLI |  |  | EWLI-CBL-10 (9ZT02AC10) | PRESSURE VESSEL (8 PORT) PROBE EL 56850 ; NEAR S9R | ASCERTOR CABINET (RIGHT) VALIDATION SYSTEM EL 56850 ; NEAR S9R | 10P X 0.5 Paired Screened ( 0.6 kV ) | 12 | [5 empty] | EXTERNAL CONNECTION FOR EWLI (BV 20M) INDICATION VESSEL | TRICHY SCOPE CABLE | BR15-03, ZZ99-
1 | SADC |  |  | SA-CBL-1 (9ZT08AC01) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIE-1 EL 56850 ; NEAR S10R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 140 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-04, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, ZZ99-
2 | SADC |  |  | SA-CBL-LIE-1 (9ZT08AC02) | SADC-LIE-1 EL 56850 ; NEAR S10R | DPT-1, HBK20CP003 EL 57820 ; NEAR S10R | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 16 | [6 empty] | TRICHY SCOPE CABLE | BO06-03, BR71-03, ZZ99-
3 | SADC |  |  | SA-CBL-2 (9ZT08AC03) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIE-2 EL 56850 ; NEAR S10R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 140 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-04, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BR05-05, BR06-05, BR07-05, BR08-05, BR09-05, BR10-03, BR11-03, BR12-03, BR13-03, BR14-03, BO05-03, BO06-03, ZZ99-
4 | SADC |  |  | SA-CBL-LIE-2 (9ZT08AC04) | SADC-LIE-2 EL 56850 ; NEAR S10R | DPT-2, HBK20CP003 EL 57820 ; NEAR S10R | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 16 | [6 empty] | TRICHY SCOPE CABLE | BO06-03, BR71-03, ZZ99-
5 | SADC |  |  | SA-CBL-3-1-1 (9ZT08AC05) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-01 EL 23300 ; NEAR S2R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 106 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-04, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BE05-03, ZZ99-
6 | SADC |  |  | SA-CBL-3-1-2 (9ZT08AC06) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-01 EL 23300 ; NEAR S2R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 106 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-02, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BE05-03, ZZ99-
7 | SADC |  |  | SA-CBL-3-1-3 (9ZT08AC07) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-01 EL 23300 ; NEAR S2R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 103 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-02, CC69-02, CC70-02, CC51-04, CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BE05-03, ZZ99-
8 | SADC |  |  | SA-CBL-3-2-1 (9ZT08AC08) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-01 EL 23300 ; NEAR S2R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 103 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC68-02, CC69-02, CC70-02, CC51-04, CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BE05-03, ZZ99-
9 | SADC |  |  | SA-CBL-3-2-2 (9ZT08AC09) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-01 EL 23300 ; NEAR S2R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 103 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC68-02, CC69-02, CC70-02, CC51-04, CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BE05-03, ZZ99-
10 | SADC |  |  | SA-CBL-3-2-3 (9ZT08AC10) | CJF53 CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-01 EL 23300 ; NEAR S2R | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 103 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC68-02, CC69-02, CC70-02, CC51-04, CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BE05-03, ZZ99-
11 | SADC |  |  | SA-CBL-LIR-1-1 (9ZT08AC11) | SADC-JB-2 EL 23300 ; NEAR S2R | I/P CONVERTER, EL A EL 21083 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 38 | [6 empty] | TRICHY SCOPE CABLE | BE05-03, BR04-05, BD13-03, BD14-03, BD15-03, ZZ99-
12 | SADC |  |  | SA-CBL-LIR-1-2 (9ZT08AC12) | SADC-JB-2EL 23300 ; NEAR S2R | I/P CONVERTER, EL AB EL 21783 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 38 | [6 empty] | TRICHY SCOPE CABLE | BE05-03, BR04-05, BD13-03, BD14-03, BD15-03, ZZ99-
13 | SADC |  |  | SA-CBL-LIR-1-3 (9ZT08AC13) | SADC-JB-2EL 23300 ; NEAR S2R | I/P CONVERTER, EL B EL 22503 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 38 | [6 empty] | TRICHY SCOPE CABLE | BE05-03, BR04-05, BD13-03, BD14-03, BD15-03, ZZ99-
14 | SADC |  |  | SA-CBL-LIR-1-4 (9ZT08AC14) | SADC-JB-2EL 23300 ; NEAR S2R | I/P CONVERTER, EL BC EL 23300 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 28 | [6 empty] | TRICHY SCOPE CABLE | BE05-03, BR05-05, ZZ99-
15 | SADC |  |  | SA-CBL-LIR-1-5 (9ZT08AC15) | SADC-JB-2EL 23300 ; NEAR S2R | I/P CONVERTER, EL C EL 23923 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 28 | [6 empty] | TRICHY SCOPE CABLE | BE05-03, BR05-05, ZZ99-
16 | SADC |  |  | SA-CBL-LIR-1-6 (9ZT08AC16) | SADC-JB-2EL 23300 ; NEAR S2R | I/P CONVERTER, EL CD EL 24623 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 28 | [6 empty] | TRICHY SCOPE CABLE | BE05-03, BR05-05, ZZ99-
17 | SADC |  |  | SA-CBL-4-1-1 (9ZT08AC17) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-02 EL 26300 ; NEAR S3L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 151 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC68-02, CC69-04, CC70-02, CC51-04, CC71-07, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, BE01-03, BE02-03, BE03-03, BE04-03, BR46-03, BF01-03, ZZ99-
18 | SADC |  |  | SA-CBL-4-1-2 (9ZT08AC18) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-02 EL 26300 ; NEAR S3L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 154 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC68-04, CC69-04, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, BE01-03, BE02-03, BE03-03, BE04-03, BR46-03, BF01-03, ZZ99-
19 | SADC |  |  | SA-CBL-4-1-3 (9ZT08AC19) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-02 EL 26300 ; NEAR S3L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 154 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-04, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, BE01-03, BE02-03, BE03-03, BE04-03, BR46-03, BF01-03, ZZ99-
20 | SADC |  |  | SA-CBL-4-2-1 (9ZT08AC20) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-02 EL 26300 ; NEAR S3L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 154 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-04, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-02, IC50-02, IC51-02, IC52-02, BR17-02, BR18-02, BR19-03, BE01-03, BE02-03, BE03-03, BE04-03, BR46-03, BF01-03, ZZ99-
21 | SADC |  |  | SA-CBL-4-2-2 (9ZT08AC21) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-02 EL 26300 ; NEAR S3L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 154 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-04, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-02, BR18-02, BR19-03, BE01-03, BE02-03, BE03-03, BE04-03, BR46-03, BF01-03, ZZ99-
22 | SADC |  |  | SA-CBL-4-2-3 (9ZT08AC22) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-02 EL 26300 ; NEAR S3L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 154 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-04, CC69-02, CC70-02, CC51-04, CC71-06, CR01-R2, IC01-R3, IC02-R3, IC03-R2, IC04-R2, IC05-R2, IC06-R2, IR07-04, IC50-04, IC51-04, IC52-04, BR17-02, BR18-02, BR19-03, BE01-03, BE02-03, BE03-03, BE04-03, BR46-03, BF01-03, ZZ99-
23 | SADC |  |  | SA-CBL-LIR-2-1 (9ZT08AC23) | SADC-JB-3EL 26300 ; NEAR S3L | I/P CONVERTER, EL D EL 25343 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 81 | [6 empty] | TRICHY SCOPE CABLE | BF01-03, BR48-03, BG03-01, BG02-01, BG01-01, BG22-03, BG24-03, BG23-03, BR06-05, BR05-05, ZZ99-
24 | SADC |  |  | SA-CBL-LIR-2-2 (9ZT08AC24) | SADC-JB-3EL 26300 ; NEAR S3L | I/P CONVERTER, EL DE EL 26300 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 52 | [6 empty] | TRICHY SCOPE CABLE | BF01-03, BR46-03, BE04-03, BE03-03, BE02-03, BE01-03, BR20-03, ZZ99-
25 | SADC |  |  | SA-CBL-LIR-2-3 (9ZT08AC25) | SADC-JB-3EL 26300 ; NEAR S3L | I/P CONVERTER, EL E EL 26763 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 52 | [6 empty] | TRICHY SCOPE CABLE | BF01-03, BR46-03, BE04-03, BE03-03, BE02-03, BE01-03, BR20-03, ZZ99-
26 | SADC |  |  | SA-CBL-LIR-2-4 (9ZT08AC26) | SADC-JB-3EL 26300 ; NEAR S3L | I/P CONVERTER, EL EF EL 27463 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 55 | [6 empty] | TRICHY SCOPE CABLE | BF01-03, BR48-03, BG03-01, BG02-01, BG01-01, BR21-03, ZZ99-
27 | SADC |  |  | SA-CBL-LIR-2-5 (9ZT08AC27) | SADC-JB-3EL 26300 ; NEAR S3L | I/P CONVERTER, EL F EL 28183 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 55 | [6 empty] | TRICHY SCOPE CABLE | BF01-03, BR48-03, BG03-01, BG02-01, BG01-01, BR21-03, ZZ99-
28 | SADC |  |  | SA-CBL-LIR-2-6 (9ZT08AC28) | SADC-JB-3EL 26300 ; NEAR S3L | I/P CONVERTER, EL FF EL 28700 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 55 | [6 empty] | TRICHY SCOPE CABLE | BF01-03, BR48-03, BG03-01, BG02-01, BG01-01, BR21-03, ZZ99-
29 | SADC |  |  | SA-CBL-5-1 (9ZT08AC29) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-03 EL 34000 ; NEAR S12L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 155 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-02, CC68-02, CC69-02, CC70-02, CC51-04, CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BR05-05, BR06-05, BG23-03, BG24-03, BG22-03, BG01-01, BG02-01, BG03-01, BR49-03, BH02-01, ZZ99-
30 | SADC |  |  | SA-CBL-5-2 (9ZT08AC30) | CJF53CONTROL EQUIPMENT ROOM (CER) | SADC-LIR-03 EL 34000 ; NEAR S12L | 04P X 0.5 Paired Screened(I) ( 0.6 kV ) | 155 | [6 empty] | TRICHY SCOPE CABLE | CC11-03, CC63-04, CC64-04, CC65-04, CC66-02, CC67-04, CC68-02, CC69-02, CC70-02, CC51-04, CC71-07, CR01-R2, IC01-R3, IC02-R3, IR06-04, IC46-04, IC47-04, BR02-02, BR03-04, BR04-05, BR05-05, BR06-05, BG23-03, BG24-03, BG22-03, BG01-01, BG02-01, BG03-01, BR49-03, BH02-01, ZZ99-
31 | SADC |  |  | SA-CBL-JB-3-1 (9ZT08AC31) | SADC-JB-2EL 34000 ; NEAR S12L | I/P CONVERTER, EL UPPER OFA EL 29500 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 57 | [6 empty] | TRICHY SCOPE CABLE | BH02-01, BR49-03, BG03-01, BG02-01, BG01-01, BR21-03, ZZ99-
32 | SADC |  |  | SA-CBL-JB-3-2 (9ZT08AC32) | SADC-JB-2EL 34000 ; NEAR S12L | I/P CONVERTER, EL LOWER OFA EL 29100 ; NEAR S17 | 02P X 0.5 Paired Screened(I) ( 0.6 kV ) | 57 | [6 empty] | TRICHY SCOPE CABLE | BH02-01, BR49-03, BG03-01, BG02-01, BG01-01, BR21-03, ZZ99-
1 | SOLV |  |  | CTE01-SV-D001 (9ZI02AC01) | CTE01, EER, 15.5 Mtr | 1HLD01AA201, S25, EL:26300 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 198 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-03, LV79-03, LR10-R3, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BR19-04, BE01-02, BE02-02, BE03-02, BE04-02, BR46-02, BF01-02, ZZ99-
2 | SOLV |  |  | CTE01-SV-D002 (9ZI02AC02) | CTE01, EER, 15.5 Mtr | 1HLD02AA201, S25 @ EL26300 | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 159 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC70-03, CC51-02, CC71-03, CR01-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BR04-04, BE05-02, BE06-02, BE07-02, BR45-02, BF02-02, ZZ99-
3 | SOLV |  |  | CTE01-SV-D003 (9ZI02AC03) | CTE01, EER, 15.5 Mtr | 1LAE40AA001, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC70-03, CC51-02, CC71-03, CR01-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99-
4 | SOLV |  |  | CTE01-SV-D004 (9ZI02AC04) | CTE01, EER, 15.5 Mtr | 1LAE40AA002, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC70-03, CC51-02, CC71-03, CR01-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99-
5 | SOLV |  |  | CTE01-SV-D005 (9ZI02AC05) | CTE01, EER, 15.5 Mtr | 1LAE40AA003, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC70-03, CC51-02, CC71-03, CR01-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99-
6 | SOLV |  |  | CTE01-SV-D006 (9ZI02AC06) | CTE01, EER, 15.5 Mtr | 1LAE40AA004, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 109 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC70-03, CC51-02, CC71-03, CR01-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, BD14-02, BD15-02, BD16-02, ZZ99-
7 | SOLV |  |  | CTE01-SV-D007 (9ZI02AC07) | CTE01, EER, 15.5 Mtr | 1LAE40AA503, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 91 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC52-02, CC71-03, CR01-L4, IC01-L5, IC02-L5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, ZZ99-
8 | SOLV |  |  | CTE01-SV-D008 (9ZI02AC08) | CTE01, EER, 15.5 Mtr | 1LAE30AA001, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 90 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC52-02, CC71-03, CR01-R3, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, ZZ99-
9 | SOLV |  |  | CTE01-SV-D009 (9ZI02AC09) | CTE01, EER, 15.5 Mtr | 1LAE30AA002, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 90 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC52-02, CC71-03, CR01-R3, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, ZZ99-
10 | SOLV |  |  | CTE01-SV-D010 (9ZI02AC10) | CTE01, EER, 15.5 Mtr | 1LAE30AA003, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 89 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC52-02, CC71-02, CR01-R3, IC01-R5, IC02-R5, IR06-02, IC46-02, IC47-02, BR02-03, BR03-03, BD13-02, ZZ99-
11 | SOLV |  |  | CTE01-SV-D011 (9ZI02AC11) | CTE01, EER, 15.5 Mtr | 1LAE30AA004, El. 21.0 m @Boiler Front-L | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 132 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-03, LV79-03, LR10-R3, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BD17-02, ZZ99-
12 | SOLV |  |  | CTE01-SV-D012 (9ZI02AC12) | CTE01, EER, 15.5 Mtr | 1LAE30AA503, El. 21.0 m @Boiler Front | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 132 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-03, LV79-03, LR10-R3, IC01-R5, IC02-R5, IC03-R3, IC04-R3, IC05-R3, IC06-R3, IR07-03, IC50-03, IC51-03, IC52-03, BR17-03, BR18-03, BD17-02, ZZ99-
13 | SOLV |  |  | CTE01-SV-D013 (9ZI02AC13) | CTE01, EER, 15.5 Mtr | 1LAC10AA201, El : 0.600 mtr, Near B Row | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 160 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
14 | SOLV |  |  | CTE01-SV-D014 (9ZI02AC14) | CTE01, EER, 15.5 Mtr | 1LCB11AA301, Near CEP-A | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, TG08-R2, TG07-03, ZZ99-
15 | SOLV |  |  | CTE01-SV-D015 (9ZI02AC15) | CTE01, EER, 15.5 Mtr | 1LAC20AA201, El : 600 mtr, Near B Row | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 140 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, ZZ99-
16 | SOLV |  |  | CTE01-SV-D016 (9ZI02AC16) | CTE01, EER, 15.5 Mtr | 1LCB12AA301, Near CEP-B | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 173 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, TG08-R2, TG07-03, ZZ99-
17 | SOLV |  |  | CTE01-SV-D017 (9ZI02AC17) | CTE01, EER, 15.5 Mtr | 1LAC30AA201, El : 0.600 mtr, Near B Row | 03C X 2.5 XLPE-Cu FRLS ( 1.1 kV ) | 160 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , CC45-02, CC44-02, CC87-02, CC88-03, CC92-02, LR05-02, MR10-03, MA05-03, MV68-05, MV10-02, MV11-02, MV86-02, MR18-03, MA04-02, TG21-02, TG20-02, TG89-02, TG88-02, TG16-L3, TG15-R2, TG14-R2, TG13-R2, TG12-R2, TG11-R2, TG10-R2, TG09-R2, ZZ99-
18 | SOLV |  |  | CVP03-SV-C001 (9ZI02AC18) | 1HLD01AA201, S25, EL:26300 | CVP03, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 190 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BF01-03, BR46-03, BE04-03, BE03-03, BE02-03, BE01-03, BR19-05, BR18-04, BR17-04, IC52-04, IC51-04, IC50-04, IR07-04, IC06-R4, IC05-R4, IC04-R4, IC03-R4, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
19 | SOLV |  |  | CVP04-SV-C001 (9ZI02AC19) | 1HLD02AA201, S25 @ EL26300 | CVP04, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 164 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BF02-03, BR45-03, BE07-03, BE06-03, BE05-03, BR04-05, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC43-04, CC42-04, CC34-03, CC67-04, CC30-03, ZZ99-
20 | SOLV |  |  | CVP10-SV-C001 (9ZI02AC20) | 1LAE40AA001, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 105 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD16-03, BD15-03, BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
21 | SOLV |  |  | CVP10-SV-C002 (9ZI02AC21) | 1LAE40AA002, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 105 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD16-03, BD15-03, BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
22 | SOLV |  |  | CVP10-SV-C003 (9ZI02AC22) | 1LAE40AA003, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 105 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD16-03, BD15-03, BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
23 | SOLV |  |  | CVP10-SV-C004 (9ZI02AC23) | 1LAE40AA004, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 105 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD16-03, BD15-03, BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
24 | SOLV |  |  | CVP10-SV-C005 (9ZI02AC24) | 1LAE40AA503, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 90 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
25 | SOLV |  |  | CVP10-SV-C006 (9ZI02AC25) | 1LAE30AA001, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 90 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
26 | SOLV |  |  | CVP10-SV-C007 (9ZI02AC26) | 1LAE30AA002, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 90 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
27 | SOLV |  |  | CVP10-SV-C008 (9ZI02AC27) | 1LAE30AA003, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 90 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
28 | SOLV |  |  | CVP10-SV-C009 (9ZI02AC28) | 1LAE30AA004, El. 21.0 m @Boiler Front-L | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 112 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD17-03, BD16-03, BD15-03, BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
29 | SOLV |  |  | CVP10-SV-C010 (9ZI02AC29) | 1LAE30AA503, El. 21.0 m @Boiler Front | CVP10, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 112 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , BD17-03, BD16-03, BD15-03, BD14-03, BD13-03, BR03-04, BR02-04, IC47-04, IC46-04, IR06-04, IC02-R6, IC01-R6, CR01-R4, CC71-06, CC52-04, CC44-03, CC45-03, ZZ99-
30 | SOLV |  |  | CVP11-SV-C001 (9ZI02AC30) | 1LAC10AA201, El : 0.600 mtr, Near B Row | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 139 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
31 | SOLV |  |  | CVP11-SV-C002 (9ZI02AC31) | 1LCB11AA301, Near CEP-A | CVP11, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , TG07-04, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
32 | SOLV |  |  | CVP12-SV-C001 (9ZI02AC32) | 1LAC20AA201, El : 600 mtr, Near B Row | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 119 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
33 | SOLV |  |  | CVP12-SV-C002 (9ZI02AC33) | 1LCB12AA301, Near CEP-B | CVP12, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 151 | [5 empty] | CONTROL & MONITORING |  | ZZ99- , TG07-04, TG08-R3, TG09-R3, TG10-R3, TG11-R3, TG12-R3, TG13-R3, TG14-R3, TG15-R3, TG17-R3, TG87-03, TR01-03, MR14-03, TR49-03, LV54-03, LV06-R4, LV07-R4, LV76-04, LR05-04, CC92-04, CC88-04, CC86-04, CC85-03, CC41-03, ZZ99-
34 | SOLV |  |  | CVP13-SV-C001 (9ZI02AC34) | 1LAC30AA201, El : 0.600 mtr, Near B Row | CVP13, EER, 15.5 Mtr | 04P X 0.5 Paired Screened(O) ( 225 V ) | 139 | [5 empty] | CONTROL & MONITORING |  | `

## Summery SheetCnI
[7 empty] | CABLE LENGTH RECONCILIATION | [5 empty] | CABLE RUN QUANTITY |  | UNIT WISE GLAND QUANTITY
CABLE CODE | PTX BOQ | CABLE SIZE DESCRIPTION | CABLE DIA | RATED AMPS | GLAND | QTY | SUPPLY | SCHEDULE LENGTH | PTX SCOPE | ACTUAL LENGTH | % COMPLETED | BALANCE STOCK % | TOTAL RUN CABLE | TOTAL RUN LAYED | EPD | PEM | BPL | JHS | RPT | HWR | HYD | TRY | EDN | ISG
D03J2.5 | 10.3.03 | 03Cx2.5Sqmm CU XLPE-FRLS ARM P CABLE | 14 mm | 24 A | CBW01S | 2 | 5987 | 0 | 8000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D01Q035 | 10.4.01 | 01Cx035Sqmm AL XLPE-FRLS UNARM CABLE | 13 mm | 114 A | CBW01S | 284 | 5962 | 3969 | 8000 | 2984 | 75.18% | 49.9497 | 142 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0
D02Q010 | 10.4.06 | 02Cx010Sqmm AL XLPE-FRLS UNARM CABLE | 16 mm | 59 A | CBW01 | 284 | 8876 | 8028 | 6000 | 1387 | 17.28% | 84.3736 | 142 | 24 | 160 | 91 | 13 | 3 | 0 | 0 | 0 | 0 | 17 | 0
D03Q010 | 10.4.11 | 03Cx010Sqmm AL XLPE-FRLS UNARM CABLE | 17 mm | 57 A | CBW01 | 328 | 25842 | 21030 | 36100 | 2490 | 11.84% | 90.3645 | 164 | 20 | 132 | 98 | 0 | 0 | 71 | 7 | 20 | 0 | 0 | 0
D03Q025 | 10.4.12 | 03Cx025Sqmm AL XLPE-FRLS UNARM CABLE | 20 mm | 94 A | CBW03 | 160 | 16849 | 15121 | 14000 | 585 | 3.869% | 96.528 | 80 | 9 | 80 | 55 | 0 | 0 | 10 | 2 | 13 | 0 | 0 | 0
D03Q035 | 10.4.13 | 03Cx035Sqmm AL XLPE-FRLS UNARM CABLE | 22 mm | 113 A | CBW03 | 16 | 794 | 520 | 800 | 0 | 0% | 100 | 8 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0
D03Q050 | 10.4.14 | 03Cx050Sqmm AL XLPE-FRLS UNARM CABLE | 25 mm | 133 A | CBW05 | 140 | 2974 | 3260 | 2000 | 204 | 6.258% | 93.1406 | 70 | 4 | 19 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0
D03Q095 | 10.4.15 | 03Cx095Sqmm AL XLPE-FRLS UNARM CABLE | 34 mm | 190 A | CBW07 | 66 | 5897 | 3283 | 8000 | 307 | 9.351% | 94.794 | 33 | 3 | 31 | 30 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 2
D03Q150 | 10.4.16 | 03Cx150Sqmm AL XLPE-FRLS UNARM CABLE | 39 mm | 249 A | CBW08 | 8 | 1468 | 1032 | 750 | 0 | 0% | 100 | 4 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03Q240 | 10.4.17 | 03Cx240Sqmm AL XLPE-FRLS UNARM CABLE | 49 mm | 326 A | CBW010 | 68 | 8121 | 5868 | 6750 | 128 | 2.181% | 98.4238 | 34 | 2 | 38 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D02L1.5 | 10.4.23 | 02Cx1.5Sqmm CU XLPE-FRLS UNARM CABLE | 12 mm | 13 A | CBW01SS | 2 | 0 | 0 | 140 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D02L2.5 | 10.4.24 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM CABLE | 14 mm | 25 A | CBW01S | 784 | 55130 | 24220 | 68500 | 1710 | 7.06% | 96.8982 | 392 | 20 | 191 | 81 | 81 | 47 | 343 | 6 | 0 | 6 | 24 | 2
D03L1.5 | 10.4.25 | 03Cx1.5Sqmm CU XLPE-FRLS UNARM CABLE | 12 mm | 13 A | CBW01SS | 2 | 0 | 0 | 9200 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03L2.5 | 10.4.26 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM CABLE | 14 mm | 24 A | CBW01S | 1380 | 71192 | 78238 | 95300 | 2501 | 3.197% | 96.487 | 690 | 27 | 528 | 390 | 24 | 0 | 4 | 18 | 99 | 310 | 3 | 2
D02W1.5 | 10.4.27 | 04Cx1.5Sqmm ATC TYPE-F UNARM R CABLE | 15 mm | 13 A | CBW01S | 58 | 5496 | 1400 | 5500 | 0 | 0% | 100 | 29 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0
D10L2.5 | 10.4.28 | 10Cx2.5Sqmm CU XLPE-FRLS UNARM CABLE | 17 mm | 18 A | CBW01 | 2 | 0 | 0 | 8200 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D02C1.5 | 10.5.01 | 02Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 13 mm | 20 A | CBW01S | 798 | 61485 | 55129 | 50000 | 2031 | 3.684% | 96.6968 | 399 | 22 | 658 | 3 | 94 | 2 | 0 | 1 | 0 | 0 | 22 | 4
D02C2.5 | 10.5.02 | 02Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 27 A | CBW01S | 2 | 1482 | 0 | 3000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03C1.5 | 10.5.03 | 03Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 13 mm | 17 A | CBW01S | 504 | 35493 | 6473 | 2500 | 0 | 0% | 100 | 252 | 0 | 0 | 0 | 6 | 56 | 408 | 0 | 0 | 0 | 34 | 0
D03C2.5 | 10.5.04 | 03Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 24 A | CBW01S | 136 | 43391 | 1620 | 18500 | 0 | 0% | 100 | 68 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 16 | 0 | 0
D03C16 | 10.5.05 | 03Cx16Sqmm CU PVC-FRLS UNARM CABLE | 19 mm | 24 A | CBW02 | 2 | 0 | 0 | 1500 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D05C1.5 | 10.5.06 | 05Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 13 mm | 10 A | CBW01S | 200 | 14908 | 18502 | 15000 | 1092 | 5.902% | 92.6751 | 100 | 15 | 47 | 3 | 94 | 26 | 0 | 0 | 0 | 0 | 20 | 4
D05C2.5 | 10.5.07 | 05Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 13 A | CBW01S | 160 | 12607 | 10585 | 7000 | 100 | 0.9447% | 99.2068 | 80 | 1 | 4 | 0 | 74 | 8 | 0 | 0 | 0 | 10 | 27 | 4
D07C1.5 | 10.5.08 | 07Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 14 mm | 10 A | CBW01S | 64 | 11973 | 4788 | 12000 | 0 | 0% | 100 | 32 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D07C2.5 | 10.5.09 | 07Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 16 mm | 13 A | CBW01S | 2 | 2000 | 104 | 1000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0
D10C1.5 | 10.5.10 | 10Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 17 mm | 10 A | CBW01 | 138 | 8070 | 2400 | 8200 | 318 | 13.25% | 96.0595 | 69 | 3 | 0 | 0 | 0 | 56 | 80 | 0 | 0 | 0 | 0 | 0
D10C2.5 | 10.5.11 | 10Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 19 mm | 13 A | CBW02 | 2 | 499 | 0 | 250 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D12C1.5 | 10.5.12 | 12Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 18 mm | 10 A | CBW02 | 12 | 14909 | 592 | 15000 | 0 | 0% | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0
D12C2.5 | 10.5.13 | 12Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 20 mm | 13 A | CBW02 | 2 | 4942 | 0 | 5000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D16C2.5 | 10.5.14 | 16Cx2.5Sqmm CU PVC-FRLS UNARM CABLE | 22 mm | 13 A | CBW03 | 2 | 7841 | 0 | 4000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D19C1.5 | 10.5.15 | 19Cx1.5Sqmm CU PVC-FRLS UNARM CABLE | 20 mm | 10 A | CBW03 | 4 | 4981 | 0 | 2000 | 0 | 0% | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E02V0.5 | 10.7.01 | 02Px0.5Sqmm ATC TYPE-G UNAR CABLE | 8 mm | 5 A | CBW01SS | 2 | 16297 | 0 | 1000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E04V0.5 | 10.7.02 | 04Px0.5Sqmm ATC TYPE-G UNAR CABLE | 12 mm | 5 A | CBW01SS | 1054 | 171965 | 46324 | 5000 | 14465 | 31.23% | 91.5884 | 527 | 200 | 194 | 9 | 160 | 16 | 0 | 9 | 0 | 81 | 501 | 6
E06V0.5 | 10.7.03 | 06Px0.5Sqmm ATC TYPE-G UNAR CABLE | 13 mm | 6 A | CBW01SS | 2 | 0 | 0 | 10000 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E08V0.5 | 10.7.04 | 08Px0.5Sqmm ATC TYPE-G UNAR CABLE | 15 mm | 7 A | CBW01S | 18 | 45535 | 1034 | 1000 | 0 | 0% | 100 | 9 | 0 | 0 | 1 | 4 | 2 | 0 | 0 | 0 | 0 | 11 | 0
E12V0.5 | 10.7.05 | 12Px0.5Sqmm ATC TYPE-G UNAR CABLE | 19 mm | 8 A | CBW02 | 2 | 17958 | 0 | 15000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E16V0.5 | 10.7.06 | 16Px0.5Sqmm ATC TYPE-G UNAR CABLE | 20 mm | 9 A | CBW02 | 2 | 0 | 0 | 10000 | 0 | 0% | 99.99 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E02W0.5 | 10.8.01 | 02Px0.5Sqmm ATC TYPE-F UNAR CABLE | 8 mm | 5 A | CBW01SS | 68 | 64768 | 2500 | 6000 | 1003 | 40.12% | 98.4514 | 34 | 16 | 11 | 0 | 16 | 0 | 0 | 3 | 0 | 4 | 34 | 0
E04W0.5 | 10.8.02 | 04Px0.5Sqmm ATC TYPE-F UNAR CABLE | 12 mm | 5 A | CBW01SS | 86 | 110242 | 4702 | 14000 | 0 | 0% | 100 | 43 | 0 | 2 | 2 | 8 | 16 | 0 | 2 | 0 | 8 | 48 | 0
E08W0.5 | 10.8.03 | 08Px0.5Sqmm ATC TYPE-F UNAR CABLE | 15 mm | 5 A | CBW01S | 4 | 40983 | 56 | 10000 | 0 | 0% | 100 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
E12W0.5 | 10.8.04 | 12Px0.5Sqmm ATC TYPE-F UNAR CABLE | 19 mm | 5 A | CBW02 | 2 | 22855 | 0 | 5000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F04-0.5 | 10.9.01 | OFC CABLE WITHOUT HDPE PIPE | 12 mm | 0 A | CBW01SS | 2 | 8674 | 0 | 8000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F12-0.5 | 10.9.02 | OFC CABLE WITH HDPE PIPE | 12 mm | 0 A | CBW01SS | 2 | 41206 | 0 | 3000 | 0 | 0% | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D04C2.5 | NA | 04Cx2.5Sqmm CU PVC-FRLS EDN UA CABLE | 17 mm | 18 A | CBW01 | 0 | 2994 | 0 | 0 | 0 | 0% | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D03J1.5 | NA | 03Cx1.5Sqmm CU XLPE-FRLS ARM FIRE CABLE | 13 mm | 17 A | CBW01S | 0 | 85473 | 0 | 0 | 0 | 0% | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D01C050 | NA | 01Cx050Sqmm CU XLPE-FRLS UNARM CABLE | 18 mm | 150 A | CBW02 | 4 | 400 | 140 | 0 | 0 | 0% | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
[6 empty] | 6860 |  | 320918 |  | 31305 | 9.755% |  | 3430 | 452
|  |  | GLAND SELECTION |  |  | TOTAL | GLAND QUANTITY | bar: UNIT WISE GLAND QUANTITY EPD
|  |  | MIN-OD | MAX-OD | TYPE | QTY | EPD | PEM | BPL | JHS | RPT | EDN | HWR | TRY | UNIT WISE GLAND QUANTITY EPD: ISG
|  |  | 8 | 13 | CBW01SS | 1220 | 207 | 11 | 184 | 32 | 0 | 583 | 14 | 93 | UNIT WISE GLAND QUANTITY EPD: 6
|  |  | 13.5 | 16 | CBW01S | 4396 | 1494 | 478 | 377 | 197 | 875 | 428 | 26 | 342 | UNIT WISE GLAND QUANTITY EPD: 16
|  |  | 16.5 | 18 | CBW01 | 752 | 292 | 189 | 13 | 59 | 151 | 17 | 7 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 18.5 | 20 | CBW02 | 28 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 20.5 | 23 | CBW03 | 182 | 80 | 55 | 0 | 0 | 26 | 0 | 2 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 23.5 | 26 | CBW04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 26.5 | 30 | CBW05 | 140 | 19 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 30.5 | 33 | CBW06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 33.5 | 37 | CBW07 | 66 | 31 | 30 | 0 | 0 | 2 | 0 | 1 | 0 | UNIT WISE GLAND QUANTITY EPD: 2
|  |  | 37.5 | 41 | CBW08 | 8 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 41.5 | 46 | CBW09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 46.5 | 52 | CBW010 | 68 | 38 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 52.5 | 56 | CBW011S | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 56.5 | 60 | CBW011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 60.5 | 66 | CBW012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 66.5 | 72 | CBW013A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 72.5 | 78 | CBW013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 78.5 | 84 | CBW014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 84.5 | 92 | CBW015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
|  |  | 92.5 | 104 | CBW016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNIT WISE GLAND QUANTITY EPD: 0
[5 empty] | TOTAL | 6860

## Cable Stock
SL NO | DRUM NO | QTY |  | DBR | DBR DT | CABLE | CORE | CU/AL | TYPE | A/UA | VOLT | APPLICATION | CABLE CODE | DESCRIPTION | LOCATION | LR NO. | LR DATE | VEHICLE NO. | SU VENDOR | INVOICE NO. | INVOICE DATE | PO REF | PO DT.
|  | MTR |  | NO |  | SIZE | SIZE |  |  |  | GR |  | CODE
1 | DR0345_1533 | 1005 | 1150 | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
2 | DR0345_1534 | 1001 |  | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
3 | DR0345_1535 | 991 |  | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
4 | DR0345_1536 | 1009 |  | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
5 | DR0345_1537 | 1014 |  | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
6 | DR0345_1538 | 1000 |  | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
7 | DR0345_1539 | 987 |  | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
8 | DR0345_1540 | 1001 |  | 345 | 2017-12-06 | 02C | 120 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02G120 | 02Cx120Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
9 | DR0345_1541 | 1023 |  | 345 | 2017-12-06 | 03C | 10 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03Q010 | 03Cx010Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
10 | DR0345_1542 | 1040 |  | 345 | 2017-12-06 | 03C | 10 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03Q010 | 03Cx010Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
11 | DR0345_1543 | 1010 |  | 345 | 2017-12-06 | 03C | 10 | AL | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03Q010 | 03Cx010Sqmm AL PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
12 | DR0345_1545 | 794 |  | 345 | 2017-12-06 | 03C | 35 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03Q035 | 03Cx035Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
13 | DR0345_1546 | 992 |  | 345 | 2017-12-06 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
14 | DR0345_1547 | 1002 |  | 345 | 2017-12-06 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
15 | DR0345_1548 | 1000 |  | 345 | 2017-12-06 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
16 | DR0345_1549 | 1008 |  | 345 | 2017-12-06 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
17 | DR0345_1550 | 995 |  | 345 | 2017-12-06 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
18 | DR0345_1551 | 304 |  | 345 | 2017-12-06 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
19 | DR0345_1552 | 1005 |  | 345 | 2017-12-06 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT LT POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
20 | DR0345_1553 | 1000 |  | 345 | 2017-12-06 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
21 | DR0345_1554 | 991 |  | 345 | 2017-12-06 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
22 | DR0345_1555 | 1003 |  | 345 | 2017-12-06 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
23 | DR0345_1556 | 998 |  | 345 | 2017-12-06 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
24 | DR0345_1557 | 510 |  | 345 | 2017-12-06 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | RPT LT POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM RPT LT POWER CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1169 | 29-05-2017 | RJ02GB 3242 | TPPL | 93 | 29-05-2017 | 4263079 | 21-01-2017
25 | DR0352_C-1334 | 1002 |  | 352 | 15-06-2017 | 02P | 1.5 | ATC | TYPE-F | UNARM | 1.1 KV | RPT INSTRUMENT | D02W1.5 | 02Px1.5Sqmm ATC TYPE-F UNARM RPT INSTRUMENT CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 6000418001 | 31-03-2017 | OR14D 2809 | ELKAY LTD | 565 | 31-03-2017 | 4263039 | 31-03-2017
26 | DR0352_C-1335 | 1003 |  | 352 | 15-06-2017 | 02P | 1.5 | ATC | TYPE-F | UNARM | 1.1 KV | RPT INSTRUMENT | D02W1.5 | 02Px1.5Sqmm ATC TYPE-F UNARM RPT INSTRUMENT CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 6000418001 | 31-03-2017 | OR14D 2809 | ELKAY LTD | 565 | 31-03-2017 | 4263039 | 31-03-2017
27 | DR0352_C-1336 | 995 |  | 352 | 15-06-2017 | 02P | 1.5 | ATC | TYPE-F | UNARM | 1.1 KV | RPT INSTRUMENT | D02W1.5 | 02Px1.5Sqmm ATC TYPE-F UNARM RPT INSTRUMENT CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 6000418001 | 31-03-2017 | OR14D 2809 | ELKAY LTD | 565 | 31-03-2017 | 4263039 | 31-03-2017
28 | DR0352_C-1337 | 1000 |  | 352 | 15-06-2017 | 02P | 1.5 | ATC | TYPE-F | UNARM | 1.1 KV | RPT INSTRUMENT | D02W1.5 | 02Px1.5Sqmm ATC TYPE-F UNARM RPT INSTRUMENT CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 6000418001 | 31-03-2017 | OR14D 2809 | ELKAY LTD | 565 | 31-03-2017 | 4263039 | 31-03-2017
29 | DR0352_C-1338 | 995 |  | 352 | 15-06-2017 | 02P | 1.5 | ATC | TYPE-F | UNARM | 1.1 KV | RPT INSTRUMENT | D02W1.5 | 02Px1.5Sqmm ATC TYPE-F UNARM RPT INSTRUMENT CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 6000418001 | 31-03-2017 | OR14D 2809 | ELKAY LTD | 565 | 31-03-2017 | 4263039 | 31-03-2017
30 | DR0352_C-1339 | 501 |  | 352 | 15-06-2017 | 02P | 1.5 | ATC | TYPE-F | UNARM | 1.1 KV | RPT INSTRUMENT | D02W1.5 | 02Px1.5Sqmm ATC TYPE-F UNARM RPT INSTRUMENT CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 6000418001 | 31-03-2017 | OR14D 2809 | ELKAY LTD | 565 | 31-03-2017 | 4263039 | 31-03-2017
31 | DR0400_1558 | 1006 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
32 | DR0400_1559 | 1021 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
33 | DR0400_1560 | 1015 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
34 | DR0400_1561 | 1015 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
35 | DR0400_1562 | 994 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
36 | DR0400_1563 | 997 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
37 | DR0400_1564 | 1010 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
38 | DR0400_1565 | 1010 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
39 | DR0400_1566 | 996 |  | 400 | 2017-04-07 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
40 | DR0400_1567 | 1010 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
41 | DR0400_1568 | 1008 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
42 | DR0400_1569 | 1015 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
43 | DR0400_1570 | 1006 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
44 | DR0400_1571 | 1010 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
45 | DR0400_1572 | 1008 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
46 | DR0400_1573 | 1008 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
47 | DR0400_1574 | 1005 |  | 400 | 2017-04-07 | 10C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | RPT CONTROL | D10C1.5 | 10Cx1.5Sqmm CU PVC-FRLS UNARM RPT CONTROL CABLE | PAVEMENT -1 (NEAR NSPCL GATE-01) | 1176 | 27-06-2017 | OD05J 2035 | TPPL | 170 | 27-06-2017 | 4263624 | 20-03-2017
48 | DR0720_4794-12F-01 | 998 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
49 | DR0720_4794-12F-02 | 996 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
50 | DR0720_4794-12F-03 | 1000 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
51 | DR0720_4794-12F-04 | 1001 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
52 | DR0720_4794-12F-05 | 1000 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
53 | DR0720_4794-12F-06 | 998 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
54 | DR0720_4794-12F-07 | 981 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
55 | DR0720_4794-12F-08 | 999 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
56 | DR0720_4794-12F-09 | 999 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
57 | DR0720_4794-12F-10 | 995 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
58 | DR0720_4794-12F-11 | 1001 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
59 | DR0720_4794-12F-12 | 1000 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
60 | DR0720_4794-12F-13 | 996 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
61 | DR0720_4794-12F-14 | 1003 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
62 | DR0720_4794-12F-15 | 997 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
63 | DR0720_4794-12F-16 | 1003 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
64 | DR0720_4794-12F-17 | 991 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
65 | DR0720_4794-12F-18 | 997 |  | 720 | 2017-06-10 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29-09-2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29-09-2017 | P-88/17 | 14-06-2017
66 | DR0720_4798-4G-02 | 1020 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
67 | DR0720_4798-4G-03 | 1020 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
68 | DR0720_4798-4G-04 | 999 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
69 | DR0720_4798-4G-07 | 1025 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
70 | DR0720_4798-4G-09 | 1024 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
71 | DR0720_4798-4G-11 | 1022 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
72 | DR0720_4798-4G-15 | 1019 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
73 | DR0720_4798-4G-18 | 1022 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
74 | DR0720_4798-4G-19 | 1022 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
75 | DR0720_4798-4G-20 | 1013 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
76 | DR0720_4798-4G-21 | 1018 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
77 | DR0720_4798-4G-22 | 1020 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
78 | DR0720_4798-4G-25 | 1010 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
79 | DR0720_4798-4G-31 | 1023 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
80 | DR0720_4798-4G-32 | 1013 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
81 | DR0720_4798-4G-33 | 1018 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
82 | DR0720_4798-4G-35 | 1019 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
83 | DR0720_4798-4G-42 | 1015 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
84 | DR0720_4798-4G-43 | 1012 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
85 | DR0720_4798-4G-45 | 1009 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
86 | DR0720_4798-4G-49 | 1026 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
87 | DR0720_4798-4G-55 | 1016 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
88 | DR0720_4798-4G-56 | 1011 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
89 | DR0720_4798-4G-59 | 998 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
90 | DR0720_4798-4G-60 | 998 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
91 | DR0720_4798-4G-65 | 1012 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
92 | DR0720_4798-4G-66 | 1015 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
93 | DR0720_4798-4G-70 | 1008 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
94 | DR0720_4798-4G-75 | 1012 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
95 | DR0720_4798-4G-79 | 1005 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
96 | DR0720_4798-4G-81 | 1018 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
97 | DR0720_4798-4G-82 | 1008 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
98 | DR0720_4798-4G-83 | 1014 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
99 | DR0720_4798-4G-85 | 990 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
100 | DR0720_4798-4G-86 | 1017 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
101 | DR0720_4798-4G-89 | 1011 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
102 | DR0720_4798-4G-92 | 1018 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
103 | DR0720_4798-4G-94 | 1027 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
104 | DR0720_4798-4G-95 | 1021 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
105 | DR0720_4798-4G-96 | 1019 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
106 | DR0720_4798-4G-103 | 1019 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
107 | DR0720_4798-4G-106 | 1024 |  | 720 | 2017-06-10 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10110 | 29/09/2017 | HR63C 7927 | CMI LTD | CMI/4794/00691 | 29/09/2017 | P-88/17 | 14-06-2017
108 | DR0816_0002 | 999 |  | 816 | 13-10-2017 | 03C | 2.5 | CU | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D03J2.5 | 03Cx2.5Sqmm CU XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
109 | DR0816_0003 | 1012 |  | 816 | 13-10-2017 | 03C | 2.5 | CU | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D03J2.5 | 03Cx2.5Sqmm CU XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
110 | DR0816_0004 | 996 |  | 816 | 13-10-2017 | 03C | 2.5 | CU | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D03J2.5 | 03Cx2.5Sqmm CU XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
111 | DR0816_0005 | 993 |  | 816 | 13-10-2017 | 03C | 2.5 | CU | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D03J2.5 | 03Cx2.5Sqmm CU XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
112 | DR0816_0006 | 984 |  | 816 | 13-10-2017 | 03C | 2.5 | CU | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D03J2.5 | 03Cx2.5Sqmm CU XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
113 | DR0816_0001 | 978 |  | 816 | 13-10-2017 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
114 | DR0816_0002 | 984 |  | 816 | 13-10-2017 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
115 | DR0816_0003 | 984 |  | 816 | 13-10-2017 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
116 | DR0816_0004 | 958 |  | 816 | 13-10-2017 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
117 | DR0816_0001 | 995 |  | 816 | 13-10-2017 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
118 | DR0816_0002 | 981 |  | 816 | 13-10-2017 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
119 | DR0816_0003 | 984 |  | 816 | 13-10-2017 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
120 | DR0816_0004 | 986 |  | 816 | 13-10-2017 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
121 | DR0816_0006 | 990 |  | 816 | 13-10-2017 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
122 | DR0816_0001 | 997 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
123 | DR0816_0002 | 998 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
124 | DR0816_0003 | 1000 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
125 | DR0816_0004 | 1000 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
126 | DR0816_0005 | 994 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
127 | DR0816_0006 | 996 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
128 | DR0816_0007 | 1000 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
129 | DR0816_0008 | 1000 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
130 | DR0816_0009 | 995 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
131 | DR0816_0010 | 913 |  | 816 | 13-10-2017 | 01C | 70 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q070 | 01Cx070Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
132 | DR0816_0001 | 972 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
133 | DR0816_0002 | 1012 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
134 | DR0816_0003 | 990 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
135 | DR0816_0004 | 1006 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
136 | DR0816_0005 | 1002 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
137 | DR0816_0006 | 1002 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
138 | DR0816_0007 | 1000 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
139 | DR0816_0008 | 982 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
140 | DR0816_0009 | 999 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
141 | DR0816_0010 | 1005 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
142 | DR0816_0011 | 1002 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
143 | DR0816_0012 | 985 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
144 | DR0816_0013 | 967 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
145 | DR0816_0014 | 1000 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
146 | DR0816_0015 | 990 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
147 | DR0816_0016 | 990 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
148 | DR0816_0017 | 980 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
149 | DR0816_0022 | 990 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
150 | DR0816_0023 | 978 |  | 816 | 13-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
151 | DR0816_0008 | 993 |  | 816 | 13-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
152 | DR0816_0001 | 998 |  | 816 | 13-10-2017 | 01C | 35 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q035 | 01Cx035Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
153 | DR0816_0002 | 995 |  | 816 | 13-10-2017 | 01C | 35 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q035 | 01Cx035Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
154 | DR0816_0003 | 994 |  | 816 | 13-10-2017 | 01C | 35 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q035 | 01Cx035Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
155 | DR0816_0004 | 977 |  | 816 | 13-10-2017 | 01C | 35 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q035 | 01Cx035Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
156 | DR0816_0005 | 996 |  | 816 | 13-10-2017 | 01C | 35 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q035 | 01Cx035Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
157 | DR0816_0006 | 1002 |  | 816 | 13-10-2017 | 01C | 35 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q035 | 01Cx035Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439804 | 29-09-2017 | CG04J 9474 | SPECIAL CABLE PVT LTD | SCPL/R/G0170 | 29-09-2017 | P-81/17 | 2017-12-06
158 | DR0817_4798-4G-01 | 1000 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
159 | DR0817_4798-4G-05 | 1022 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
160 | DR0817_4798-4G-06 | 1023 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
161 | DR0817_4798-4G-08 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
162 | DR0817_4798-4G-10 | 1013 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
163 | DR0817_4798-4G-12 | 1008 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
164 | DR0817_4798-4G-13 | 1016 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
165 | DR0817_4798-4G-14 | 1022 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
166 | DR0817_4798-4G-16 | 1018 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
167 | DR0817_4798-4G-17 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
168 | DR0817_4798-4G-23 | 1020 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
169 | DR0817_4798-4G-24 | 1020 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
170 | DR0817_4798-4G-26 | 1022 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
171 | DR0817_4798-4G-27 | 1025 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
172 | DR0817_4798-4G-28 | 1008 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
173 | DR0817_4798-4G-29 | 1019 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
174 | DR0817_4798-4G-30 | 1006 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
175 | DR0817_4798-4G-34 | 1027 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
176 | DR0817_4798-4G-36 | 1029 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
177 | DR0817_4798-4G-37 | 993 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
178 | DR0817_4798-4G-38 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
179 | DR0817_4798-4G-39 | 1027 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
180 | DR0817_4798-4G-40 | 1016 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
181 | DR0817_4798-4G-41 | 1026 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
182 | DR0817_4798-4G-44 | 1013 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
183 | DR0817_4798-4G-46 | 992 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
184 | DR0817_4798-4G-47 | 1019 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
185 | DR0817_4798-4G-48 | 1026 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
186 | DR0817_4798-4G-50 | 992 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
187 | DR0817_4798-4G-51 | 1023 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
188 | DR0817_4798-4G-52 | 1021 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
189 | DR0817_4798-4G-53 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
190 | DR0817_4798-4G-54 | 1014 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
191 | DR0817_4798-4G-57 | 1008 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
192 | DR0817_4798-4G-58 | 1012 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
193 | DR0817_4798-4G-61 | 1009 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
194 | DR0817_4798-4G-62 | 1004 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
195 | DR0817_4798-4G-63 | 1002 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
196 | DR0817_4798-4G-64 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
197 | DR0817_4798-4G-67 | 1002 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
198 | DR0817_4798-4G-68 | 1016 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
199 | DR0817_4798-4G-69 | 999 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
200 | DR0817_4798-4G-71 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
201 | DR0817_4798-4G-72 | 1012 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
202 | DR0817_4798-4G-73 | 1004 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
203 | DR0817_4798-4G-74 | 1003 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
204 | DR0817_4798-4G-76 | 1013 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
205 | DR0817_4798-4G-77 | 1013 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
206 | DR0817_4798-4G-78 | 1015 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
207 | DR0817_4798-4G-80 | 1022 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
208 | DR0817_4798-4G-84 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
209 | DR0817_4798-4G-87 | 1006 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
210 | DR0817_4798-4G-88 | 1013 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
211 | DR0817_4798-4G-90 | 1003 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
212 | DR0817_4798-4G-91 | 1015 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
213 | DR0817_4798-4G-93 | 1019 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
214 | DR0817_4798-4G-97 | 1017 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
215 | DR0817_4798-4G-98 | 1011 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
216 | DR0817_4798-4G-99 | 1008 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
217 | DR0817_4798-4G-100 | 1006 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
218 | DR0817_4798-4G-101 | 1012 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
219 | DR0817_4798-4G-102 | 1024 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
220 | DR0817_4798-4G-104 | 1023 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
221 | DR0817_4798-4G-105 | 1016 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
222 | DR0817_4798-4G-107 | 1018 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
223 | DR0817_4798-4G-108 | 1022 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
224 | DR0817_4798-4G-109 | 1023 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
225 | DR0817_4798-4G-110 | 1003 |  | 817 | 13/10/2017 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10111 | 29/09/2017 | HR63D 6944 | CMI LTD | CMI/4794/00692 | 29/09/2017 | P-88/17 | 14-06-2017
226 | DR0818_0001 | 741 |  | 818 | 13-10-2017 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
227 | DR0818_0002 | 741 |  | 818 | 13-10-2017 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
228 | DR0818_0003 | 731 |  | 818 | 13-10-2017 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
229 | DR0818_0004 | 736 |  | 818 | 13-10-2017 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
230 | DR0818_0005 | 746 |  | 818 | 13-10-2017 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
231 | DR0818_0006 | 728 |  | 818 | 13-10-2017 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
232 | DR0818_0001 | 1006 |  | 818 | 13-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
233 | DR0818_0002 | 978 |  | 818 | 13-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
234 | DR0818_0003 | 978 |  | 818 | 13-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
235 | DR0818_0004 | 974 |  | 818 | 13-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
236 | DR0818_0001 | 975 |  | 818 | 13-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
237 | DR0818_0002 | 1003 |  | 818 | 13-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439807 | 29-09-2017 | NL02Q 3462 | SPECIAL CABLE PVT LTD | SCPL/R/G0171 | 29-09-2017 | P-81/17 | 2017-12-06
238 | DR0819_0001 | 1003 |  | 819 | 14-10-2017 | 03C | 2.5 | CU | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D03J2.5 | 03Cx2.5Sqmm CU XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
239 | DR0819_0005 | 1019 |  | 819 | 14-10-2017 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
240 | DR0819_0001 | 988 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
241 | DR0819_0002 | 993 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
242 | DR0819_0003 | 975 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
243 | DR0819_0004 | 977 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
244 | DR0819_0005 | 996 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
245 | DR0819_0006 | 1050 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
246 | DR0819_0007 | 996 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
247 | DR0819_0008 | 1001 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
248 | DR0819_0009 | 994 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
249 | DR0819_0010 | 977 |  | 819 | 14-10-2017 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
250 | DR0819_0005 | 1005 |  | 819 | 14-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
251 | DR0819_0018 | 958 |  | 819 | 14-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
252 | DR0819_0019 | 1007 |  | 819 | 14-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
253 | DR0819_0020 | 978 |  | 819 | 14-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
254 | DR0819_0021 | 974 |  | 819 | 14-10-2017 | 03C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q010 | 03Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
255 | DR0819_0003 | 1008 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
256 | DR0819_0004 | 1002 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
257 | DR0819_0005 | 998 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
258 | DR0819_0006 | 984 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
259 | DR0819_0007 | 1041 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
260 | DR0819_0009 | 973 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
261 | DR0819_0010 | 1007 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
262 | DR0819_0011 | 1015 |  | 819 | 14-10-2017 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439809 | 29-09-2017 | PB05N 6401 | SPECIAL CABLE PVT LTD | SCPL/R/G0173 | 29-09-2017 | P-81/17 | 2017-12-06
263 | DR0822_0001 | 1010 |  | 822 | 14-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ025 | 3.5Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
264 | DR0822_0002 | 998 |  | 822 | 14-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ025 | 3.5Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
265 | DR0822_0003 | 999 |  | 822 | 14-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ025 | 3.5Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
266 | DR0822_0004 | 968 |  | 822 | 14-10-2017 | 3.5C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ025 | 3.5Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
267 | DR0822_0001 | 994 |  | 822 | 14-10-2017 | 02C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q095 | 02Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
268 | DR0822_0002 | 985 |  | 822 | 14-10-2017 | 02C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q095 | 02Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
269 | DR0822_0003 | 995 |  | 822 | 14-10-2017 | 02C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q095 | 02Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
270 | DR0822_0004 | 980 |  | 822 | 14-10-2017 | 02C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q095 | 02Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
271 | DR0822_0001 | 976 |  | 822 | 14-10-2017 | 03C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q050 | 03Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
272 | DR0822_0002 | 1017 |  | 822 | 14-10-2017 | 03C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q050 | 03Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
273 | DR0822_0001 | 998 |  | 822 | 14-10-2017 | 03C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q095 | 03Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
274 | DR0822_0002 | 995 |  | 822 | 14-10-2017 | 03C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q095 | 03Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
275 | DR0822_0003 | 981 |  | 822 | 14-10-2017 | 03C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q095 | 03Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
276 | DR0822_0004 | 990 |  | 822 | 14-10-2017 | 03C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q095 | 03Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
277 | DR0822_0005 | 943 |  | 822 | 14-10-2017 | 03C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q095 | 03Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
278 | DR0822_0006 | 990 |  | 822 | 14-10-2017 | 03C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q095 | 03Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439808 | 29-09-2017 | NL02G 5091 | SPECIAL CABLE PVT LTD | SCPL/R/G0172 | 29-09-2017 | P-81/17 | 2017-12-06
279 | DR0897_4794-2F-111 | 1014 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
280 | DR0897_4794-2F-112 | 967 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
281 | DR0897_4794-2F-113 | 1007 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
282 | DR0897_4794-2F-114 | 1002 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
283 | DR0897_4794-2F-115 | 1017 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
284 | DR0897_4794-2F-116 | 1014 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
285 | DR0897_4794-2F-117 | 965 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
286 | DR0897_4794-2F-118 | 1015 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
287 | DR0897_4794-2F-119 | 1016 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
288 | DR0897_4794-2F-120 | 1011 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
289 | DR0897_4794-2F-121 | 1010 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
290 | DR0897_4794-2F-122 | 1021 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
291 | DR0897_4794-2F-123 | 1000 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
292 | DR0897_4794-2F-124 | 1001 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
293 | DR0897_4794-2F-125 | 1014 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
294 | DR0897_4794-2F-126 | 991 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
295 | DR0897_4794-2F-127 | 963 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
296 | DR0897_4794-2F-128 | 1019 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
297 | DR0897_4794-2F-129 | 1006 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
298 | DR0897_4794-2F-130 | 1005 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
299 | DR0897_4794-2F-131 | 985 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
300 | DR0897_4794-2F-132 | 997 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
301 | DR0897_4794-2F-133 | 1006 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
302 | DR0897_4794-2F-134 | 1009 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
303 | DR0897_4794-2F-135 | 1010 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
304 | DR0897_4794-2F-136 | 1002 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
305 | DR0897_4794-2F-137 | 1003 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
306 | DR0897_4794-2F-138 | 998 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
307 | DR0897_4794-2F-139 | 1009 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
308 | DR0897_4794-2F-140 | 987 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
309 | DR0897_4794-2F-141 | 999 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
310 | DR0897_4794-2F-142 | 1005 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
311 | DR0897_4794-2F-143 | 977 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
312 | DR0897_4794-2F-144 | 991 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
313 | DR0897_4794-2F-145 | 965 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
314 | DR0897_4794-2F-146 | 1000 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
315 | DR0897_4794-2F-147 | 1001 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
316 | DR0897_4794-2F-148 | 991 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
317 | DR0897_4794-2F-149 | 1006 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
318 | DR0897_4794-2F-150 | 992 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
319 | DR0897_4794-2F-151 | 998 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
320 | DR0897_4794-2F-152 | 997 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
321 | DR0897_4794-2F-153 | 1005 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
322 | DR0897_4794-2F-154 | 1004 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
323 | DR0897_4794-2F-155 | 1001 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
324 | DR0897_4794-2F-156 | 988 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
325 | DR0897_4794-2F-157 | 1006 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
326 | DR0897_4794-2F-158 | 1006 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
327 | DR0897_4794-2F-159 | 1003 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
328 | DR0897_4794-2F-160 | 1005 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
329 | DR0897_4794-2F-161 | 1011 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
330 | DR0897_4794-2F-162 | 998 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
331 | DR0897_4794-2F-163 | 978 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
332 | DR0897_4794-2F-164 | 1009 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
333 | DR0897_4794-2F-165 | 1003 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
334 | DR0897_4794-2F-166 | 1004 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
335 | DR0897_4794-2F-167 | 1001 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
336 | DR0897_4794-2F-168 | 991 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
337 | DR0897_4794-2F-169 | 1009 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
338 | DR0897_4794-2F-170 | 1006 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
339 | DR0897_4794-2F-171 | 991 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
340 | DR0897_4794-2F-172 | 1007 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
341 | DR0897_4794-2F-173 | 1000 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
342 | DR0897_4794-2F-174 | 1004 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
343 | DR0897_4794-2F-175 | 1004 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
344 | DR0897_4794-2F-176 | 1008 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
345 | DR0897_4794-2F-177 | 1001 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
346 | DR0897_4794-2F-178 | 1006 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
347 | DR0897_4794-2F-179 | 1005 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
348 | DR0897_4794-2F-180 | 1010 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
349 | DR0897_4794-2F-181 | 985 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
350 | DR0897_4794-2F-182 | 1004 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
351 | DR0897_4794-2F-183 | 977 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
352 | DR0897_4794-2F-184 | 990 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
353 | DR0897_4794-2F-185 | 983 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
354 | DR0897_4794-2F-186 | 993 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
355 | DR0897_4794-2F-187 | 1009 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
356 | DR0897_4794-2F-188 | 1000 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
357 | DR0897_4794-2F-189 | 1016 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
358 | DR0897_4794-2F-190 | 999 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
359 | DR0897_4794-2F-191 | 997 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
360 | DR0897_4794-2F-192 | 1002 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
361 | DR0897_4794-2F-193 | 991 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
362 | DR0897_4794-2F-194 | 1000 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
363 | DR0897_4794-2F-195 | 1003 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
364 | DR0897_4794-2G(O)A-196 | 989 |  | 897 | 26/10/2017 | 02P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
365 | DR0897_4794-4G(O)A-197 | 1001 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
366 | DR0897_4794-4G(O)A-198 | 980 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
367 | DR0897_4794-4G(O)A-199 | 995 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
368 | DR0897_4794-4G(O)A-200 | 1009 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
369 | DR0897_4794-4G(O)A-201 | 998 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
370 | DR0897_4794-4G(O)A-202 | 1004 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
371 | DR0897_4794-4G(O)A-203 | 999 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
372 | DR0897_4794-4G(O)A-204 | 1002 |  | 897 | 26/10/2017 | 04P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10118 | 2017-10-10 | HR63B 4200 | CMI LTD | CMI/4794/00729 | 2017-10-10 | P-88/17 | 14-06-2017
373 | DR0954_4794-8G(O)-229 | 987 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
374 | DR0954_4794-8G(O)-230 | 998 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
375 | DR0954_4794-8G(O)-231 | 1001 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
376 | DR0954_4794-8G(O)-232 | 1001 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
377 | DR0954_4794-8G(O)-233 | 1000 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
378 | DR0954_4794-8G(O)-234 | 994 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
379 | DR0954_4794-8G(O)-235 | 1002 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
380 | DR0954_4794-8G(O)-236 | 1001 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
381 | DR0954_4794-8G(O)-237 | 1002 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
382 | DR0954_4794-8G(O)-238 | 994 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
383 | DR0954_4794-8G(O)-239 | 997 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
384 | DR0954_4794-8G(O)-240 | 982 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
385 | DR0954_4794-8G(O)-241 | 997 |  | 954 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
387 | DR0954_4794-12G(O)-242 | 994 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
388 | DR0954_4794-12G(O)-243 | 999 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
389 | DR0954_4794-12G(O)-244 | 998 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
390 | DR0954_4794-12G(O)-245 | 999 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
391 | DR0954_4794-12G(O)-246 | 1008 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
392 | DR0954_4794-12G(O)-247 | 1005 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
393 | DR0954_4794-12G(O)-248 | 986 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
394 | DR0954_4794-12G(O)-249 | 1000 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
395 | DR0954_4794-12G(O)-250 | 1005 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
396 | DR0954_4794-12G(O)-251 | 999 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
397 | DR0954_4794-12G(O)-252 | 976 |  | 954 | 2017-06-11 | 12P | 0.5 | ATC | TYPE-G | ARM | 1.1 KV | PEM INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G ARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10162 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00823 | 30/10/2017 | P-88/17 | 14-06-2017
398 | DR0955_4794-8F(IO)-205 | 971 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
399 | DR0955_4794-8F(IO)-206 | 1006 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
400 | DR0955_4794-8F(IO)-207 | 998 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
401 | DR0955_4794-8F(IO)-208 | 986 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
402 | DR0955_4794-8F(IO)-209 | 950 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
403 | DR0955_4794-8F(IO)-210 | 997 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
404 | DR0955_4794-8F(IO)-211 | 1002 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
405 | DR0955_4794-8F(IO)-212 | 994 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
406 | DR0955_4794-8F(IO)-213 | 975 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
407 | DR0955_4794-8F(IO)-214 | 998 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
408 | DR0955_4794-8F(IO)-215 | 999 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
409 | DR0955_4794-8F(IO)-216 | 981 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
410 | DR0955_4794-8F(IO)-217 | 990 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
411 | DR0955_4794-8F(IO)-218 | 995 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
412 | DR0955_4794-8F(IO)-219 | 997 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
413 | DR0955_4794-8F(IO)-220 | 987 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
414 | DR0955_4794-8F(IO)-221 | 988 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
415 | DR0955_4794-8F(IO)-222 | 978 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
416 | DR0955_4794-8F(IO)-223 | 982 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
417 | DR0955_4794-8F(IO)-224 | 996 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
418 | DR0955_4794-8F(IO)-225 | 984 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
419 | DR0955_4794-8F(IO)-226 | 988 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
420 | DR0955_4794-8F(IO)-227 | 992 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
421 | DR0955_4794-8F(IO)-228 | 989 |  | 955 | 2017-06-11 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | PEM INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM PEM INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 10161 | 30/10/2017 | OD14K 1010 | CMI LTD | CMI/4794/00822 | 30/10/2017 | P-88/17 | 14-06-2017
422 | DR0968_0019 | 993 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
423 | DR0968_0020 | 987 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
424 | DR0968_0021 | 987 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
425 | DR0968_0022 | 985 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
426 | DR0968_0023 | 990 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
427 | DR0968_0024 | 987 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
428 | DR0968_0025 | 1002 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
429 | DR0968_0026 | 990 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
430 | DR0968_0027 | 991 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
431 | DR0968_0028 | 991 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
432 | DR0968_0029 | 991 |  | 968 | 2017-07-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
433 | DR0968_0001 | 967 |  | 968 | 2017-07-11 | 3.5C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ095 | 3.5Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
434 | DR0968_0002 | 988 |  | 968 | 2017-07-11 | 3.5C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ095 | 3.5Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
435 | DR0968_0003 | 977 |  | 968 | 2017-07-11 | 3.5C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ095 | 3.5Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
436 | DR0968_0004 | 980 |  | 968 | 2017-07-11 | 3.5C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ095 | 3.5Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
437 | DR0968_0005 | 962 |  | 968 | 2017-07-11 | 3.5C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ095 | 3.5Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
438 | DR0968_0006 | 997 |  | 968 | 2017-07-11 | 3.5C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ095 | 3.5Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
439 | DR0968_0007 | 963 |  | 968 | 2017-07-11 | 3.5C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ095 | 3.5Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
440 | DR0968_0017 | 751 |  | 968 | 2017-07-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
441 | DR0968_0009 | 727 |  | 968 | 2017-07-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
442 | DR0968_0010 | 731 |  | 968 | 2017-07-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
443 | DR0968_0011 | 762 |  | 968 | 2017-07-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
444 | DR0968_0012 | 761 |  | 968 | 2017-07-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439825 | 31-10-2017 | NL01Q 5271 | SPECIAL CABLE PVT LTD | SCPL/R/G0208 | 31-10-2017 | P-81/17 | 2017-12-06
445 | DR0969_0030 | 991 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
446 | DR0969_0031 | 992 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
447 | DR0969_0032 | 990 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
448 | DR0969_0033 | 996 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
449 | DR0969_0034 | 991 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
450 | DR0969_0035 | 959 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
451 | DR0969_0036 | 996 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
452 | DR0969_0037 | 989 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
453 | DR0969_0038 | 1006 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
454 | DR0969_0039 | 989 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
455 | DR0969_0040 | 1002 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
456 | DR0969_0041 | 991 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
457 | DR0969_0042 | 996 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
458 | DR0969_0043 | 992 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
459 | DR0969_0044 | 991 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
460 | DR0969_0045 | 1007 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
461 | DR0969_0046 | 970 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
462 | DR0969_0047 | 986 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
463 | DR0969_0048 | 996 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
464 | DR0969_0049 | 996 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
465 | DR0969_0050 | 975 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
466 | DR0969_0051 | 1000 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
467 | DR0969_0052 | 980 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
468 | DR0969_0053 | 1001 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
469 | DR0969_0054 | 1001 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
470 | DR0969_0055 | 974 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
471 | DR0969_0056 | 997 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
472 | DR0969_0057 | 986 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
473 | DR0969_0058 | 985 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
474 | DR0969_0059 | 982 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
475 | DR0969_0060 | 985 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
476 | DR0969_0061 | 998 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
477 | DR0969_0062 | 843 |  | 969 | 2017-08-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
478 | DR0969_0001 | 1017 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
479 | DR0969_0002 | 969 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
480 | DR0969_0003 | 981 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
481 | DR0969_0004 | 981 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
482 | DR0969_0005 | 981 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
483 | DR0969_0006 | 983 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
484 | DR0969_0007 | 990 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
485 | DR0969_0008 | 1014 |  | 969 | 2017-08-11 | 3.5C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ050 | 3.5Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
486 | DR0969_0001 | 994 |  | 969 | 2017-08-11 | 01C | 120 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q120 | 01Cx120Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
487 | DR0969_0002 | 1006 |  | 969 | 2017-08-11 | 01C | 120 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q120 | 01Cx120Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439824 | 31-10-2017 | NL02K 6329 | SPECIAL CABLE PVT LTD | SCPL/R/G0207 | 31-10-2017 | P-81/17 | 2017-12-06
488 | DR1006_0001 | 990 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
489 | DR1006_0002 | 992 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
490 | DR1006_0003 | 995 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
491 | DR1006_0004 | 981 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
492 | DR1006_0005 | 987 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
493 | DR1006_0006 | 998 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
494 | DR1006_0007 | 987 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
495 | DR1006_0008 | 992 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
496 | DR1006_0009 | 998 |  | 1006 | 2017-11-11 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
497 | DR1006_0001 | 742 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
498 | DR1006_0002 | 746 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
499 | DR1006_0003 | 747 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
500 | DR1006_0004 | 745 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
501 | DR1006_0005 | 745 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
502 | DR1006_0006 | 751 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
503 | DR1006_0007 | 755 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
504 | DR1006_0008 | 746 |  | 1006 | 2017-11-11 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
505 | DR1006_0001 | 754 |  | 1006 | 2017-11-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
506 | DR1006_0002 | 743 |  | 1006 | 2017-11-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
507 | DR1006_0003 | 715 |  | 1006 | 2017-11-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
508 | DR1006_0004 | 742 |  | 1006 | 2017-11-11 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754874 | 31-10-2017 | NL01K 6988 | SPECIAL CABLE PVT LTD | SCPL/R/G0210 | 31-10-2017 | P-81/17 | 2017-12-06
509 | DR1050_0010 | 993 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
510 | DR1050_0011 | 989 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
511 | DR1050_0012 | 985 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
512 | DR1050_0013 | 979 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
513 | DR1050_0014 | 989 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
514 | DR1050_0015 | 986 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
515 | DR1050_0016 | 988 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
516 | DR1050_0017 | 984 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
517 | DR1050_0018 | 987 |  | 1050 | 16-11-2017 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
518 | DR1050_0009 | 747 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
519 | DR1050_0010 | 750 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
520 | DR1050_0011 | 750 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
521 | DR1050_0012 | 754 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
522 | DR1050_0013 | 748 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
523 | DR1050_0014 | 749 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
524 | DR1050_0015 | 747 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
525 | DR1050_0016 | 768 |  | 1050 | 16-11-2017 | 01C | 630 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q630 | 01Cx630Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
526 | DR1050_0005 | 740 |  | 1050 | 16-11-2017 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
527 | DR1050_0006 | 744 |  | 1050 | 16-11-2017 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
528 | DR1050_0007 | 735 |  | 1050 | 16-11-2017 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
529 | DR1050_0008 | 742 |  | 1050 | 16-11-2017 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 148754863 | 31-10-2017 | NL01K 6982 | SPECIAL CABLE PVT LTD | SCPL/R/G0209 | 31-10-2017 | P-81/17 | 2017-12-06
530 | DR1095_0001 | 978 |  | 1095 | 28-11-2017 | 3.5C | 50 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN050 | 3.5Cx050Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
531 | DR1095_0001 | 998 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
532 | DR1095_0002 | 984 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
533 | DR1095_0003 | 1007 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
534 | DR1095_0004 | 1000 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
535 | DR1095_0005 | 974 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
536 | DR1095_0006 | 995 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
537 | DR1095_0007 | 1002 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
538 | DR1095_0008 | 1003 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
539 | DR1095_0009 | 996 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
540 | DR1095_0010 | 996 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
541 | DR1095_0011 | 982 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
542 | DR1095_0012 | 988 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
543 | DR1095_0013 | 992 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
544 | DR1095_0014 | 982 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
545 | DR1095_0015 | 998 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
546 | DR1095_0016 | 996 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
547 | DR1095_0017 | 983 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
548 | DR1095_0018 | 995 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
549 | DR1095_0019 | 995 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
550 | DR1095_0020 | 974 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
551 | DR1095_0021 | 1017 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
552 | DR1095_0022 | 979 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
553 | DR1095_0023 | 981 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
554 | DR1095_0024 | 987 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
555 | DR1095_0025 | 989 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
556 | DR1095_0026 | 989 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
557 | DR1095_0027 | 1017 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
558 | DR1095_0028 | 987 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
559 | DR1095_0029 | 988 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
560 | DR1095_0030 | 992 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
561 | DR1095_0031 | 998 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
562 | DR1095_0032 | 991 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
563 | DR1095_0033 | 991 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
564 | DR1095_0034 | 1017 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
565 | DR1095_0035 | 992 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
566 | DR1095_0036 | 995 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
567 | DR1095_0037 | 984 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
568 | DR1095_0038 | 987 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
569 | DR1095_0039 | 1014 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
570 | DR1095_0040 | 1013 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
571 | DR1095_0041 | 982 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
572 | DR1095_0042 | 986 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
573 | DR1095_0043 | 986 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
574 | DR1095_0044 | 970 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
575 | DR1095_0045 | 956 |  | 1095 | 28-11-2017 | 02C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02L2.5 | 02Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
576 | DR1095_0001 | 734 |  | 1095 | 28-11-2017 | 3.5C | 185 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ185 | 3.5Cx185Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
577 | DR1095_0001 | 733 |  | 1095 | 28-11-2017 | 03C | 150 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
578 | DR1095_0001 | 999 |  | 1095 | 28-11-2017 | 02C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q050 | 02Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 439837 | 16-11-2017 | NL01L 1372 | SPECIAL CABLE PVT LTD | SCPL/R/G0248 | 16-11-2017 | P-81/17 | 2017-12-06
579 | DR1146_17PW011461 | 992 |  | 1146 | 2017-08-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
580 | DR1146_17PW011465 | 1000 |  | 1146 | 2017-08-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
581 | DR1146_17PW011459 | 997 |  | 1146 | 2017-08-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
582 | DR1146_17PW011460 | 1000 |  | 1146 | 2017-08-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
583 | DR1146_17PW011462 | 995 |  | 1146 | 2017-08-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
584 | DR1146_17PW011463 | 995 |  | 1146 | 2017-08-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
585 | DR1146_17PW011464 | 992 |  | 1146 | 2017-08-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
586 | DR1146_17PV011148 | 994 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
587 | DR1146_17PV011410 | 997 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
588 | DR1146_17PV011480 | 999 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
589 | DR1146_17PV011146 | 990 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
590 | DR1146_17PV011147 | 992 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
591 | DR1146_17PV011414 | 988 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
592 | DR1146_17PV011479 | 1000 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
593 | DR1146_17PV011411 | 993 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
594 | DR1146_17PV011413 | 998 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
595 | DR1146_17PV011424 | 990 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
596 | DR1146_17PV011425 | 992 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
597 | DR1146_17PV011426 | 992 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
598 | DR1146_17PV011412 | 992 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
599 | DR1146_17PV011415 | 992 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
600 | DR1146_17PV011481 | 1000 |  | 1146 | 2017-08-12 | 12C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C1.5 | 12Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
601 | DR1146_17PT011474 | 993 |  | 1146 | 2017-08-12 | 12C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C2.5 | 12Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
602 | DR1146_17PT011145 | 986 |  | 1146 | 2017-08-12 | 12C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C2.5 | 12Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
603 | DR1146_17PT011477 | 990 |  | 1146 | 2017-08-12 | 12C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C2.5 | 12Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
604 | DR1146_17PT011478 | 986 |  | 1146 | 2017-08-12 | 12C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C2.5 | 12Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
605 | DR1146_17PT011475 | 987 |  | 1146 | 2017-08-12 | 12C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D12C2.5 | 12Cx2.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406302 | 30-11-2017 | GJ12AY 7204 | KEC INTERNATIONAL LTD | 00510E117601654 | 30-11-2017 | P-149/17 | 16-09-2017
606 | DR1150_17PA011427 | 989 |  | 1150 | 2017-09-12 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
607 | DR1150_17PA011430 | 990 |  | 1150 | 2017-09-12 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
608 | DR1150_17PA011428 | 992 |  | 1150 | 2017-09-12 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
609 | DR1150_17PW011473 | 1000 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
610 | DR1150_17PW011469 | 980 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
611 | DR1150_17PW011471 | 1000 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
612 | DR1150_17PW011472 | 989 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
613 | DR1150_17PW011468 | 985 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
614 | DR1150_17PA011773 | 990 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
615 | DR1150_17PA011774 | 997 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
616 | DR1150_17PA011775 | 997 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
617 | DR1150_17PA011776 | 1000 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
618 | DR1150_17PA011777 | 1000 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
619 | DR1150_17PA011778 | 986 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
620 | DR1150_17PA011779 | 984 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
621 | DR1150_17PW011470 | 1000 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
622 | DR1150_17PA011780 | 1000 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
623 | DR1150_17PA011781 | 1000 |  | 1150 | 2017-09-12 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
624 | DR1150_17PW011416 | 992 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
625 | DR1150_17PW011417 | 993 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
626 | DR1150_17PW011422 | 1000 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
627 | DR1150_17PW011423 | 1000 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
628 | DR1150_17PW011432 | 1000 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
629 | DR1150_17PW011433 | 998 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
630 | DR1150_17PW011554 | 1000 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
631 | DR1150_17PW011418 | 999 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
632 | DR1150_17PW011419 | 999 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
633 | DR1150_17PW011421 | 1000 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
634 | DR1150_17PW011420 | 992 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
635 | DR1150_17PW011782 | 1000 |  | 1150 | 2017-09-12 | 07C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D07C1.5 | 07Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
636 | DR1150_17PA011555 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
637 | DR1150_17PA011556 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
638 | DR1150_17PA011557 | 1003 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
639 | DR1150_17PA011558 | 1001 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
640 | DR1150_17PA011559 | 1003 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
641 | DR1150_17PA011560 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
642 | DR1150_17PA011562 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
643 | DR1150_17PA011566 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
644 | DR1150_17PA011676 | 998 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
645 | DR1150_17PA011677 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
646 | DR1150_17PA011678 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
647 | DR1150_17PA011564 | 1003 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
648 | DR1150_17PA011565 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
649 | DR1150_17PA011675 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
650 | DR1150_17PA011783 | 995 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
651 | DR1150_17PA011784 | 995 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
652 | DR1150_17PA011785 | 993 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
653 | DR1150_17PA011786 | 993 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
654 | DR1150_17PA011787 | 993 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
655 | DR1150_17PA011788 | 995 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
656 | DR1150_17PA011685 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
657 | DR1150_17PA011789 | 993 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
658 | DR1150_17PA011686 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
659 | DR1150_17PA011687 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
660 | DR1150_17PA011688 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
661 | DR1150_17PA011679 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
662 | DR1150_17PA011680 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
663 | DR1150_17PA011681 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
664 | DR1150_17PA011682 | 991 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
665 | DR1150_17PA011683 | 1002 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
666 | DR1150_17PA011684 | 1002 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
667 | DR1150_17PA011561 | 1000 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
668 | DR1150_17PA011563 | 1020 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
669 | DR1150_17PA011790 | 995 |  | 1150 | 2017-09-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 406301 | 30-11-2017 | CG07BG 8555 | KEC INTERNATIONAL LTD | 00510E117601653 | 30-11-2017 | P-149/17 | 16-09-2017
670 | DR1323_KR-10-/17-4316 | 995 |  | 1323 | 2018-07-01 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449071 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2129 | 31-12-2017 | 400051542
671 | DR1323_KR-10-/17-4317 | 996 |  | 1323 | 2018-07-01 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449071 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2129 | 31-12-2017 | 400051542
672 | DR1323_KR-10-/17-4318 | 980 |  | 1323 | 2018-07-01 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449071 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2129 | 31-12-2017 | 400051542
673 | DR1323_KR-10-/17-4319 | 1007 |  | 1323 | 2018-07-01 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449071 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2129 | 31-12-2017 | 400051542
674 | DR1323_KR-10-/17-4321 | 995 |  | 1323 | 2018-07-01 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449071 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2129 | 31-12-2017 | 400051542
675 | DR1323_KR-10-/17-4401 | 1025 |  | 1323 | 2018-07-01 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449071 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2129 | 31-12-2017 | 400051542
676 | DR1323_KR-10-/17-4402 | 1025 |  | 1323 | 2018-07-01 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449071 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2129 | 31-12-2017 | 400051542
677 | DR1324_KR-10-/17-4052 | 1000 |  | 1324 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
678 | DR1324_KR-10-/17-4055 | 998 |  | 1324 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
679 | DR1324_KR-10-/17-4056 | 1020 |  | 1324 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
680 | DR1324_KR-10-/17-4059 | 1000 |  | 1324 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
681 | DR1324_KR-10-/17-4070 | 995 |  | 1324 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
682 | DR1324_KR-10-/17-4039 | 1014 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
683 | DR1324_KR-10-/17-4072 | 1005 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
684 | DR1324_KR-10-/17-4173 | 1000 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
685 | DR1324_KR-10-/17-4174 | 1000 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
686 | DR1324_KR-10-/17-4176 | 1210 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
687 | DR1324_KR-10-/17-4177 | 1010 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
688 | DR1324_KR-10-/17-4178 | 1017 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
689 | DR1324_KR-10-/17-4179 | 998 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
690 | DR1324_KR-10-/17-4180 | 1005 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
691 | DR1324_KR-10-/17-4192 | 990 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
692 | DR1324_KR-10-/17-4194 | 1035 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
693 | DR1324_KR-10-/17-4315 | 1003 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
694 | DR1324_KR-10-/17-4320 | 999 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
695 | DR1324_KR-10-/17-4305 | 968 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
696 | DR1324_KR-10-/17-4306 | 1020 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
697 | DR1324_KR-10-/17-4308 | 999 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
698 | DR1324_KR-10-/17-4312 | 991 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
699 | DR1324_KR-10-/17-4069 | 1015 |  | 1324 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
700 | DR1324_KR-10-/17-4032 | 994 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
701 | DR1324_KR-10-/17-4035 | 1002 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
702 | DR1324_KR-10-/17-4036 | 1000 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
703 | DR1324_KR-10-/17-4037 | 999 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
704 | DR1324_KR-10-/17-4046 | 990 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
705 | DR1324_KR-10-/17-4047 | 1001 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
706 | DR1324_KR-10-/17-4048 | 1009 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
707 | DR1324_KR-10-/17-4050 | 1005 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
708 | DR1324_KR-10-/17-4051 | 1005 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
709 | DR1324_KR-10-/17-4058 | 1005 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
710 | DR1324_KR-10-/17-4033 | 992 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
711 | DR1324_KR-10-/17-4043 | 1000 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
712 | DR1324_KR-10-/17-4044 | 501 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
713 | DR1324_KR-10-/17-4314 | 998 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
714 | DR1324_KR-10-/17-4191 | 1001 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
715 | DR1324_KR-10-/17-4198 | 1034 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
716 | DR1324_KR-10-/17-4200 | 1045 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
717 | DR1324_KR-10-/17-4201 | 1020 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
718 | DR1324_KR-10-/17-4202 | 1050 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
719 | DR1324_KR-10-/17-4203 | 1012 |  | 1324 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
720 | DR1324_KR-10-/17-4074 | 1000 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
721 | DR1324_KR-10-/17-4079 | 1050 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
722 | DR1324_KR-10-/17-4161 | 990 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
723 | DR1324_KR-10-/17-4162 | 1000 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
724 | DR1324_KR-10-/17-4163 | 995 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
725 | DR1324_KR-10-/17-4164 | 1000 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
726 | DR1324_KR-10-/17-4165 | 995 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
727 | DR1324_KR-10-/17-4166 | 1024 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
728 | DR1324_KR-10-/17-4167 | 1050 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
729 | DR1324_KR-10-/17-4170 | 1006 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
730 | DR1324_KR-10-/17-4171 | 995 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
731 | DR1324_KR-10-/17-4172 | 1010 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
732 | DR1324_KR-10-/17-4189 | 1004 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
733 | DR1324_KR-10-/17-4404 | 975 |  | 1324 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 6449070 | 31-12-2017 | HR38Q 5984 | PARAMOUNT | K17-2127 | 31-12-2017 | 400051541
734 | DR1325_KR-10-/17-4053 | 1000 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
735 | DR1325_KR-10-/17-4054 | 500 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
736 | DR1325_KR-10-/17-4060 | 1002 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
737 | DR1325_KR-10-/17-4061 | 1000 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
738 | DR1325_KR-10-/17-4062 | 1009 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
739 | DR1325_KR-10-/17-4063 | 1000 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
740 | DR1325_KR-10-/17-4064 | 999 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
741 | DR1325_KR-10-/17-4071 | 988 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
742 | DR1325_KR-10-/17-4038 | 975 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
743 | DR1325_KR-10-/17-4073 | 1010 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
744 | DR1325_KR-10-/17-4175 | 1005 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
745 | DR1325_KR-10-/17-4193 | 995 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
746 | DR1325_KR-10-/17-4195 | 992 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
747 | DR1325_KR-10-/17-4196 | 1020 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
748 | DR1325_KR-10-/17-4403 | 994 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
749 | DR1325_KR-10-/17-4307 | 402 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
750 | DR1325_KR-10-/17-4310 | 1000 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
751 | DR1325_KR-10-/17-4311 | 992 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
752 | DR1325_KR-10-/17-4313 | 991 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | EDN INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
753 | DR1325_KR-10-/17-4068 | 1008 |  | 1325 | 2018-07-01 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
754 | DR1325_KR-10-/17-4034 | 1005 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
755 | DR1325_KR-10-/17-4045 | 1027 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
756 | DR1325_KR-10-/17-4049 | 1009 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
757 | DR1325_KR-10-/17-4057 | 1000 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
758 | DR1325_KR-10-/17-4065 | 1010 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
759 | DR1325_KR-10-/17-4066 | 998 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
760 | DR1325_KR-10-/17-4067 | 1002 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
761 | DR1325_KR-10-/17-4407 | 1006 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
762 | DR1325_KR-10-/17-4408 | 990 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
763 | DR1325_KR-10-/17-4190 | 525 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
764 | DR1325_KR-10-/17-4197 | 1020 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
765 | DR1325_KR-10-/17-4199 | 1013 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
766 | DR1325_KR-10-/17-1533 | 970 |  | 1325 | 2018-07-01 | 08P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E08V0.5 | 08Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
767 | DR1325_KR-10-/17-4309 | 1020 |  | 1325 | 2018-07-01 | 12P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E12V0.5 | 12Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
768 | DR1325_KR-10-/17-4075 | 994 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
769 | DR1325_KR-10-/17-4076 | 1005 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
770 | DR1325_KR-10-/17-4077 | 1004 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
771 | DR1325_KR-10-/17-4078 | 998 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
772 | DR1325_KR-10-/17-4160 | 995 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
773 | DR1325_KR-10-/17-4168 | 1000 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
774 | DR1325_KR-10-/17-4169 | 995 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
775 | DR1325_KR-10-/17-4188 | 990 |  | 1325 | 2018-07-01 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11297 | 31-12-2017 | OD15B 7257 | PARAMOUNT | K17-2128 | 31-12-2017 | 400051541
776 | DR1337_2147483647 | 989 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
777 | DR1337_2147483647 | 995 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
778 | DR1337_2147483647 | 1050 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
779 | DR1337_2147483647 | 1019 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
780 | DR1337_2147483647 | 1007 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
781 | DR1337_2147483647 | 995 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
782 | DR1337_2147483647 | 1001 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
783 | DR1337_2147483647 | 996 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
784 | DR1337_2147483647 | 957 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
785 | DR1337_2147483647 | 987 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
786 | DR1337_2147483647 | 998 |  | 1337 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181452 | 31/12/2017 | CG04DE 4777 | APAR INDUSTRIES | 9701612215 | 31/12/2017 | P-185/17 | 2017-08-11
787 | DR1338_2147483647 | 1011 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
788 | DR1338_2147483647 | 1042 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
789 | DR1338_2147483647 | 1000 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
790 | DR1338_2147483647 | 967 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
791 | DR1338_2147483647 | 991 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
792 | DR1338_2147483647 | 1000 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
793 | DR1338_2147483647 | 1002 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
794 | DR1338_2147483647 | 998 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
795 | DR1338_2147483647 | 997 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
796 | DR1338_2147483647 | 995 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
797 | DR1338_2147483647 | 1003 |  | 1338 | 2018-09-01 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 181451 | 31/12/2017 | CG07AV 9977 | APAR INDUSTRIES | 9701612214 | 31/12/2017 | P-185/17 | 2017-08-11
798 | DR1568_LPA//192 | 982 |  | 1568 | 2018-12-02 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D02C2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
799 | DR1568_LPA//190 | 1020 |  | 1568 | 2018-12-02 | 04C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D04C2.5 | 04Cx2.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
800 | DR1568_LPA//189 | 987 |  | 1568 | 2018-12-02 | 04C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D04C2.5 | 04Cx2.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
801 | DR1568_LPA//191 | 987 |  | 1568 | 2018-12-02 | 04C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D04C2.5 | 04Cx2.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
802 | DR1568_LPA//170 | 1050 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
803 | DR1568_LPA//182 | 1045 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
804 | DR1568_LPA//178 | 1038 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
805 | DR1568_LPA//181 | 1035 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
806 | DR1568_LPA//183 | 1030 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
807 | DR1568_LPA//184 | 1030 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
808 | DR1568_LPA//180 | 1030 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
809 | DR1568_LPA//179 | 1025 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
810 | DR1568_LPA//177 | 1025 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
811 | DR1568_LPA//166 | 1020 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
812 | DR1568_LPA//176 | 1020 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
813 | DR1568_LPA//185 | 1020 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
814 | DR1568_LPA//186 | 1020 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
815 | DR1568_LPA//167 | 1020 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
816 | DR1568_LPA//188 | 1020 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
817 | DR1568_LPA//168 | 1020 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
818 | DR1568_LPA//187 | 1011 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
819 | DR1568_LPA//173 | 1011 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
820 | DR1568_LPA//169 | 1011 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
821 | DR1568_LPA//174 | 1010 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
822 | DR1568_LPA//172 | 1010 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
823 | DR1568_LPA//171 | 1010 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
824 | DR1568_LPA//175 | 947 |  | 1568 | 2018-12-02 | 03C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | D03C1.5 | 03Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 12203 | 2018-04-02 | OR02BF 4392 | GUPTA POWER | 9117315219 | 2018-04-02 | 4000052004
825 | DR1592_1.1' | 1013 |  | 1592 | 19-02-2018 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
826 | DR1592_1.2' | 1010 |  | 1592 | 19-02-2018 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
827 | DR1592_1.3' | 1006 |  | 1592 | 19-02-2018 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
828 | DR1592_1.4' | 1003 |  | 1592 | 19-02-2018 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
829 | DR1592_2.1' | 1002 |  | 1592 | 19-02-2018 | 04P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E04V0.5 | 04Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
830 | DR1592_3.1' | 1001 |  | 1592 | 19-02-2018 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
831 | DR1592_3.2' | 1005 |  | 1592 | 19-02-2018 | 02P | 0.5 | CR-CRAL | TYPE-KX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Px0.5Sqmm CR-CRAL TYPE-KX UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
832 | DR1592_4.1' | 1010 |  | 1592 | 19-02-2018 | 02T | 0.5 | CU-CUNI | TYPE-TX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Tx0.5Sqmm CU-CUNI TYPE-TX UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
833 | DR1592_4.2' | 1022 |  | 1592 | 19-02-2018 | 02T | 0.5 | CU-CUNI | TYPE-TX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Tx0.5Sqmm CU-CUNI TYPE-TX UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
834 | DR1592_4.3' | 505 |  | 1592 | 19-02-2018 | 02T | 0.5 | CU-CUNI | TYPE-TX | UNARM | 1.1 KV | EDN INSTRUMENT | E02X0.5 | 02Tx0.5Sqmm CU-CUNI TYPE-TX UNARM EDN INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
835 | DR1592_5.1' | 1020 |  | 1592 | 19-02-2018 | 05C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN CONTROL | E05C1.5 | 05Cx1.5Sqmm CU PVC-FRLS UNARM EDN CONTROL CABLE | CS-1 (COVER STORE-1) | 488742424 | 2018-08-02 | OD14A 8974 | TEMPSENS | 1637 | 29-12-2017 | 4000051705
836 | DR1617_KR-10-/17-4322 | 1000 |  | 1617 | 23-02-2018 | 02T | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Tx0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11485 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2571 | 16-02-2018 | 4000051541
837 | DR1617_KR-10-/17-4405 | 1232 |  | 1617 | 23-02-2018 | 02T | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Tx0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11485 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2571 | 16-02-2018 | 4000051541
838 | DR1617_KR-10-/17-4406 | 1030 |  | 1617 | 23-02-2018 | 02T | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Tx0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11485 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2571 | 16-02-2018 | 4000051541
839 | DR1617_KR-10-/17-4323 | 1005 |  | 1617 | 23-02-2018 | 02T | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Tx0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11485 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2571 | 16-02-2018 | 4000051541
840 | DR1617_KR-10-/17-4324 | 1003 |  | 1617 | 23-02-2018 | 02T | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Tx0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11485 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2571 | 16-02-2018 | 4000051541
841 | DR1617_KR-10-/17-4325 | 1001 |  | 1617 | 23-02-2018 | 02T | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Tx0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11485 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2571 | 16-02-2018 | 4000051541
842 | DR1617_KR-10-/17-4326 | 1024 |  | 1617 | 23-02-2018 | 02T | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUMENT | E02W0.5 | 02Tx0.5Sqmm ATC TYPE-F ARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11485 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2571 | 16-02-2018 | 4000051541
843 | DR1618_KR-10-/18-0008 | 306 |  | 1618 | 23-02-2018 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM EDN INSTRUMENT CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 11481 | 16-02-2018 | OD19E 6681 | PARAMOUNT | K17-2570 | 16-02-2018 | 4000051542
844 | DR1621_CK-001 | 739 |  | 1658 | 2018-06-03 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19269 | 28-02-2018 | OD15C 7868 | APAR INDUSTRIES | 9701613762 | 28-02-2018 | P-185/17 | 2017-08-11
845 | DR1621_OF-001 | 749 |  | 1658 | 2018-06-03 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19269 | 28-02-2018 | OD15C 7868 | APAR INDUSTRIES | 9701613762 | 28-02-2018 | P-185/17 | 2017-08-11
846 | DR1658_2147483647A | 749 |  | 1658 | 2018-06-03 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19269 | 28-02-2018 | OD15C 7868 | APAR INDUSTRIES | 9701613762 | 28-02-2018 | P-185/17 | 2017-08-11
847 | DR1658_2147483647B | 746 |  | 1658 | 2018-06-03 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19269 | 28-02-2018 | OD15C 7868 | APAR INDUSTRIES | 9701613762 | 28-02-2018 | P-185/17 | 2017-08-11
848 | DR1658_2147483647A | 742 |  | 1682 | 14-03-2018 | 03C | 240 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q240 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19268 | 28-02-2018 | CG07CA 4427 | APAR INDUSTRIES | 9701613765 | 28-02-2018 | P-185/17 | 2017-08-11
849 | DR1658_2147483647B | 732 |  | 1682 | 14-03-2018 | 03C | 240 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q240 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19268 | 28-02-2018 | CG07CA 4427 | APAR INDUSTRIES | 9701613765 | 28-02-2018 | P-185/17 | 2017-08-11
850 | DR1682_2147483647C | 732 |  | 1682 | 14-03-2018 | 03C | 240 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19268 | 28-02-2018 | CG07CA 4427 | APAR INDUSTRIES | 9701613765 | 28-02-2018 | P-185/17 | 2017-08-11
851 | DR1682_2147483647D | 743 |  | 1682 | 14-03-2018 | 03C | 240 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19268 | 28-02-2018 | CG07CA 4427 | APAR INDUSTRIES | 9701613765 | 28-02-2018 | P-185/17 | 2017-08-11
852 | DR1682_2147483647 | 723 |  | 1682 | 14-03-2018 | 03C | 120 | AL | XLPE-FRLS | UNARM | 33 KV | PEM HT POWER | A03Q120 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19268 | 28-02-2018 | CG07CA 4427 | APAR INDUSTRIES | 9701613765 | 28-02-2018 | P-185/17 | 2017-08-11
853 | DR1682_2147483647 | 725 |  | 1682 | 14-03-2018 | 03C | 120 | AL | XLPE-FRLS | UNARM | 33 KV | PEM HT POWER | A03Q120 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19268 | 28-02-2018 | CG07CA 4427 | APAR INDUSTRIES | 9701613765 | 28-02-2018 | P-185/17 | 2017-08-11
854 | DR1682_2147483647C | 746 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613763 | 28-02-2018 | P-185/17 | 2017-08-11
855 | DR1682_2147483647D | 744 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613763 | 28-02-2018 | P-185/17 | 2017-08-11
856 | DR1685_2147483647E | 747 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613763 | 28-02-2018 | P-185/17 | 2017-08-11
857 | DR1685_2147483647F | 742 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613763 | 28-02-2018 | P-185/17 | 2017-08-11
858 | DR1685_2147483647G | 746 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613764 | 28-02-2018 | P-185/17 | 2017-08-11
859 | DR1685_2147483647H | 746 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613764 | 28-02-2018 | P-185/17 | 2017-08-11
860 | DR1685_2147483647I | 746 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613764 | 28-02-2018 | P-185/17 | 2017-08-11
861 | DR1685_2147483647J | 742 |  | 1685 | 14-03-2018 | 03C | 150 | AL | XLPE-FRLS | UNARM | 6.6 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 19270 | 28-02-2018 | CG04HT 5525 | APAR INDUSTRIES | 9701613764 | 28-02-2018 | P-185/17 | 2017-08-11
862 | DR1685_2147483647 | 1006 |  | 1792 | 2018-05-04 | 02P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
863 | DR1685_2147483647 | 992 |  | 1792 | 2018-05-04 | 02P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
864 | DR1792_CK-2608 | 968 |  | 1792 | 2018-05-04 | 02P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E02V0.5 | 02Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
865 | DR1792_CK-2609 | 996 |  | 1792 | 2018-05-04 | 02P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E02V0.5 | 02Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
866 | DR1792_CK-2610 | 1015 |  | 1792 | 2018-05-04 | 02P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E02V0.5 | 02Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
867 | DR1792_CK-2611 | 1004 |  | 1792 | 2018-05-04 | 02P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E02V0.5 | 02Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
868 | DR1792_CK-2612 | 989 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E02V0.5 | 02Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
869 | DR1792_CK-2613 | 975 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E02V0.5 | 02Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
870 | DR1792_CK-2633 | 975 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
871 | DR1792_CK-2634 | 997 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
872 | DR1792_CK-2635 | 990 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
873 | DR1792_CK-2636 | 990 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
874 | DR1792_CK-2637 | 983 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
875 | DR1792_CK-2638 | 960 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
876 | DR1792_CK-2639 | 960 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
877 | DR1792_CK-2640 | 1007 |  | 1792 | 2018-05-04 | 04P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
878 | DR1792_CK-2641 | 979 |  | 1792 | 2018-05-04 | 08P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
879 | DR1792_CK-2642 | 1004 |  | 1792 | 2018-05-04 | 08P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
880 | DR1792_CK-2628 | 962 |  | 1792 | 2018-05-04 | 08P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
881 | DR1792_CK-2629 | 995 |  | 1792 | 2018-05-04 | 08P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
882 | DR1792_CK-2630 | 991 |  | 1792 | 2018-05-04 | 08P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
883 | DR1792_CK-2631 | 960 |  | 1792 | 2018-05-04 | 12P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
884 | DR1792_CK-2632 | 981 |  | 1792 | 2018-05-04 | 12P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
885 | DR1792_CK-2616 | 981 |  | 1792 | 2018-05-04 | 12P | 0.5 | CU | TYPE-G | UNARM | 1.1 KV | HWR INSTRUMENT | E12V0.5 | 12Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
886 | DR1792_CK-2617 | 1004 |  | 1792 | 2018-05-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E12V0.5 | 12Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
887 | DR1792_CK-2618 | 984 |  | 1792 | 2018-05-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E12V0.5 | 12Px0.5Sqmm CU TYPE-G UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
888 | DR1792_CK-2619 | 984 |  | 1792 | 2018-05-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
889 | DR1792_CK-2620 | 984 |  | 1792 | 2018-05-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
890 | DR1792_CK-2621 | 984 |  | 1792 | 2018-05-04 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
891 | DR1792_CK-2622 | 990 |  | 1792 | 2018-05-04 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
892 | DR1792_CK-2623 | 980 |  | 1792 | 2018-05-04 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
893 | DR1792_CK-2624 | 968 |  | 1792 | 2018-05-04 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
894 | DR1792_CK-2625 | 981 |  | 1792 | 2018-05-04 | 08P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
895 | DR1792_CK-2626 | 986 |  | 1792 | 2018-05-04 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
896 | DR1792_CK-2627 | 982 |  | 1792 | 2018-05-04 | 12P | 0.5 | ATC | TYPE-F | UNARM | 1.1 KV | HWR INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 96557 | 22-03-2018 | OR15N 0094 | CORDS | I-KH/G17-18/1332 | 22-03-2018 | B7V0883 | 2017-02-09
897 | DR1792_CK-2614 | 2400 |  | 1621 | 23-02-2018 | 02P | 0.5 | ATC | TYPE-G | UNARM | 1.1 KV | EDN INSTRUMENT | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 954 | 30-12-2017 | HR55R 8154 | NETWARE COMPUTERS | NC/17-18/120 | 30-12-2017 | 4000052152
898 | DR1792_CK-2615 | 2500 |  | 1621 | 23-02-2018 | 06C | 0.5 | OFC | SINGLE MODE | ARM | 1.1 KV | EDN OPTICAL FIBER | E12W0.5 | 12Px0.5Sqmm ATC TYPE-F UNARM HWR INSTRUMENT CABLE | CS-1 (COVER STORE-1) | 954 | 30-12-2017 | HR55R 8154 | NETWARE COMPUTERS | NC/17-18/120 | 30-12-2017 | 4000052152
899 | DR2071_A1 | 654 |  | 2071 | 15-06-2018 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUSPECIAL | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUSPECIAL CABLE | STORE-2 (NEAR YARD-6) | 652514575 | 2018-01-06 | OD14M-5105 | FORBES MARSHALL | 559502429 | 2018-01-06
900 | DR2071_A2 | 648 |  | 2071 | 15-06-2018 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUSPECIAL | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUSPECIAL CABLE | STORE-2 (NEAR YARD-6) | 652514575 | 2018-01-06 | OD14M-5105 | FORBES MARSHALL | 559502429 | 2018-01-06
901 | DR2071_A3 | 648 |  | 2071 | 15-06-2018 | 04P | 0.5 | ATC | TYPE-F | ARM | 1.1 KV | EDN INSTRUSPECIAL | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F ARM EDN INSTRUSPECIAL CABLE | STORE-2 (NEAR YARD-6) | 652514575 | 2018-01-06 | OD14M-5105 | FORBES MARSHALL | 559502429 | 2018-01-06
902 | DR2192_LPA/4633 | 1015 |  | 2192 | 2018-03-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
903 | DR2192_LPA/4636 | 1020 |  | 2192 | 2018-03-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
904 | DR2192_LPA/4638 | 1016 |  | 2192 | 2018-03-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
905 | DR2192_LPA/4640 | 1006 |  | 2192 | 2018-03-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
906 | DR2192_LPA/4657 | 1001 |  | 2192 | 2018-03-08 | 07C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D07C2.5 | 07Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
907 | DR2192_LPA/4658 | 999 |  | 2192 | 2018-03-08 | 07C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D07C2.5 | 07Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
908 | DR2192_LPA/4644 | 994 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
909 | DR2192_LPA/4645 | 971 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
910 | DR2192_LPA/4646 | 971 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
911 | DR2192_LPA/4647 | 981 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
912 | DR2192_LPA/4648 | 953 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
913 | DR2192_LPA/4649 | 989 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
914 | DR2192_LPA/4650 | 991 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
915 | DR2192_LPA/4651 | 991 |  | 2192 | 2018-03-08 | 16C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D16C2.5 | 16Cx2.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
916 | DR2192_LPA/4656 | 1027 |  | 2192 | 2018-03-08 | 19C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D19C1.5 | 19Cx1.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
917 | DR2192_LPA/4654 | 1000 |  | 2192 | 2018-03-08 | 19C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D19C1.5 | 19Cx1.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
918 | DR2192_LPA/4655 | 996 |  | 2192 | 2018-03-08 | 19C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D19C1.5 | 19Cx1.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
919 | DR2192_LPA/4652 | 982 |  | 2192 | 2018-03-08 | 19C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D19C1.5 | 19Cx1.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
920 | DR2192_LPA/4653 | 976 |  | 2192 | 2018-03-08 | 19C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D19C1.5 | 19Cx1.5Sqmm CU PVC-FRLS UNARM TRY CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 31736 | 29-07-2018 | OR04M-0634 | GUPTA POWER INFRASTRUCTURE | 9118312245 | 29-07-2018
921 | DR2197_LPA/4627 | 1013 |  | 2197 | 2018-07-08 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM TRY POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
922 | DR2197_LPA/4628 | 1011 |  | 2197 | 2018-07-08 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM TRY POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
923 | DR2197_LPA/4626 | 1010 |  | 2197 | 2018-07-08 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM TRY POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
924 | DR2197_LPA/4630 | 1001 |  | 2197 | 2018-07-08 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM TRY POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
925 | DR2197_LPA/4629 | 989 |  | 2197 | 2018-07-08 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM TRY POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
926 | DR2197_LPA/4633 | 976 |  | 2197 | 2018-07-08 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D02L2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM TRY POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
927 | DR2197_LPA/4635 | 1006 |  | 2197 | 2018-07-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
928 | DR2197_LPA/4639 | 1005 |  | 2197 | 2018-07-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
929 | DR2197_LPA/4632 | 1005 |  | 2197 | 2018-07-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
930 | DR2197_LPA/4637 | 975 |  | 2197 | 2018-07-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
931 | DR2197_LPA/4634 | 952 |  | 2197 | 2018-07-08 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
932 | DR2197_LPA/4641 | 999 |  | 2197 | 2018-07-08 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
933 | DR2197_LPA/4642 | 501 |  | 2197 | 2018-07-08 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
934 | DR2197_LPA/4643 | 499 |  | 2197 | 2018-07-08 | 10C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY CONTROL | D10C2.5 | 10Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1001 | 31-07-2018 | OD02AF-6010 | GUPTA POWER INFRASTRUCTURE | 9118312329 | 31-07-2018
935 | DR2266_1000208390 | 400 |  | 2266 | 24-08-2018 | 01C | 50 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN DCPOWER | D01C050 | 01Cx50Sqmm CU PVC-FRLS UNARM EDN DC POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 254407985 | 2018-10-08 | OD14-9819 | BANGALORE | 981700196 | 2018-10-08
936 | DR2266_1000208391 | 500 |  | 2266 | 24-08-2018 | 02C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | EDN POWER | D02C2.5 | 02Cx2.5Sqmm CU PVC-FRLS UNARM EDN LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 254407985 | 2018-10-08 | OD14-9819 | BANGALORE | 981700196 | 2018-10-08
937 | DR2351_104 | 982 |  | 2351 | 2018-03-10 | 02P | 1.3 | CU | TYPE-F | ARM | 1.1 KV | TRY SCANER | E02W1.3 | 02Px1.3Sqmm CU TYPE-F UNARM TRY SCANNER CABLE | INFRONT OF BHEL PROJECT OFFICE | 6000750389 | 2018-05-07 | OR14N-6471 | DELTON CABLES LTD | 2100000480 | 2018-05-07
938 | DR2351_105 | 1006 |  | 2351 | 2018-03-10 | 02P | 1.3 | CU | TYPE-F | ARM | 1.1 KV | TRY SCANER | E02W1.3 | 02Px1.3Sqmm CU TYPE-F UNARM TRY SCANNER CABLE | INFRONT OF BHEL PROJECT OFFICE | 6000750389 | 2018-05-07 | OR14N-6471 | DELTON CABLES LTD | 2100000480 | 2018-05-07
939 | DR2351_106 | 495 |  | 2351 | 2018-03-10 | 02P | 1.3 | CU | TYPE-F | ARM | 1.1 KV | TRY SCANER | E02W1.3 | 02Px1.3Sqmm CU TYPE-F UNARM TRY SCANNER CABLE | INFRONT OF BHEL PROJECT OFFICE | 6000750389 | 2018-05-07 | OR14N-6471 | DELTON CABLES LTD | 2100000480 | 2018-05-07
940 | DR2351_107 | 1005 |  | 2351 | 2018-03-10 | 02P | 1.3 | CU | TYPE-F | ARM | 1.1 KV | TRY SCANER | E02W1.3 | 02Px1.3Sqmm CU TYPE-F UNARM TRY SCANNER CABLE | INFRONT OF BHEL PROJECT OFFICE | 6000750389 | 2018-05-07 | OR14N-6471 | DELTON CABLES LTD | 2100000480 | 2018-05-07
941 | DR2351_108 | 996 |  | 2351 | 2018-03-10 | 02P | 1.3 | CU | TYPE-F | ARM | 1.1 KV | TRY SCANER | E02W1.3 | 02Px1.3Sqmm CU TYPE-F UNARM TRY SCANNER CABLE | INFRONT OF BHEL PROJECT OFFICE | 6000750389 | 2018-05-07 | OR14N-6471 | DELTON CABLES LTD | 2100000480 | 2018-05-07
942 | DR2351_109 | 990 |  | 2351 | 2018-03-10 | 02P | 1.3 | CU | TYPE-F | ARM | 1.1 KV | TRY SCANER | E02W1.3 | 02Px1.3Sqmm CU TYPE-F UNARM TRY SCANNER CABLE | INFRONT OF BHEL PROJECT OFFICE | 6000750389 | 2018-05-07 | OR14N-6471 | DELTON CABLES LTD | 2100000480 | 2018-05-07
943 | DR2362_DRM1 |  |  | 2362 | 2018-08-10 | 01C | 1 | CU | TYPE-F | ARM | 1.1 KV | EDN COAXIAL | E01W1.0 | 01Px1.0Sqmm CU TYPE-F UNARM EDN COAXIAL CLOCK CABLE | STORE-2 (NEAR YARD-6) | 455489158 | 18-08-2018 | OD14-9819 | SIGNALS AND SYSTEMS INDIA | SS-914 | 18-08-2018
944 | DR2450_N-460 | 1000 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
945 | DR2450_N-461 | 1000 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
946 | DR2450_N-462 | 1001 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
947 | DR2450_N-463 | 1001 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
948 | DR2450_N-464 | 990 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
949 | DR2450_N-465 | 1001 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
950 | DR2450_N-466 | 1040 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
951 | DR2450_N-467 | 999 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
952 | DR2450_N-468 | 1006 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
953 | DR2450_N-469 | 1002 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
954 | DR2450_N-470 | 1001 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
955 | DR2450_N-471 | 1002 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
956 | DR2450_N-472 | 1000 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
957 | DR2450_N-473 | 1004 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
958 | DR2450_N-474 | 1002 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
959 | DR2450_N-475 | 1002 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
960 | DR2450_N-476 | 999 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
961 | DR2450_N-477 | 1003 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
962 | DR2450_N-478 | 1002 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
963 | DR2450_N-479 | 986 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
964 | DR2450_N-480 | 992 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
965 | DR2450_N-481 | 1002 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
966 | DR2450_N-482 | 1002 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
967 | DR2450_N-483 | 1003 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
968 | DR2450_N-484 | 1001 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
969 | DR2450_N-485 | 1001 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
970 | DR2450_N-486 | 1023 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
971 | DR2450_N-487 | 1020 |  | 2450 | 29-11-2018 | 03C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03C2.5 | 03Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
972 | DR2450_N-488 | 998 |  | 2450 | 29-11-2018 | 03C | 16 | AL | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03Q016 | 03Cx016Sqmm AL PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
973 | DR2450_N-489 | 1002 |  | 2450 | 29-11-2018 | 03C | 16 | AL | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03Q016 | 03Cx016Sqmm AL PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
974 | DR2450_N-490 | 1010 |  | 2450 | 29-11-2018 | 03C | 16 | AL | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D03Q016 | 03Cx016Sqmm AL PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 1443 | 23-11-2018 | OR19M-4569 | SUYOG ELECTRICAL | 852 | 23-11-2018
975 | DR2465_8012201001 | 1000 |  | 2465 | 2018-07-12 | 01C | 400 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
976 | DR2465_8012201002 | 1002 |  | 2465 | 2018-07-12 | 01C | 400 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
977 | DR2465_8012201003 | 998 |  | 2465 | 2018-07-12 | 01C | 400 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
978 | DR2465_8012201004 | 999 |  | 2465 | 2018-07-12 | 01C | 400 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
979 | DR2465_8012201005 | 982 |  | 2465 | 2018-07-12 | 01C | 400 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
980 | DR2465_8012202001 | 741 |  | 2465 | 2018-07-12 | 03C | 150 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
981 | DR2465_8012202002 | 747 |  | 2465 | 2018-07-12 | 03C | 150 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
982 | DR2465_8012202003 | 750 |  | 2465 | 2018-07-12 | 03C | 150 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
983 | DR2465_8012202004 | 750 |  | 2465 | 2018-07-12 | 03C | 150 | AL | XLPE-FRLS | UNARM | 11 KV | PEM HT POWER | B03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 5101 | 30-11-2018 | CG07CA-5385 | APAR INDUSTRIESN LIMITED | 9701617744 | 30-11-2018
984 | DR2597_MRN04-12011 | 779 |  | 2597 | 2019-04-02 | 04C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F04-0.5 | 04Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-14 (BACK SIDE OF BHEL PROJECT OFFICE) | 19796026 | 21-01-2019 | OD14-9819 | AKSH OPTIFIBRE | CB1018001629 | 21-01-2019
985 | DR2597_MRN04-12015 | 1907 |  | 2597 | 2019-04-02 | 04C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F04-0.5 | 04Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-14 (BACK SIDE OF BHEL PROJECT OFFICE) | 19796026 | 21-01-2019 | OD14-9819 | AKSH OPTIFIBRE | CB1018001629 | 21-01-2019
986 | DR2597_MRN04-12016 | 1908 |  | 2597 | 2019-04-02 | 04C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F04-0.5 | 04Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-14 (BACK SIDE OF BHEL PROJECT OFFICE) | 19796026 | 21-01-2019 | OD14-9819 | AKSH OPTIFIBRE | CB1018001629 | 21-01-2019
987 | DR2597_MRN04-12020 | 2022 |  | 2597 | 2019-04-02 | 04C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F04-0.5 | 04Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-14 (BACK SIDE OF BHEL PROJECT OFFICE) | 19796026 | 21-01-2019 | OD14-9819 | AKSH OPTIFIBRE | CB1018001629 | 21-01-2019
988 | DR2597_MRN04-12021 | 2058 |  | 2597 | 2019-04-02 | 04C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F04-0.5 | 04Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-14 (BACK SIDE OF BHEL PROJECT OFFICE) | 19796026 | 21-01-2019 | OD14-9819 | AKSH OPTIFIBRE | CB1018001629 | 21-01-2019
989 | DR2715_4871-2PG-3 | 1006 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E02V0.5 | 02Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
990 | DR2715_4871-4PG-7 | 1016 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
991 | DR2715_4871-4PG-8 | 1016 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
992 | DR2715_4871-4PG-11 | 1007 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
993 | DR2715_4871-4PG-13 | 974 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
994 | DR2715_4871-4PG-16 | 1020 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
995 | DR2715_4871-4PG-18 | 972 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
996 | DR2715_4871-4PG-20 | 1009 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
997 | DR2715_4871-8PG-23 | 979 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
998 | DR2715_4871-8PG-26 | 989 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
999 | DR2715_4871-8PG-27 | 1005 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1000 | DR2715_4871-8PG-29 | 1004 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1001 | DR2715_4871-8PG-32 | 1000 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1002 | DR2715_4871-8PG-34 | 1006 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1003 | DR2715_4871-8PG-35 | 1007 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1004 | DR2715_4871-8PG-36 | 1006 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1005 | DR2715_4871-8PG-37 | 991 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1006 | DR2715_4871-8PG-38 | 1009 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1007 | DR2715_4871-8PG-39 | 1008 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1008 | 4871-12PG-40 | 995 |  | 2715 | 30-03-2019 | 12P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E12V0.5 | 12Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1009 | 4871-12PG-41 | 1005 |  | 2715 | 30-03-2019 | 12P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E12V0.5 | 12Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1010 | 4871-2PF-43 | 1000 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1011 | DR2715_4871-4PF-47 | 1011 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1012 | DR2715_4871-4PF-49 | 1004 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1013 | DR2715_4871-4PF-53 | 1012 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1014 | DR2715_4871-4PF-56 | 1012 |  | 2715 | 30-03-2019 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1015 | DR2715_4871-8PF-59 | 1010 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1016 | DR2715_4871-8PF-60 | 1009 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1017 | DR2715_4871-8PF-61 | 974 |  | 2715 | 30-03-2019 | 08P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1018 | DR2715_4871-2PFx1.5-62 | 1004 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1019 | DR2715_4871-2PFx1.5-63 | 1002 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1020 | DR2715_4871-2PFx1.5-65 | 984 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1021 | DR2715_4871-2PFx1.5-66 | 998 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1022 | DR2715_4871-2PFx1.5-68 | 1000 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1023 | DR2715_4871-2PFx1.5-69 | 1005 |  | 2715 | 30-03-2019 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11333 | 25-03-2019 | HR38T-7137 | CMI LIMITED | 1592 | 25-03-2019 | 151018/06 | 30-11-2017
1024 | DR2717_4871-2PG-1 | 976 |  | 2717 | 2019-01-04 | 02P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1025 | DR2717_4871-2PG-2 | 1018 |  | 2717 | 2019-01-04 | 02P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E02V0.5 | 02Px0.5Sqmm ATC TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1026 | DR2717_4871-4PG-4 | 1007 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1027 | DR2717_4871-4PG-5 | 1012 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1028 | DR2717_4871-4PG-6 | 970 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1029 | DR2717_4871-4PG-9 | 1010 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1030 | DR2717_4871-4PG-10 | 1010 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1031 | DR2717_4871-4PG-12 | 1000 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1032 | DR2717_4871-4PG-14 | 1014 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1033 | DR2717_4871-4PG-15 | 990 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1034 | DR2717_4871-4PG-17 | 979 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1035 | DR2717_4871-4PG-19 | 1021 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1036 | DR2717_4871-4PG-20 | 973 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1037 | DR2717_4871-8PG-22 | 974 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1038 | DR2717_4871-8PG-24 | 988 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1039 | DR2717_4871-8PG-25 | 1010 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1040 | DR2717_4871-8PG-28 | 1013 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1041 | DR2717_4871-8PG-30 | 1009 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1042 | DR2717_4871-8PG-31 | 1013 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1043 | DR2717_4871-8PG-33 | 989 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E08V0.5 | 08Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1044 | DR2717_4871-12PG-42 | 1000 |  | 2717 | 2019-01-04 | 12P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E12V0.5 | 12Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1045 | DR2717_4871-4PF-44 | 1000 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-G | UNARM | 225 V | TRY INSTRUMENT | E04V0.5 | 04Px0.5Sqmm CU TYPE-G UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1046 | DR2717_4871-4PF-45 | 979 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1047 | DR2717_4871-4PF-46 | 980 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1048 | DR2717_4871-4PF-48 | 993 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1049 | DR2717_4871-4PF-50 | 1010 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1050 | DR2717_4871-4PF-51 | 1005 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1051 | DR2717_4871-4PF-52 | 1001 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1052 | DR2717_4871-4PF-54 | 1011 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1053 | DR2717_4871-4PF-55 | 982 |  | 2717 | 2019-01-04 | 04P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E04W0.5 | 04Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1054 | DR2717_4871-8PF-57 | 989 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1055 | DR2717_4871-8PF-58 | 1018 |  | 2717 | 2019-01-04 | 08P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E08W0.5 | 08Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1056 | DR2717_4871-2PFx1.5-64 | 981 |  | 2717 | 2019-01-04 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1057 | DR2717_4871-2PFx1.5-67 | 981 |  | 2717 | 2019-01-04 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1058 | DR2717_4871-2PFx1.5-70 | 1006 |  | 2717 | 2019-01-04 | 02P | 0.5 | ATC | TYPE-F | UNARM | 225 V | TRY INSTRUMENT | E02W0.5 | 02Px0.5Sqmm ATC TYPE-F UNARM TRY INSTRUMENT CABLE | YARD-12 (BACK SIDE OF CWPH) | 11332 | 24-03-2019 | HR63B-0879 | CMI LIMITED | 1590 | 24-03-2019 | 151018/06 | 30-11-2017
1059 | DR2725_19000474 | 4150 |  | 2725 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101853 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502911 | 29-03-2019 | 4000055560 | 2019-02-02
1060 | DR2725_19000475 | 4074 |  | 2725 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101853 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502911 | 29-03-2019 | 4000055560 | 2019-02-02
1061 | DR2725_19011764 | 4120 |  | 2725 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101853 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502911 | 29-03-2019 | 4000055560 | 2019-02-02
1062 | DR2725_19011765 | 4119 |  | 2725 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101853 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502911 | 29-03-2019 | 4000055560 | 2019-02-02
1063 | DR2725_19011766 | 4132 |  | 2725 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101853 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502911 | 29-03-2019 | 4000055560 | 2019-02-02
1064 | DR2725_19000469 | 4303 |  | 2726 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101852 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502910 | 29-03-2019 | 4000055560 | 2019-02-02
1065 | DR2725_19000470 | 4002 |  | 2726 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101852 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502910 | 29-03-2019 | 4000055560 | 2019-02-02
1066 | DR2725_19000471 | 4085 |  | 2726 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101852 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502910 | 29-03-2019 | 4000055560 | 2019-02-02
1067 | DR2725_19000472 | 4072 |  | 2726 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101852 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502910 | 29-03-2019 | 4000055560 | 2019-02-02
1068 | DR2725_19000473 | 4149 |  | 2726 | 2019-03-04 | 12C | 0.5 | OFC | SINGLE MODE | ARM | NO VOLT | EDN OPTICAL FIBER | F12-0.5 | 12Cx0.5Sqmm OFC SINGLE MODE ARM EDN OPTICAL FIBER CABLE | YARD-12 (BACK SIDE OF CWPH) | 101852 | 29-03-2019 | MP19HA-2375 | BIRLA CABLE LIMITED | 1841502910 | 29-03-2019 | 4000055560 | 2019-02-02
1069 | DR2685-3 | 976 |  | 2685 | 2019-12-03 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1070 | DR2685-4 | 981 |  | 2685 | 2019-12-03 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1071 | DR2685-8 | 986 |  | 2685 | 2019-12-03 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1072 | DR2685-1 | 981 |  | 2685 | 2019-12-03 | 03C | 50 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q050 | 03Cx050Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1073 | DR2685-1 | 734 |  | 2685 | 2019-12-03 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1074 | DR2685-2 | 746 |  | 2685 | 2019-12-03 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1075 | DR2685-3 | 743 |  | 2685 | 2019-12-03 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1076 | DR2685-4 | 732 |  | 2685 | 2019-12-03 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1077 | DR2685-5 | 743 |  | 2685 | 2019-12-03 | 03C | 240 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q240 | 03Cx240Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1078 | DR2685-1 | 987 |  | 2685 | 2019-12-03 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1079 | DR2685-2 | 972 |  | 2685 | 2019-12-03 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1080 | DR2685-3 | 985 |  | 2685 | 2019-12-03 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1081 | DR2685-4 | 982 |  | 2685 | 2019-12-03 | 3.5C | 25 | AL | XLPE-FRLS | ARM | 1.1 KV | PEM LT POWER | D3HN025 | 3.5Cx025Sqmm AL XLPE-FRLS ARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1082 | DR2685-2 | 1009.5 |  | 2685 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1083 | DR2685-3 | 982.5 |  | 2685 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1084 | DR2685-4 | 993 |  | 2685 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1085 | DR2685-6 | 1000 |  | 2685 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1086 | DR2685-9 | 1005 |  | 2685 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1087 | DR2685-10 | 954 |  | 2685 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059956 | 2019-03-03 | OR14R-3068 | SPECIAL CABLES | 528 | 2019-03-03
1088 | DR2687-1 | 735 |  | 2687 | 2019-12-03 | 01C | 400 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D01Q400 | 01Cx400Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1089 | DR2687-1 | 1001.5 |  | 2687 | 2019-12-03 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1090 | DR2687-2 | 984.5 |  | 2687 | 2019-12-03 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1091 | DR2687-3 | 989 |  | 2687 | 2019-12-03 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1092 | DR2687-4 | 1001 |  | 2687 | 2019-12-03 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1093 | DR2687-5 | 996 |  | 2687 | 2019-12-03 | 02C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q010 | 02Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1094 | DR2687-1 | 989 |  | 2687 | 2019-12-03 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1095 | DR2687-2 | 986 |  | 2687 | 2019-12-03 | 02C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q025 | 02Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1096 | DR2687-1 | 976 |  | 2687 | 2019-12-03 | 02C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q095 | 02Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1097 | DR2687-2 | 986 |  | 2687 | 2019-12-03 | 02C | 95 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D02Q095 | 02Cx095Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1098 | DR2687-1 | 993 |  | 2687 | 2019-12-03 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1099 | DR2687-2 | 993 |  | 2687 | 2019-12-03 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1100 | DR2687-5 | 975.5 |  | 2687 | 2019-12-03 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1101 | DR2687-7 | 997.5 |  | 2687 | 2019-12-03 | 03C | 25 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q025 | 03Cx025Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1102 | DR2687-1 | 735 |  | 2687 | 2019-12-03 | 03C | 150 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03Q150 | 03Cx150Sqmm AL XLPE-FRLS UNARM PEM HT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1103 | DR2687-1 | 751 |  | 2687 | 2019-12-03 | 3.5C | 185 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ185 | 3.5Cx185Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1104 | DR2687-2 | 736 |  | 2687 | 2019-12-03 | 3.5C | 185 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ185 | 3.5Cx185Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1105 | DR2687-3 | 750 |  | 2687 | 2019-12-03 | 3.5C | 185 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D3HQ185 | 3.5Cx185Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1106 | DR2687-1 | 979 |  | 2687 | 2019-12-03 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1107 | DR2687-2 | 981 |  | 2687 | 2019-12-03 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1108 | DR2687-3 | 974 |  | 2687 | 2019-12-03 | 04C | 10 | AL | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D04Q010 | 04Cx010Sqmm AL XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1109 | DR2687-1 | 997 |  | 2687 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1110 | DR2687-5 | 1015 |  | 2687 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1111 | DR2687-7 | 1011 |  | 2687 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1112 | DR2687-8 | 998 |  | 2687 | 2019-12-03 | 03C | 2.5 | CU | XLPE-FRLS | UNARM | 1.1 KV | PEM LT POWER | D03L2.5 | 03Cx2.5Sqmm CU XLPE-FRLS UNARM PEM LT POWER CABLE | YARD-12 (BACK SIDE OF CWPH) | 149059960 | 2019-03-03 | CG07CA-5215 | SPECIAL CABLES | 529 | 2019-03-03
1113 | DR2904-1 | 1012 |  | 2904 | 2019-06-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1114 | DR2904-2 | 1030 |  | 2904 | 2019-07-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1115 | DR2904-3 | 1012 |  | 2904 | 2019-08-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1116 | DR2904-4 | 1029 |  | 2904 | 2019-09-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1117 | DR2904-5 | 1020 |  | 2904 | 2019-10-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1118 | DR2904-6 | 1030 |  | 2904 | 2019-11-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1119 | DR2904-7 | 1020 |  | 2904 | 2019-12-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1120 | DR2904-8 | 1003 |  | 2904 | 13-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1121 | DR2904-9 | 1000 |  | 2904 | 14-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1122 | DR2904-10 | 1000 |  | 2904 | 15-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1123 | DR2904-11 | 1019 |  | 2904 | 16-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1124 | DR2904-12 | 1009 |  | 2904 | 17-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1125 | DR2904-13 | 1003 |  | 2904 | 18-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1126 | DR2904-14 | 1014 |  | 2904 | 19-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1127 | DR2904-15 | 1020 |  | 2904 | 20-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1128 | DR2904-16 | 1019 |  | 2904 | 21-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1129 | DR2904-17 | 1010 |  | 2904 | 22-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1130 | DR2904-18 | 1022 |  | 2904 | 23-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1131 | DR2904-19 | 1013 |  | 2904 | 24-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1132 | DR2904-20 | 1000 |  | 2904 | 25-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1133 | DR2904-21 | 1011 |  | 2904 | 26-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1134 | DR2904-22 | 1030 |  | 2904 | 27-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1135 | DR2904-23 | 1010 |  | 2904 | 28-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1136 | DR2904-24 | 1010 |  | 2904 | 29-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1137 | DR2904-25 | 1030 |  | 2904 | 30-06-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1138 | DR2904-26 | 1028 |  | 2904 | 2019-01-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1139 | DR2904-27 | 1024 |  | 2904 | 2019-02-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1140 | DR2904-28 | 1025 |  | 2904 | 2019-03-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1141 | DR2904-29 | 1019 |  | 2904 | 2019-04-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1142 | DR2904-30 | 1009 |  | 2904 | 2019-05-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1143 | DR2904-31 | 1001 |  | 2904 | 2019-06-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1144 | DR2904-32 | 1019 |  | 2904 | 2019-07-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1145 | DR2904-33 | 1002 |  | 2904 | 2019-08-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1146 | DR2904-34 | 1027 |  | 2904 | 2019-09-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1147 | DR2904-35 | 1001 |  | 2904 | 2019-10-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1148 | DR2904-36 | 1004 |  | 2904 | 2019-11-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1149 | DR2904-37 | 1026 |  | 2904 | 2019-12-07 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1150 | DR2904-38 | 1030 |  | 2904 | 13-07-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1151 | DR2904-39 | 1020 |  | 2904 | 14-07-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1152 | DR2904-40 | 1020 |  | 2904 | 15-07-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1153 | DR2904-41 | 1017 |  | 2904 | 16-07-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1154 | DR2904-42 | 1008 |  | 2904 | 17-07-2019 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1016 | 30-05-2019 | UP42AT-5714 | ELKAY TELELINKS LTD | 100087 | 30-05-2019 | T718A00460 | 31-12-2018
1155 | DR2910-43 | 1011 |  | 2910 | 2019-02-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1156 | DR2910-44 | 1007 |  | 2910 | 2019-03-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1157 | DR2910-45 | 1016 |  | 2910 | 2019-04-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1158 | DR2910-46 | 1000 |  | 2910 | 2019-05-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1159 | DR2910-47 | 1030 |  | 2910 | 2019-06-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1160 | DR2910-48 | 1024 |  | 2910 | 2019-07-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1161 | DR2910-49 | 1023 |  | 2910 | 2019-08-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1162 | DR2910-50 | 1030 |  | 2910 | 2019-02-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1163 | DR2910-51 | 1030 |  | 2910 | 2019-03-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1164 | DR2910-52 | 1028 |  | 2910 | 2019-04-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1165 | DR2910-53 | 1030 |  | 2910 | 2019-05-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1166 | DR2910-54 | 1029 |  | 2910 | 2019-06-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1167 | DR2910-55 | 1017 |  | 2910 | 2019-07-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1168 | DR2910-56 | 1023 |  | 2910 | 2019-08-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1169 | DR2910-57 | 1030 |  | 2910 | 2019-02-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1170 | DR2910-58 | 1023 |  | 2910 | 2019-03-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1171 | DR2910-59 | 1018 |  | 2910 | 2019-04-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1172 | DR2910-60 | 1003 |  | 2910 | 2019-05-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1173 | DR2910-61 | 1003 |  | 2910 | 2019-06-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1174 | DR2910-62 | 1015 |  | 2910 | 2019-07-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1175 | DR2910-63 | 1023 |  | 2910 | 2019-08-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1176 | DR2910-64 | 1021 |  | 2910 | 2019-02-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1177 | DR2910-65 | 1018 |  | 2910 | 2019-03-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1178 | DR2910-66 | 1030 |  | 2910 | 2019-04-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1179 | DR2910-67 | 1030 |  | 2910 | 2019-05-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1180 | DR2910-68 | 1030 |  | 2910 | 2019-06-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1181 | DR2910-69 | 1026 |  | 2910 | 2019-07-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1182 | DR2910-70 | 1030 |  | 2910 | 2019-08-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1183 | DR2910-71 | 1025 |  | 2910 | 2019-02-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1184 | DR2910-72 | 1028 |  | 2910 | 2019-03-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1185 | DR2910-73 | 1015 |  | 2910 | 2019-04-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1186 | DR2910-74 | 1030 |  | 2910 | 2019-05-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1187 | DR2910-75 | 1004 |  | 2910 | 2019-06-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1188 | DR2910-76 | 1018 |  | 2910 | 2019-07-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1189 | DR2910-77 | 1011 |  | 2910 | 2019-08-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1190 | DR2910-78 | 1018 |  | 2910 | 2019-02-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1191 | DR2910-79 | 1018 |  | 2910 | 2019-03-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1192 | DR2910-80 | 1010 |  | 2910 | 2019-04-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1193 | DR2910-81 | 1001 |  | 2910 | 2019-05-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1194 | DR2910-82 | 1011 |  | 2910 | 2019-06-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1195 | DR2910-83 | 1015 |  | 2910 | 2019-07-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1196 | DR2910-84 | 1015 |  | 2910 | 2019-08-06 | 03C | 1.5 | CU | XLPE-FRLS | ARM | 1.1 KV | HYD CONTROL | D03J1.5 | 03Cx1.5Sqmm CU XLPE-FRLS ARM HYD CONTROL FIRE CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 1017 | 30-05-2019 | HR69C-6037 | ELKAY TELELINKS LTD | 100088 | 30-05-2019 | T718A00460 | 31-12-2018
1197 | DR3111-12001 | 1033 |  | 3111 | 2019-10-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1198 | DR3111-12002 | 1053 |  | 3111 | 2019-10-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1199 | DR3111-12003 | 1021 |  | 3111 | 2019-10-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1200 | DR3111-12004 | 1029 |  | 3111 | 2019-10-12 | 05C | 2.5 | CU | PVC-FRLS | UNARM | 1.1 KV | TRY POWER | D05C2.5 | 05Cx2.5Sqmm CU PVC-FRLS UNARM TRY LT POWER CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1201 | DR3111-11571 | 1003 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1202 | DR3111-11572 | 1020 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1203 | DR3111-11573 | 1023 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF EXITING CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1204 | DR3111-11574 | 1021 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1205 | DR3111-11575 | 1022 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1206 | DR3111-11576 | 1020 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1207 | DR3111-11577 | 1003 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1208 | DR3111-11578 | 1020 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1209 | DR3111-11579 | 1017 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1210 | DR3111-11580 | 1017 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1211 | DR3111-11581 | 1032 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1212 | DR3111-11582 | 1014 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1213 | DR3111-11583 | 983 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1214 | DR3111-11584 | 1020 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1215 | DR3111-11585 | 1021 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1216 | DR3111-11586 | 1040 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1217 | DR3111-11587 | 1011 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1218 | DR3111-11588 | 1005 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1219 | DR3111-11589 | 1014 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1220 | DR3111-11590 | 1018 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1221 | DR3111-11591 | 1022 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1222 | DR3111-11592 | 1023 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1223 | DR3111-11593 | 1013 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1224 | DR3111-11601 | 1021 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1225 | DR3111-11602 | 1036 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1226 | DR3111-11603 | 1025 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019
1227 | DR3111-11604 | 1046 |  | 3111 | 2019-10-12 | 02C | 1.5 | CU | PVC-FRLS | UNARM | 1.1 KV | PEM CONTROL | D02C1.5 | 02Cx1.5Sqmm CU PVC-FRLS UNARM PEM CONTROL CABLE | YARD-12 (BACK SIDE OF CWPH) | 13116 | 30-11-2019 | CG07AB-5267 | KEC INTERNATIONAL LTD | IN1924002504 | 30-11-2019 | P-149/17 | 16-09-2019