## Dynamic HP Joint report
SNO | JOINT NO | Size | Material | WELDER NO | FITUP DATE | PRE-HEATING | WELDING DATE | RT DATE | RT REPORT NO. | OBSERVATION | SR DATE | CHART NO | AFTER REPAIR | CHART NO. | REMARKS
1 | WS-98-J-A-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-10-31 | 220°C | 2019-10-31 | 2019-11-12 | GTC/PMPL/1518 | ACC | 2019-10-31 | CTH/PMPL/4407
2 | WS-98-J-B-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-04 | 220°C | 2019-11-04 | 2019-11-21 | GTC/PMPL/1540 | ACC | 2019-11-04 | CTH/PMPL/4416
3 | WS-98-J-C-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-04 | 220°C | 2019-11-04 | 2019-12-05 | GTC/PMPL/1576 | ACC | 2019-11-04 | CTH/PMPL/4416
4 | WS-98-J-D-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-04 | 220°C | 2019-11-04 | 2019-11-12 | GTC/PMPL/1518 | ACC | 2019-11-04 | CTH/PMPL/4416
5 | WS-98-J-E-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-04 | 220°C | 2019-11-04 | 2019-12-06 | GTC/PMPL/1581 | ACC | 2019-11-04 | CTH/PMPL/4416
6 | WS-98-J-F-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-04 | 220°C | 2019-11-04 | 2019-11-12 | GTC/PMPL/1518 | REP | 2019-11-04 | CTH/PMPL/4417
7 | WS-98-J-G-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-04 | 220°C | 2019-11-04 | 2019-12-14 | GTC/PMPL/1591 | ACC | 2019-11-04 | CTH/PMPL/4417
8 | WS-98-J-H-01 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-04 | 220°C | 2019-11-04 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-04 | CTH/PMPL/4417
9 | WS-98-J-A-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-10-31 | 220°C | 2019-10-31 |  |  |  | 2019-10-31 | CTH/PMPL/4407
10 | WS-98-J-B-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-14 | 220°C | 2019-11-14 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-14 | CTH/PMPL/4436
11 | WS-98-J-C-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-16 | 220°C | 2019-11-16 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-16 | CTH/PMPL/4444
12 | WS-98-J-D-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-16 | 220°C | 2019-11-16 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-16 | CTH/PMPL/4444
13 | WS-98-J-E-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-16 | 220°C | 2019-11-16 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-16 | CTH/PMPL/4444
14 | WS-98-J-F-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-16 | 220°C | 2019-11-16 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-16 | CTH/PMPL/4445
15 | WS-98-J-G-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-16 | 220°C | 2019-11-16 | 2019-12-14 | GTC/PMPL/1591 | ACC | 2019-11-16 | CTH/PMPL/4445
16 | WS-98-J-H-02 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-16 | 220°C | 2019-11-16 | 2019-12-06 | GTC/PMPL/1581 | ACC | 2019-11-16 | CTH/PMPL/4445
17 | WS-98-J-A-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-10-31 | 220°C | 2019-10-31 | 2019-12-06 | GTC/PMPL/1581 | ACC | 2019-10-31 | CTH/PMPL/4407
18 | WS-98-J-B-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-14 | 220°C | 2019-11-14 | 2019-12-06 | GTC/PMPL/1581 | ACC | 2019-11-14 | CTH/PMPL/4436
19 | WS-98-J-C-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-19 | 220°C | 2019-11-19 | 2019-12-05 | GTC/PMPL/1576 | ACC | 2019-11-19 | CTH/PMPL/4446
20 | WS-98-J-D-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-98 | 2019-11-22 | 220°C | 2019-11-22 | 2019-12-14 | GTC/PMPL/1591 | ACC | 2019-11-22 | CTH/PMPL/4456
21 | WS-98-J-E-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-98 | 2019-11-22 | 220°C | 2019-11-22 | 2019-12-14 | GTC/PMPL/1591 | REP | 2019-11-22 | CTH/PMPL/4456 | 2019-12-21 | CTH/PMPL/4541 | CRW
22 | WS-98-J-F-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-98 | 2019-11-22 | 220°C | 2019-11-22 | 2019-12-05 | GTC/PMPL/1576 | ACC | 2019-11-22 | CTH/PMPL/4456
23 | WS-98-J-G-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-98 | 2019-11-22 | 220°C | 2019-11-22 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-22 | CTH/PMPL/4456
24 | WS-98-J-H-03 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-98 | 2019-11-22 | 220°C | 2019-11-22 | 2019-12-05 | GTC/PMPL/1576 | ACC | 2019-11-22 | CTH/PMPL/4456
25 | WS-98-J-A-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-10-31 | 220°C | 2019-10-31 | 2019-11-01 | SNS/PMPL/2025 | ACC | 2019-10-31 | CTH/PMPL/4407
26 | WS-98-J-B-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-14 | 220°C | 2019-11-14 | 2019-12-05 | GTC/PMPL/1576 | GRIND & SHOW | 2019-11-14 | CTH/PMPL/4436
27 | WS-98-J-C-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-19 | 220°C | 2019-11-19 | 2019-12-05 | GTC/PMPL/1576 | ACC | 2019-11-19 | CTH/PMPL/4446
28 | WS-98-J-D-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-23 | 220°C | 2019-11-23 |  |  |  | 2019-11-23 | CTH/PMPL/4463
29 | WS-98-J-E-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-26 | 220°C | 2019-11-26 | 2019-11-29 | GTC/PMPL/1565 | ACC | 2019-11-26 | CTH/PMPL/4475
30 | WS-98-J-F-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-26 | 220°C | 2019-11-26 | 2019-11-29 | GTC/PMPL/1565 | ACC | 2019-11-26 | CTH/PMPL/4475
31 | WS-98-J-G-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-26 | 220°C | 2019-11-26 | 2019-12-14 | GTC/PMPL/1591 | ACC | 2019-11-26 | CTH/PMPL/4475
32 | WS-98-J-H-04 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-26 | 220°C | 2019-11-26 | 2019-11-29 | GTC/PMPL/1565 | ACC | 2019-11-26 | CTH/PMPL/4475
33 | WS-98-J-A-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-05 | 220°C | 2019-11-05 | 2019-12-06 | GTC/PMPL/1581 | ACC | 2019-11-05 | CTH/PMPL/4422
34 | WS-98-J-B-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-14 | 220°C | 2019-11-14 | 2019-12-05 | GTC/PMPL/1576 | DRS | 2019-11-14 | CTH/PMPL/4436
35 | WS-98-J-C-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-19 | 220°C | 2019-11-19 | 2019-11-26 | GTC/PMPL/1556 | ACC | 2019-11-19 | CTH/PMPL/4446
36 | WS-98-J-D-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-97 | 2019-11-23 | 220°C | 2019-11-23 | 2020-01-25 | GTC/PMPL/1648 |  | 2019-11-23 | CTH/PMPL/4463
37 | WS-98-J-E-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-27 | 220°C | 2019-11-27 | 2019-11-29 | GTC/PMPL/1565 | ACC | 2019-11-27 | CTH/PMPL/4480
38 | WS-98-J-F-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-27 | 220°C | 2019-11-27 | 2019-12-14 | GTC/PMPL/1591 | REP | 2019-11-27 | CTH/PMPL/4480 | 2019-12-21 | CTH/PMPL/4541 | CRW
39 | WS-98-J-G-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-27 | 220°C | 2019-11-27 | 2019-11-29 | GTC/PMPL/1565 | ACC | 2019-11-27 | CTH/PMPL/4480 | 2020-02-09 | CTH/PMPL/R.S-243 | RE-SR
40 | WS-98-J-H-05 | 44.5X8.1 | SA213 T91 + SA213 T91 | HP-28 | 2019-11-27 | 220°C | 2019-11-27 | 2019-11-29 | GTC/PMPL/1565 | ACC | 2019-11-27 | CTH/PMPL/4480
Formulas:
FITUP DATE = [WELDING DATE]
WELDING DATE = [SR DATE]

## Hardness Protocols
|  | INSTRUMENT REGN NO. |  |  | HARDNESS TESTER
|  | DATE OF INSPECTION |  |  | 31.01.2020 |  |  | Report No: HT/CP/227
|  | DRAWING/DOCUMENT REF. |  |  | 1-12-178-01646/47
PSER
PGMA:-12-178 |  |  |  | MATERIAL :-SA335 P91
JOINT NO: | WS-92, J-02
SYSTEM: | LINK PIPE
Equipment Used: |  | HARDNESS TESTER |  | Surface condition: SMOOTH
NEXT DUE DATE: 10/09/20 |  |  |  | MAKE: | TIME |  | MODEL NO: TH 110
HARDNESS VALUE
LOCATION | PM1 |  |  |  | WELD |  |  |  | PM2
READINGS | 1 | 2 | 3 | AVG | 1 | 2 | 3 | AVG | 1 | 2 | 3 | AVG
0° | 197 | 201 | 192 | 196.6667 | 224 | 211 | 245 | 226.6667 | 208 | 193 | 178 | 193
90° | 213 | 205 | 196 | 204.6667 | 236 | 228 | 240 | 234.6667 | 195 | 201 | 185 | 193.6667
180° | 186 | 198 | 207 | 197 | 248 | 239 | 255 | 247.3333 | 175 | 185 | 199 | 186.3333
270° | 195 | 201 | 209 | 201.6667 | 265 | 229 | 258 | 250.6667 | 210 | 196 | 193 | 199.6667
Note:- The maximum allowable Hardness at weld and parent metal shall be 300HV
RESULT:- ACCEPTED
|  | PMPL |  |  | BHEL |  |  | NPGCL(ME) |  | NPGCL(FQA)
NAME
SIGNATURE
DATE

## HP welder Performance report
POWER MECH PROJECTS LIMITED
NABINAGAR,NPGCL,BIHAR# 3(Boiler)
WELDER PERFORMANCE REPORT FROM 01.02.2020 TO 29.02.2020
SL. No. | WELDER NAME | IBR CERTIFICATE NO: | WELDER CODE | RT TAKEN in SEP'19 | TOTAL REPAIR JOINTS | REPAIR % | REMARKS
1 | SANJAY PRAJAPATI | JH/W/01.198.A/18-19 | PMPL/HP-10 | 3 | 0 | 0 | LEFT SITE
2 | AKILESH GUPTHA | JH/W/11/13/25/13-14 | PMPL/HP-28 | 89 | 6 | 6.7416
3 | AJIT KUMAR YADAV | JH/W/PSD/09.21.B/18-19 | PMPL/HP-87 | 19 | 1 | 5.2632
4 | VIKAS SINGH | BR/W/48/15-16 | PMPL/HP-97 | 244 | 14 | 5.7377
5 | PRAMOD CHOUDARY | JH/W/JSR/13.157.A/18-19 | PMPL/HP-98 | 19 | 5 | 26.3158 | LEFT SITE
TOTAL |  |  |  | 374 | 26

## Calibaration of instruments
INSTRUMENTS CALIBRATION DETAILS,NPGCL,NABINAGAR (POWERMECH)
S.NO: | NAME OF THE INSTRUMENT | INSTRUMENT SERIAL NO: | CALIBRATION DATE | DUE DATE | REMARKS
1 | DIG.TEMP.CONTROLLER OF MOTHER OVEN | PMPL/ABFPL/BO-02 | 2019-01-10 | 2020-01-09
2 | DIG.TEMP.CONTROLLER OF MOTHER OVEN | PMPL/DMO-01 | 2019-01-10 | 2020-01-09
3 | DIG.TEMP.CONTROLLER OF MOTHER OVEN | PMPL/DMO-02 | 2019-01-10 | 2020-01-09
4 | DIG.TEMP.CONTROLLER OF MOTHER OVEN | PMPL/DMO-03 | 2019-01-10 | 2020-01-09
5 | DIG.TEMP.CONTROLLER OF MOTHER OVEN | PMPL/DMO-04 | 2019-01-10 | 2020-01-09
6 | DIG.TEMP.CONTROLLER OF MOTHER OVEN | PMPL/DMO-05 | 2019-01-10 | 2020-01-09
7 | DIAL INDICATOR | XJJ3844 | 2019-10-22 | 2020-10-21
8 | DIAL INDICATOR | XJJ4653 | 2019-10-22 | 2020-10-21
9 | DIAL INDICATOR | NRE935 | 2019-10-22 | 2020-10-21
10 | DIAL INDICATOR | UKM449 | 2019-10-22 | 2020-10-21
11 | DIAL INDICATOR | NRE20468 | 2019-10-22 | 2020-10-21
12 | DIAL INDICATOR | NTC977 | 2019-10-22 | 2020-10-21
13 | DIAL INDICATOR | NRE20465 | 2019-10-22 | 2020-10-21
14 | SLIPGUAGE | 1800503 | 2019-04-04 | 2020-04-02
15 | TORQUE WRENCH | 261 | 2019-10-22 | 2020-10-21
16 | TORQUE WRENCH | GTW-100R | 2019-10-22 | 2020-10-21
17 | MASTER LEVEL | 4946 | 2019-05-28 | 2020-08-27
18 | MASTER LEVEL | 4948 | 2019-05-28 | 2020-08-27

## Summary sheet of HP joints
3X 660 MW, NPGC Nabinagar BOILER#-III Date:- 19-03-20
Sl no. | System | Total No. of joints. | TOTAL WELDING COMPLETED | WELDING BALANCE JOINTS | RT Scope as per WELDED JOINTS | RT Taken | RT Balance as per WELDED JOINTS | Accepted Joints | Total Repair | Rep. Bal. | Repair Accepted | Re- Repair | Retake/DRS/others | BAL Retake/DRS/others | SR Scope as per WEDED JOINTS | SR done | SR Bal. as per WEDED JOINTS | Hardness Scope as per SR done | Hardness. Done | Hardness. Balance as per SR COMPLETED
1 | Superheater NDHT | 8028 | 7533 | 495 | 5020 | 4981 | 39 | 4956 | 223 | 25 | 198 | 8 | 362 | 61 | 4527 | 4527 | 0 | 4525 | 4525 | 0
2 | Reheater | 7169 | 6605 | 564 | 5201 | 5171 | 30 | 5133 | 369 | 38 | 331 | 15 | 157 | 29 | 4314 | 4314 | 0 | 4314 | 4314 | 0
| Total:- | 15197 | 14138 | 1059 | 10221 | 10152 | 69 | 10089 | 592 | 63 | 529 | 23 | 519 | 90 | 8841 | 8841 | 0 | 8839 | 8839 | 0
PIPING#-III
Sl no. | System | Total No. of joints. | TOTAL WELDING COMPLETED | WELDING BALANCE JOINTS | RT Scope as per WELDED JOINTS | RT Taken | RT Balance as per WELDED JOINTS | Accepted Joints | Total Repair | Rep. Bal. | Repair Accepted | Re- Repair | Retake/DRS/others | BAL Retake/DRS/others | SR Scope as per WEDED JOINTS | SR done | SR Bal. as per WEDED JOINTS | Hardness Scope as per WELDED JOINTS | Hardness. Done | Hardness. Balance as per WELDED JOINT
1 | MS LINE | 179 | 153 | 26 | 153 | 148 | 5 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 153 | 0 | 153 | 148 | 5
2 | HRH | 91 | 83 | 8 | 83 | 64 | 19 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 82 | 1 | 82 | 62 | 20
3 | LPBP | 58 | 58 | 0 | 58 | 54 | 4 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 58 | 0 | 58 | 46 | 12
4 | SAFETY VALVE | 16 | 12 | 4 | 12 | 7 | 5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | 0 | 0 | 0
5 | CRH | 108 | 92 | 16 | 92 | 89 | 3 | 85 | 14 | 4 | 10 | 0 | 5 | 4 | 92 | 71 | 21 | 2.13 | 0 | 2.13
6 | HPBP | 25 | 23 | 2 | 23 | 23 | 0 | 23 | 8 | 0 | 8 | 0 | 0 | 0 | 23 | 23 | 0 | 23 | 0 | 23
TOTAL |  | 477 | 421 | 56 | 421 | 385 | 36 | 381 | 22 | 4 | 18 | 0 | 5 | 4 | 421 | 387 | 34 | 318.13 | 256 | 62.13

## Plan-main boiler & piping
DRAINABLE HYDRO TEST PLAN OF UNIT #3
DRAINABLE SUPERHEATER SYSTEM
Sl No | Description | Joints | Status (Bal Joints) | Start Date | Finish Date | Remarks
1 | S-24 links | 20 | 1 | U/P | 15.10.2018
2 | S-2 + S-03 | 206 | 4 | 23.10.2018 | 24.10.2018
3 | Roof panel + Roof loose tubes | 204 | 17 | U/P | 10.11.2018
4 | Roof panel + Roof loose tubes | 204 | 18 | U/P | 10.11.2018
5 | S-10 links | 9 | 0 |  | COMPLETE | Welding U/P
6 | Screen Tubes+ Outlet Header (S-16+S-22) | 204 | 12 | 11.11.2018 | 20.11.2018 | open order materials (12-805)
7 | Screen tube + Front Panel (S15 + S16) | 204 | 24 | 11.11.2018 | 20.11.2018 | 12 joints left and will be done after receiving open order materials
8 | IInd Pass Ring header + Corner loose tubes | 112 | 5 | 15.11.2018 | 20.11.2018 | 36 joints shall be done after receipt of open order items (Sl No-16) for approach
9 | E-09 panel opening | 44 | 0 | 07.10.2018 | 16.10.2018
10 | R-03 panel opening | 44 | 0 | 20.10.2018 | 29.10.2018
11 | BP Front O/L header + BP roof panel | 204 | 0 | U/P | 05.10.2018
12 | Eco coil hanger tubes | 408 | 28 | 11.11.2018 | 20.11.2018 | shall be started after receipt of open order items
13 | Eco header hanger tubes (S-19B) | 280 | 45 | U/P | 06.10.2018 | 5 tubes in open order
14 | LTRH header hanger tubes (S-19A) | 280 | 160 | U/P | 28.10.2018
15 | S-25 A & B links with blanking | 10 | 6 | 14.10.2018 | 05.11.2018
16 | S-18 & S-19 tubes + Ring header | 488 | 24 | 11.11.2018 | 25.11.2018 | open order items
| TOTAL |  | 344
ECONOMISER SYSTEM
Sl No | Description | Joints | Status (Bal Joints) | Start Date | Finish Date | Remarks
1 | Eco O/L links | 22 | 0 | U/P | 27.10.2018
2 | Eco I/L Links | 18 | 0 | U/P | 09.11.2018 | preassembly U/P
3 | Eco I/L header term tubes + Eco coils | 812 | 0 | U/P | 12.10.2018
4 | Eco O/L term tubes + Eco Coils | 812 | 0 | 13.10.2015 | 15.10.2018 | 14 tubes open order, 28 joints to be done after receipt of open order items
| TOTAL |  | 0
CIRCULATION SYSTEM
Sl No | Description | Joints | Status (Bal Joints) | Start Date | Finish Date | Remarks
1 | Furnace side riser |  | 6 | U/P | 30.10.2018 | fit up balance, materials were received against MDR so 2 no of joints have increased
3 | Corner #2 | 325 | 86 | 25.10.2018 | 07.11.2018 | including upper corner panel, 2 tubes open order item
4 | Corner #3 | 325 | 82 | 22.10.2018 | 25.10.2018
5 | Burner Panel #1 | 604 | 53 | U/P | 14.10.2018
6 | Burner Panel #2 | 604 | 98 | U/P | 15.10.2018
7 | Burner Panel #3 | 604 | 189 | U/P | 07.11.2018
8 | Burner Panel #4 | 604 | 24 | U/P | 11.10.2018
9 | Hopper #1 | 320 | 22 |  | 10.11.2018 | will be done with ring header tubes
10 | Hopper #2 | 546 | 100 | 15.10.2018 | 26.10.2018 | open order materials approx 21 no tubes
11 | Hopper #3 | 320 | 230 | U/P | 15.10.2018 | open order materials approx 21 no tubes
12 | Hopper #4 | 546 | 16 |  | 10.11.2018 | will be done with ring header tubes
13 | Bottom Ring Header + term Tubes | 516 | 182 |  | 10.11.2018 | 81 tube open order, 162 joints to be done after receipt of open order items. Lug plate also required against open order for suspension system of S-Panel
14 | Ring Hdr Term tubes + panel | 516 | 512 | U/P | 10.11.2018
| TOTAL |  | 1600
| Downcomer System (incl HWL piping) |  | 20 | U/P | 27.10.2018 | 10 joints fitup balance
| TOTAL |  | 1964
Trim Piping
Sl No | Description | Approx Joints | Status (Bal Joints) | Start Date | Finish Date | Remarks
1 | Eco O/L Header Vent | 40 | 40 | 13.10.2018 | 28.10.2018
2 | S-25 Link vent | 30 | 30 | 06.11.2018 | 16.11.2018 | After completion of S-25 Link
3 | F-01 Drain | 25 | 15 | U/P | 12.10.2018
4 | Eco Drain (LHS & RHS) | 20 | 10 | U/P | 30.10.2018
5 | Iind Pass Ring Header Drain | 25 | 15 | U/P | 25.10.2018
6 | Intermmediate Header Drain | 60 | 60 | 26.10.2018 | 15.11.2018
7 | Start Up Sytem Drains | 30 | 30 | 28.10.2018 | 08.11.2018
| Total |  | 200
| Air filling prior to Hydro Test |  |  |  | 30.11.2018 | 1. Subject to availabilty of materials against open order, MDR & SAR by 10.11.2018. (124 no of tube in Ist Pass & 64 nos of tube in IInd Pass) 2. As per dispatch schedule from trichy all materials shall be dispatched by 30.10.2018. 3. Approx 20 days job required for completion of 400 joints of open order and its fins welding & SR
| Hydro Test |  |  |  | 15.12.2018
CRITICAL PIPING
Sl No | Description | Joints | Status (Bal Joints) | Start Date | Finish Date | Remarks
1 | MS Piping upto stop valve | 20 | 10 | U/P |  | 1. Preassembly jobs are U/P 2. Work hold in CD bay area due to non availability of approach for erection of piping support structure 3. PGMA-80304 DU-17 Qty-6 required which could be preassembled. 4. PGMA-80310 DU-70 Qty-01 eccentric reducer, HRH piping material
2 | MS Piping from Stop valve to ESV | 67 | 10 | U/P
3 | HRH Piping | 87 | 8 | U/P
4 | CRH Piping | 103 | 15 | U/P
5 | MS to Aux PRDS | 21 | 3
6 | LP Bypass | 62 | 24
7 | HP Bypass | 30 | 10
| Total |  | 80

## OPEN ORDER
CUST NO | PGMA | DU | DESCRIPTION | QTY | UOM | WEIGHT (KG) | REMARKS | PRIORITY REQUIREMENT
1717 | 11074 | 2 | TUBE D50.8X6.1; (S-39TI-01) | 1 | NO | 14.1 | INS-89/ Open order, Date-03/01/2020 | 1ST PRIORITY
1717 | 11074 | 4 | TUBE D44.5X5.6; (S-39TI-03) | 1 | NO | 19.88 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 5 | TUBE D44.5X5.6; (S-39TI-04) | 2 | NO | 21.04 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 6 | TUBE D44.5X5.6; (S-39TI-05) | 3 | NO | 31.56 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 7 | TUBE D44.5X5.6; (S-39TI-06) | 2 | NO | 39.76 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 8 | TUBE D44.5X5.6; (S-39TI-07) | 1 | NO | 10.1 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 10 | SH.FINISH CROSSOVER TUBES (S-39TO-01) | 3 | NO | 232.87 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 11 | SH.FINISH CROSSOVER TUBES (S-39TO-02) | 2 | NO | 45.14 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 12 | SH.FINISH CROSSVER TUBES (S-39TO-03) | 0 | NO | 280.17 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 13 | SH.FINISH CROSSOVER TUBES (S-39TO-04) | 1 | NO | 107.08 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 15 | SH.FINISH CROSSOVER TUBES (S-39TO-06) | 3 | NO | 168.85 | INS-89/ Open order, Date-03/01/2020
1717 | 11074 | 17 | SH.FINISH CROSSOVER TUBES (S-39TO-08) | 3 | NO | 187.85 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 2 | BENT TUBE(S40TO-1-1) | 2 | NO | 46.08 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 3 | BENT TUBE(S40TO-1-2) | 9 | NO | 165.06 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 4 | BENT TUBE(S40TO-1-3) | 2 | NO | 37.64 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 5 | BENT TUBE(S40TO-1-4) | 29 | NO | 569.56 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 7 | BENT TUBE(S40TO-1-6) | 1 | NO | 17.81 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 8 | BENT TUBE(S40TO-1-7) | 1 | NO | 17.33 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 9 | BENT TUBE(S40TO-1-8) | 1 | NO | 17.21 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 10 | BENT TUBE(S40TO-4-1) | 1 | NO | 23.16 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 11 | BENT TUBE(S40TO-4-2) | 1 | NO | 18.44 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 12 | BENT TUBE(S40TO-4-3) | 1 | NO | 18.91 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 13 | BENT TUBE(S40TO-4-4) | 1 | NO | 19.74 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 14 | BENT TUBE(S40TO-4-5) | 1 | NO | 30.46 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 15 | BENT TUBE(S40TO-4-6) | 1 | NO | 18.13 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 17 | BENT TUBE(S40TO-4-8) | 1 | NO | 17.54 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 18 | BENT TUBE(S40TO-5-1) | 1 | NO | 23.03 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 21 | BENT TUBE(S40TO-5-4) | 1 | NO | 19.64 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 22 | BENT TUBE(S40TO-5-5) | 1 | NO | 30.24 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 25 | BENT TUBE(S40TO-5-8) | 0 | NO | 17.39 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 26 | BENT TUBE(S40TO-3-1) | 1 | NO | 23.46 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 29 | BENT TUBE(S40TO-3-4) | 1 | NO | 19.99 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 30 | BENT TUBE(S40TO-3-5) | 1 | NO | 30.08 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 34 | BENT TUBE(S40TO-2-1) | 1 | NO | 23.29 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 37 | BENT TUBE(S40TO-2-4) | 1 | NO | 19.85 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 38 | BENT TUBE(S40TO-2-5) | 1 | NO | 29.91 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 43 | BENT TUBE(S40TO-6-1) | 1 | NO | 23.14 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 46 | BENT TUBE(S40TO-6-4) | 1 | NO | 19.73 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 47 | BENT TUBE(S40TO-6-5) | 1 | NO | 29.84 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 49 | BENT TUBE(S40TO-6-7) | 0 | NO | 17.281 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 51 | BENT TUBE(S40TO-7-1) | 1 | NO | 22.97 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 54 | BENT TUBE(S40TO-7-4) | 1 | NO | 19.59 | INS-89/ Open order, Date-03/01/2020
1717 | 11374 | 55 | BENT TUBE(S40TO-7-5) | 1 | NO | 30.06 | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 1 | SH.PLTN OUTLET TERM TUBE S-33TO-1-1 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 8 | SH.PLTN OUTLET TERM TUBE S-33TO-1-8 | 3 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 9 | SH.PLTN OUTLET TERM TUBE S-33TO-1-9 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 56 | SH.PLTN OUTLET TERM TUBE S-33TO-3-8 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 57 | SH.PLTN OUTLET TERM TUBE S-33TO-3-9 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 61 | SH.PLTN OUTLET TERM TUBE S-33TO-3-13 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 80 | SH.PLTN OUTLET TERM TUBE S-33TO-4-8 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 127 | SH.PLTN OUTLET TERM TUBE S-33TO-6-7 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 147 | SH.PLTN OUTLET TERM TUBE S-33TO-7-3 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 148 | SH.PLTN OUTLET TERM TUBE S-33TO-7-4 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 151 | SH.PLTN OUTLET TERM TUBE S-33TO-7-7 | 0 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 176 | SH.PLTN OUTLET TERM TUBE S-33TO-8-8 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 193 | SH.PLTN OUTLET TERM TUBE S-33TO-9-1 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 11378 | 202 | SH.PLTN OUTLET TERM TUBE S-33TO-9-10 | 1 | NO |  | INS-89/ Open order, Date-03/01/2020
1717 | 12803 | 001 | SH STEAM COOLED SPACER TUBES S-44-1A | 1 | NO | 15.5 | INS-78/ Open order, Date-29/06/2019 | 1ST PRIORITY
1717 | 12803 | 009 | SH STEAM COOLED SPACER TUBES S-44-2A | 1 | NO | 15.5 | INS-78/ Open order, Date-29/06/2019
1717 | 12803 | 025 | SHAPED PL.10 THK | 22 | NO | 18.7 | INS-78/ Open order, Date-29/06/2019
1717 | 10284 | 002 | TUBE OD 38.1 X 8;S-09DR-1 | 1 | NO | 49.6 | INS-78/ Open order, Date-29/06/2019
1717 | 10284 | 003 | TUBE OD 38.1 X 8;S-09DR-2 | 1 | NO | 17.3 | INS-78/ Open order, Date-29/06/2019
1717 | 19906 | 098 | HORIZONTAL PIPE CLAMP | 1 | NO | 99.9 | INS-78/ Open order, Date-29/06/2019
1717 | 19906 | 120 | HORIZONTAL PIPE CLAMP | 1 | NO | 94.49 | INS-78/ Open order, Date-29/06/2019
1717 | 19906 | 128 | HORIZONTAL PIPE CLAMP | 1 | NO | 98.85 | INS-78/ Open order, Date-29/06/2019
1717 | 19906 | 179 | HORIZONTAL PIPE CLAMP | 1 | NO | 94.49 | INS-78/ Open order, Date-29/06/2019
1717 | 12924 | 39 | TIE ROD ASSY D40 | 3 | NO | 78.96 | INS-78/ Open order, Date-29/06/2019
1717 | 24860 | 22 | NB25 NRLV 2500 A A105 SW | 1 | NO | 5 | INS-78/ Open order, Date-29/06/2019
1717 | 16203 | 21 | LTRH INLETTERM TUBE D63.5X4;R-04TI-04 | 1 | NO | 8.8 | INS-89/ Open order, Date-03/01/2020 | 2ND PRIORITY
1717 | 16203 | 22 | LTRH INLETTERM TUBE D63.5X4;R-04TI-08 | 4 | NO | 37.2 | INS-89/ Open order, Date-03/01/2020
1717 | 16203 | 23 | LTRH INLETTERM TUBE D63.5X4;R-04TI-09 | 11 | NO | 116.6 | INS-89/ Open order, Date-03/01/2020
1717 | 16203 | 25 | LTRH INLETTERM TUBE D63.5X4;R-04TI-11 | 4 | NO | 72.8 | INS-89/ Open order, Date-03/01/2020
1717 | 16203 | 26 | LTRH INLETTERM TUBE D63.5X4;R-04TI-12 | 3 | NO | 58.5 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 1 | R-13TO-1-1 | 1 | NO | 25.134 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 4 | R-13TO-1-4 | 9 | NO | 150.705 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 5 | R-13TO-1-5 | 6 | NO | 104.31 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 6 | R-13TO-1-6 | 44 | NO | 189.5 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 9 | R-13TO-1-9 | 7 | NO | 94.885 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 10 | R-13TO-1-10 | 1 | NO | 13.935 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 16 | R-13TO-2-4 | 1 | NO | 16.725 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 39 | R-13TO-4-3 | 1 | NO | 17.833 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 40 | R-13TO-4-4 | 1 | NO | 16.875 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 46 | R-13TO-4-10 | 1 | NO | 13.79 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 47 | R-13TO-4-11 | 1 | NO | 14.045 | INS-89/ Open order, Date-03/01/2020
1717 | 16379 | 83 | R-13TO-7-11 | 1 | NO | 13.69 | INS-89/ Open order, Date-03/01/2020
NOTE-
1 | QUANTITES HIGHLITED YELLOW HAVE BEEN MODIFIED AND FINAL REQUIRED QTY IS MENTIONED NOW

## MDR & SAR
CUST NO | PGMA | DU | DESCRIPTION | QTY | UOM | WEIGHT (KG) | REMARKS | PRIORITY REQUIREMENT
1717 | 16203 | 20 | LTRH INLETTERM TUBE D63.5X4;R-04TI-03 | 90 | NO | 954 | AGAINST MDR-146 | 1ST PRIORITY
1717 | 16203 | 23 | LTRH INLETTERM TUBE D63.5X4;R-04TI-09 | 75 | NO | 795 | AGAINST MDR-146
1717 | 17504 | 12 | VLH SA 10/160 WITH N. TIE ROD C/H =70.9/85.9 | 1 | NO | 137.73 | AGAINST SAR:18:TP:00394
1716 | 11074 | 2 | TUBE D50.8X6.1; (S-39TI-01) | 1 | NO | 14.1 | AGAINST CAR:19:TP:00808
1717 |  |  | GR T-23 TUBE (63.5X4) | 20 | MTRS |  | AGAINST SAR:19:TP:00487
1717 | 45802 | 3 | WINDBOX TOP CORNER 2&4 | 1 | COMPONENT OF WB |  | DIFFUSER FLANGE OF OIL GUN (SS COMPONENT) AGAINST MDR-150 DT-30.03.2015
1717 | 24860 | 62 | ACTUATOR SLEEVE | 1 | COMPONENT OF ACTUATOR |  | AGAINST SAR:18:TP:1080, MATERIAL WAS SENT FROM SITE TO TRICHY FOR THREADING.

## REGULAR SUPPLIES
CUST NO | PGMA | DU | DESCRIPTION | QTY | UOM | REMARKS | PRIORITY REQUIRMENT
1717 | 19907 | 77 | RISER CLAMP | 1 | NOS |  | 1ST PRIORITY
1717 | 24855 | 18 | FLEX HOSE3.0"X4.7M FOR PURGECOOLER-701 | 2 | NOS
1717 | 43004 | 1 | DUPLEX SCNR AIR FILTER | 1 | NOS
1717 | 33021 | 1 | WOOL MATT-100KG/CUM THK:50MM GI WIRENETT | 1283 | M2 |  | REQUIRED BY 05.04.2020
1717 | 33021 | 2 | WOOL MATT-100KG/CUM THK:50MM GI WIRENETT | 2314 | M2 |  | REQUIRED BY 30.04.2020
1717 | 33021 | 3 | WOOL MATT-100KG/CUM THK:60MM GI WIRENETT | 1340 | M2 |  | REQUIRED BY 05.04.2020
1717 | 33021 | 4 | WOOL MATT-100KG/CUM THK:60MM GI WIRENETT | 260 | M2 |  | REQUIRED BY 05.04.2020
1717 | 33021 | 5 | WOOL MATT-100KG/CUM THK:40MM GI WIRENETT | 14 | M2 |  | REQUIRED BY 05.04.2020
1717 | 33021 | 6 | ROCKWOOL MATT-150KG/CU.M 50MM 1SIDEGINET | 34214 | M2 |  | IMMEDIATE
1717 | 33021 | 7 | ROCKWOOL MATT-150KG/CU.M 60MM 1SIDEGINET | 20117 | M2 |  | IMMEDIATE
1717 | 33021 | 8 | ROCKWOOL MAT-150KG/CU.M 60MM 2SIDESSNETT | 2445 | M2 |  | REQUIRED BY 10.03.2020
1717 | 33021 | 9 | ROCKWOOL MAT-150KG/CU.M 50MM 2SIDESSNETT | 7655 | M2 |  | IMMEDIATE
1717 | 33221 | 1 | WOOL MATT-100KG/CUM THK:50MM GI WIRENETT | 11205 | M2 |  | REQUIRED BY 15.04.2020
1717 | 33221 | 2 | WOOL MATT-100KG/CUM THK:50MM GI WIRENETT | 64035 | M2 |  | REQUIRED BY 15.04.2020
1717 | 33221 | 3 | WOOL MATT-100KG/CUM THK:40MM GI WIRENETT | 29775 | M2 |  | IMMEDIATE
1717 | 33221 | 4 | WOOL MATT-100KG/CUM THK:60MM GI WIRENETT | 6305 | M2 |  | REQUIRED BY 15.04.2020