ANNEXURE-I

TECHNICAL SPECIFICATION

Scope: Design, Manufacture and Supply of LT Detuned APFC Panels.

Each 1250 kVAr automatic/manual Power Factor Correction Panel shall be fabricated out of 2mm CRCA Sheets Modular, compartmentalized, Free Standing, Floor Mounting, Front hinged doors for indoor use, removable bottom gland plates for incoming cables, dust and vrmin proof (IP: 42 protection) with TP Aluminium Busbars, complete with busbar connection, internal wiring, name plates, painting etc. generally as per details furnished below:

| Sl.No. | Item | Particulars |
| --- | --- | --- |
| 1 | Rating of APFC Panel | 850 kVAr |
| 2 | Rated Voltage of the Panel | 440 V AC |
| 3 | Frequency | 50 Hz |
| 4 | No.of Phases | 3 Phase |
| 5 | Enclosure details: | Free Standing, Floor mounted, Compartmentalized Design. |
|  | Material | CRCA |
|  | Thickness of Sheet Steel Used: | Frame-2.0mm Doors-2.0mm Partitions-1.6mm |
|  | Dimensions | 3000 (L) x 2200 (H) x 800 (D) (approx) |
|  | Protection | IP-42 |
|  | Application | Indoor |
|  | Cable Entry | Bottom |
|  | Painting | Shade Siemens grey RAL 7032 |
| 6. | Busbar Detail |  |
|  | Material | Aluminium |
|  | Cross Sectoin | 2 x 60 x 10 mm |
|  | Busbar support | SMC |
| 7 | Capacitors |  |
|  | Type | MD-XL,500 V, 3 ph, 50 Hz (Cylindrical) |
|  | No.of Steps | 12 |
|  | Configuration | 2x25kVAr + 4 x 50 kVAr + 6 x 100 kVAr (The capacitors are rates for 500 V due to the effect of detuned reactor and each 25 kVAr, 400 V unit would be designed for 3x10 kVAr, 500V) |
| 8 | Switchgear Details |  |
|  | Incomer | ACB |
|  | Steps Outgoing | SDFs, contactors (Refer Bill of Material for further details) |
| 9 | APFC Relays | 12 Stage Microprocessor based |

ANNEXURE-II

BILL OF MATERIALS

(For 850 kVAr, 440 V, 3Ph, 50 Hz, DETUNED APFC Panel)

| Sl.No. | DESCRIPTION | QTY. | MAKE |
| --- | --- | --- | --- |
|  | INCOMER |  |  |
| 1. | ACB Type C-Power, 1000A, MDO type with DN1 releases | 1 No. | L&T/Siemens/ABB |
| 2 | Analog Ammeter (0-1000A) | 1 No. | RISHAB |
| 3 | Analog Voltmeter (0-600 V) | 1 No. | RISHAB |
| 4 | Phase Indicating Lamps | 3 Nos. | ESBEE/TEKNIC |
| 5 | Ammeter S/S / Voltmeter S/S | 1 Each | SALZER |
| 6 | Auto/Off/Manual Switch | 1 No. | SALZER |
| 7 | Current Transformer (1000/5A) | 3 Nos. | PRECISE/KALPA |
| 8 | APFC Relay (12-Stage) | 1 No. | BELUK |
| 9 | Timer | 1 No. | GIC |
| 10 | Cooling Fans | 1 Lot | NADI/REPUTED |
|  | OUTGOING |  |  |
| 1 | Indicating Lamps (ON.OFF) | 24 Nos. | ESBEE/TEKNIC |
| 2 | Push Bottons (ON/OFF) | 24 Nos. | ESBEE/TEKNIC |
|  | FOR 25 kVAr – 2 STEPS |  |  |
| 1 | SDF type FN 63 | 2 Nos. | L&T/ABB/Siemens |
| 2 | Contactor MNX-45 | 2 Nos. | L&T/ABB/Siemens |
| 3 | 7% reactor for 25 kVAr filter | 2 Nos. | MEHER/ABB |
|  | FOR 50 kVAr – 4 STEPS |  |  |
| 1 | SDF type FN 125 | 4 Nos. | L&T/ABB/Siemens |
| 2 | Contactor MNX-95 | 4 Nos. | L&T/ABB/Siemens |
| 3 | 7% reactor for 50 kVAr filter | 4 Nos. | MEHER/ABB |
|  | FOR 100 kVAr – 6 STEPS |  |  |
| 1 | SDF type FN 250 | 6 Nos. | L&T/ABB/Siemens |
| 2 | Contactor MNX-185 | 6 Nos. | L&T/ABB/Siemens |
| 3 | 7% reactor for 100 kVAr filter | 6 Nos. | MEHER/ABB |