## Sheet1
FORM NO. EPD-1000-101
|  | MANUFACTURER: |  |  | MANUFACTURING QUALITY PLAN |  |  |  | CUSTOMER : RAJASHTHAN RAJYA VIDUT UTPADAN
|  | BHARAT HEAVY ELECTRICALS LTD. | [6 empty] | NIGAM LTD. (RRVUNL)
|  | ELECTROPORCELAINS DIVISION |  |  | ITEM : | QUALITY PLAN NUMBER : |  | PAGE NO. | CONSULTANT : : TATA CONSULTING ENGINEERS LIMITED (TCE)
|  | BANGALORE 560012 |  |  | LV BUSDUCT | EP-3-QP-066-002 REV-00 |  | 1 OF 6 | PROJECT: 2x660 MW SURATGARH STPS UNIT 7&8
SL. | COMPONENT/OPERATION |  | CHARACTERISTICS | CAT. | TYPE/ | EXTENT OF | REFERENCE | ACCEPTANCE | FORMAT | AGENCY |  |  | REMARKS
NO. |  |  | CHECK |  | METHOD OF | CHECK | DOCUMENT | NORM | OF RECORD
[5 empty] | CHECK |  |  |  |  | M | T | C
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11
1.0 | MATERIALS/COMPONENTS
1.1 | ALUMINIUM AND COPPER |  | 1. DIMENSION | MA | MEASUREMENT | 100% | SPEC.S./ | SPEC.S./ | LOG BOOK | P | V | V | `
| BUSBAR & FLEXIBLES |  | CHECK 7: IS:5082/IS:736; CHECK 8: IS:5082/IS:736
[7 empty] | IS:737/IS:1897 | IS:737/IS:1897
|  |  | 2.SURFACE FINISH | MA | VISUAL | 10% | -DO- | -DO- | -DO- | P | V | V
|  |  | 3.FLATNESS | MA | VISUAL | 10% | -DO- | -DO- | -DO- | P | V | V
|  |  | 4. BEND TEST | MA | MEASUREMENT | SAMPLE | -DO- | -DO- | SUPPLIER TC | V | V | V
|  |  | 5.ELECTRICAL | MA | ELECTRICAL | SAMPLE | -DO- | -DO- | SUPPLIER TC | V | V | V
CONDUCTIVITY
1.2 | ENCLOSURE MATERIALS |  | 1. DIMENSION | MA | MEASUREMENT | 10% | IS:513 | IS:513 | LOG BOOK | P | V | V
[7 empty] | SPECS. | SPECS.
|  |  | 2.SURFACE FINISH | MA | VISUAL | 10% | -DO- | -DO- | -DO- | P | V | V
|  |  | 3.FLATNESS | MA | VISUAL | 10% | -DO- | -DO- | -DO- | P | V | V
|  |  | 4.BEND TEST | MA | MEASUREMENT | 1PIECE/LOT | -DO- | -DO- | SUPPLIER TC | P | V | V
(MS ONLY)
|  |  | 5. TENSILE STRENGTH, | MA | MEASUREMENT | SAMPLE | -DO- | -DO- | SUPPLIER TC | V | V | V
PERCENTAGE ELONGATION
1.3 | INSULATORS, SEAL OFF |  | 1.ROUTINE TEST | MA | ELECTRICAL/ | 10% | SPEC.S./ | SPEC.S./ | LOG BOOK | P | V | V
| BUSHING, CABLES, WIRES, |  | CHECK 5: MEASUREMENT; CHECK 7: RELEV IS; CHECK 8: RELEV. IS
SPACE HEATERS
|  |  | 2.RATING & MAKE | MA | VISUAL | 10% | SPEC.S./ | SPEC.S./ | -DO- | P | V | V
[7 empty] | RELEV. IS/PHY. | RELEV. IS/PHY.
[7 empty] | CONDITION | CONDITION
LEGEND:
M: MANUFACTURER-VENDOR, T: CONSULTANT: TCE & BHEL, C: CUSTOMER: RRVUNL
P: PERFORM, W: WITNESS, V: VERIFICATION
CR - CRITICAL, MA - MAJOR, MI - MINOR
MANUFACTURER/ SIGNATURE |  |  | CHECK 9: APPROVED BY |  |  | APPROVAL SEAL
FORM NO. EPD-1000-101
|  | MANUFACTURER: | CHECK 5: MANUFACTURING QUALITY PLAN; CHECK 9: CUSTOMER : RAJASHTHAN RAJYA VIDUT UTPADAN
|  | BHARAT HEAVY ELECTRICALS LTD. | CHECK 9: NIGAM LTD. (RRVUNL)
|  | ELECTROPORCELAINS DIVISION | CHECK 5: ITEM :; CHECK 6: QUALITY PLAN NUMBER :; CHECK 8: PAGE NO.; CHECK 9: CONSULTANT : : TATA CONSULTING ENGINEERS LIMITED (TCE)
|  | BANGALORE 560012 | CHECK 5: LV BUSDUCT; CHECK 6: EP-3-QP-066-002 REV-00; CHECK 8: 2 OF 6; CHECK 9: PROJECT: 2x660 MW SURATGARH STPS UNIT 7&8
SL. | COMPONENT/OPERATION |  | CHARACTERISTICS | CAT. | TYPE/ | EXTENT OF | REFERENCE | ACCEPTANCE | FORMAT | AGENCY |  |  | REMARKS
NO. |  |  | CHECK |  | METHOD OF | CHECK | DOCUMENT | NORM | OF RECORD
|  |  | CHECK 5: CHECK; M 10: M | T | C
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11
|  |  | 4.TRACKING INDEX (FOR | MA | ELECTRICAL | SAMPLE | SPEC.S./ | SPEC.S./ | SUPPLIER TC | V | V | V
|  |  | INSULATION MATERIAL) |  |  |  | RELEV. IS | RELEV. IS
1.4 | RUBBER BELLOWS, PLAIN |  | 1.DIMENSION | MA | MEASUREMENT | RANDOM | -DO- | -DO- | LOG BOOK | P | V | V
| & SPRING, WASHERS & |  | CHECK 6: CHECK
FASTENERS, DISC WASHERS
|  |  | 2.SURFACE | MA | VISUAL | -DO- | -DO- | -DO- | -DO- | P | V | V
FINISH
|  |  | 3.SHORE | MA | MEASUREMENT | SAMPLE | MANUFS STD | MANUFS STD | LOG BOOK | P | V | V
HARDNESS
1.5 | NEOPRENE RUBBER |  | 1.OIL ABSORPTION | MA | MEASUREMENT | 1PIECE/ LOT | IS-3400/ | IS-3400/ | SUPPLIER TC | V | V | V
| BELLOWS & GASKET |  | CHECK 7: SPEC./BS-2752; CHECK 8: SPEC./BS-2752
|  |  | 2.AGEING TEST | MA | AGEING TEST | -DO- | -DO- | -DO- | -DO- | P | V | V
1.6 | BUS BAR SLEEVES |  | 1. DIMENSION & | MA | MEAS & TESTS | 1/LOT | MANUFS STD | MANUFS STD | SUPPLIER TC | V | V | V
|  |  | MATERIAL |  |  |  | RELV. STD | RELV. STD
CERTIFICATE
2.0 | IN-PROCESS
2.1 | FABRICATION OF |  | 1. DIMENSION | MA | MEASUREMENT | 100% | APPD./MFG DRG | APPD./MFG DRG | LOG BOOK | P | V | V | Manufactured by Sub-vendor
ENCLOSURES
LEGEND:
M: MANUFACTURER-VENDOR, T: CONSULTANT: TCE & BHEL, C: CUSTOMER: RRVUNL
P: PERFORM, W: WITNESS, V: VERIFICATION
CR - CRITICAL, MA - MAJOR, MI - MINOR
MANUFACTURER/ SIGNATURE |  |  | CHECK 9: APPROVED BY |  |  | APPROVAL SEAL
FORM NO. EPD-1000-101
|  | MANUFACTURER: | CHECK 5: MANUFACTURING QUALITY PLAN; CHECK 9: CUSTOMER : RAJASHTHAN RAJYA VIDUT UTPADAN
|  | BHARAT HEAVY ELECTRICALS LTD. | CHECK 9: NIGAM LTD. (RRVUNL)
|  | ELECTROPORCELAINS DIVISION | CHECK 5: ITEM :; CHECK 6: QUALITY PLAN NUMBER :; CHECK 8: PAGE NO.; CHECK 9: CONSULTANT : : TATA CONSULTING ENGINEERS LIMITED (TCE)
|  | BANGALORE 560012 | CHECK 5: LV BUSDUCT; CHECK 6: EP-3-QP-066-002 REV-00; CHECK 8: 3 OF 6; CHECK 9: PROJECT: 2x660 MW SURATGARH STPS UNIT 7&8
SL. | COMPONENT/OPERATION |  | CHARACTERISTICS | CAT. | TYPE/ | EXTENT OF | REFERENCE | ACCEPTANCE | FORMAT | AGENCY |  |  | REMARKS
NO. |  |  | CHECK |  | METHOD OF | CHECK | DOCUMENT | NORM | OF RECORD
|  |  | CHECK 5: CHECK; M 10: M | T | C
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11
|  |  | 2.FINISH | MA | VISUAL | 100% | MANUF'S STD | MANUF'S STD | LOG BOOK | P | V | V | Manufactured by Sub-vendor
|  |  | 3.ALIGNMENT | MA | VISUAL & | 100% | -DO- | -DO- | -DO- | P | V | V | -DO-
MEASUREMENT
|  |  | 4.ORIENTATION | MA | VISUAL | 100% | -DO- | -DO- | -DO- | P | V | V | -DO-
2.2 | SURFACE PREPARATION |  | 1.PROCESS | MA | PROCESS | PERIODIC | IS-6005 | IS-6005 | SUPPLIER TC | P | V | V | -DO-
| INCLUDING PHOSPHATING |  | 3: PARAMETERS; CHECK 5: CHECKS; CHECK 7: RELV. IS; CHECK 8: RELV. IS
| & PASSIVATION |  | 3: (SOLUTION
STRENGTH TEMP.
TIME ETC.
|  |  | 2.SURFACE | MA | VISUAL | RANDOM | -DO- | -DO- | LOG BOOK | P | V | V | -DO-
|  |  | CONDITION |  |  | CHECK
2.3 | INITIAL PAINTING (PRIMER) |  | 1.SURFACE FINISH | MA | VISUAL | RANDOM | -DO- | -DO- | -DO- | P | V | V | -DO-
|  |  | & COVERAGE |  |  | CHECK
|  |  | 2.FILM | MA | MEASUREMENT | RANDOM | -DO- | -DO- | -DO- | P | V | V | -DO-
|  |  | THICKNESS |  |  | CHECK
2.4 | FINISHING OF BUSBARS/ |  | 1.TYPE OF | MA | VISUAL | RANDOM | SPEC./FAB | SPEC./FAB | -DO- | P | V | V | -DO-
| FLEXIBLES (TINNING/ |  | 3: FINISH; CHECK 6: CHECK; CHECK 7: DRG/IS SPEC.; CHECK 8: DRG/IS SPEC.
PLATING,/PAINTING/
SLEEVING)
3.0 | ASSEMBLY
3.1 | BUSBAR ASSEMBLY |  | 1.PHASE | MA | VERIFICATION | 100% | ASSEMBLY DRG/ | ASSEMBLY DRG/ | LOG BOOK | P | V | V
|  |  | SEQUENCE |  |  |  | SPEC.. | SPEC..
[7 empty] | BS-159/BS-162 | BS-159/BS-162
LEGEND:
M: MANUFACTURER-VENDOR, T: CONSULTANT: TCE & BHEL, C: CUSTOMER: RRVUNL
P: PERFORM, W: WITNESS, V: VERIFICATION
CR - CRITICAL, MA - MAJOR, MI - MINOR
MANUFACTURER/ SIGNATURE |  |  | CHECK 9: APPROVED BY |  |  | APPROVAL SEAL
FORM NO. EPD-1000-101
|  | MANUFACTURER: | CHECK 5: MANUFACTURING QUALITY PLAN; CHECK 9: CUSTOMER : RAJASHTHAN RAJYA VIDUT UTPADAN
|  | BHARAT HEAVY ELECTRICALS LTD. | CHECK 9: NIGAM LTD. (RRVUNL)
|  | ELECTROPORCELAINS DIVISION | CHECK 5: ITEM :; CHECK 6: QUALITY PLAN NUMBER :; CHECK 8: PAGE NO.; CHECK 9: CONSULTANT : : TATA CONSULTING ENGINEERS LIMITED (TCE)
|  | BANGALORE 560012 | CHECK 5: LV BUSDUCT; CHECK 6: EP-3-QP-066-002 REV-00; CHECK 8: 4 OF 6; CHECK 9: PROJECT: 2x660 MW SURATGARH STPS UNIT 7&8
SL. | COMPONENT/OPERATION |  | CHARACTERISTICS | CAT. | TYPE/ | EXTENT OF | REFERENCE | ACCEPTANCE | FORMAT | AGENCY |  |  | REMARKS
NO. |  |  | CHECK |  | METHOD OF | CHECK | DOCUMENT | NORM | OF RECORD
|  |  | CHECK 5: CHECK; M 10: M | T | C
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11
|  |  | 2.BUSBAR MARKING | MA | VISUAL | 100% | -DO- | -DO- | -DO- | P | V | V
|  |  | 3.TIGHTNESS OF | MA | MECHANICAL | 100% | -DO- | -DO- | -DO- | P | V | V
SUPPORTS
|  |  | 4.SURFACE | MA | VISUAL | 100% | MANUF'S STD | MANUF'S STD | -DO- | P | V | V | Manufactured by Sub-vendor
PREPARATION FOR
JOINT PREPERATION
& APPLYING
CONDUCTING
MEDIUM
|  |  | 5.TIGHTNESS OF | MA | MECHANICAL | 100% | SPEC.. | SPEC.. | -DO- | P | V | V
|  |  | JOINTS AND |  |  |  | MANUFS STD | MANUFS STD
FLEXIBLE
|  |  | 6.CLEARANCE TO | MA | MEASUREMENT | 100% | -DO- | -DO- | -DO- | P | V | V
BODY /EARTH
& PHASE TO
PHASE
3.2 | EARTHING |  | 1.SIZE & | MA | MEASUREMENT | 100% | SPEC.. | SPEC.. | LOG BOOK | P | V | V
|  |  | MATERIAL |  |  |  | ASSEMBLY DRG. | ASSEMBLY DRG.
|  |  | 2.LOCATION | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
|  |  | 3.MARKINGS | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
|  |  | 4.TERMINATIONS | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
|  |  | 5.TIGHTNESS | MA | MECHANICAL | 100% | -DO- | -DO- | -DO- | P | V | V
TO SUPPORTS
LEGEND:
M: MANUFACTURER-VENDOR, T: CONSULTANT: TCE & BHEL, C: CUSTOMER: RRVUNL
P: PERFORM, W: WITNESS, V: VERIFICATION
CR - CRITICAL, MA - MAJOR, MI - MINOR
MANUFACTURER/ SIGNATURE |  |  | CHECK 9: APPROVED BY |  |  | APPROVAL SEAL
FORM NO. EPD-1000-101
|  | MANUFACTURER: | CHECK 5: MANUFACTURING QUALITY PLAN; CHECK 9: CUSTOMER : RAJASHTHAN RAJYA VIDUT UTPADAN
|  | BHARAT HEAVY ELECTRICALS LTD. | CHECK 9: NIGAM LTD. (RRVUNL)
|  | ELECTROPORCELAINS DIVISION | CHECK 5: ITEM :; CHECK 6: QUALITY PLAN NUMBER :; CHECK 8: PAGE NO.; CHECK 9: CONSULTANT : : TATA CONSULTING ENGINEERS LIMITED (TCE)
|  | BANGALORE 560012 | CHECK 5: LV BUSDUCT; CHECK 6: EP-3-QP-066-002 REV-00; CHECK 8: 5 OF 6; CHECK 9: PROJECT: 2x660 MW SURATGARH STPS UNIT 7&8
SL. | COMPONENT/OPERATION |  | CHARACTERISTICS | CAT. | TYPE/ | EXTENT OF | REFERENCE | ACCEPTANCE | FORMAT | AGENCY |  |  | REMARKS
NO. |  |  | CHECK |  | METHOD OF | CHECK | DOCUMENT | NORM | OF RECORD
|  |  | CHECK 5: CHECK; M 10: M | T | C
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11
3.3 | IDENTIFICATION MARKINGS |  | 1.SECTIONAL | MA | VISUAL | 100% | -DO- | -DO- | LOG BOOK | P | V | V
| & NAME PLATES |  | 3: IDENTIFICATION
|  |  | 2.EARTH | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
MARKING
|  |  | 3.BUSBAR | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
MARKING
|  |  | 4.NAME PLATES | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
AND DANGER
NAME PLATES
4.0 | COMPLETE ASSEMBLY
4.1 | PHYSICAL |  | 1.DIMENSIONS & VISUAL | MA | MEASUREMENT | 100% | APPD.DRG. | APPD..DRG. | LOG BOOK | P | V | V
LOG SHEET
|  |  | 2.COMPLETE | MA | VISUAL | 100% | SPEC. | SPEC. | - | P | V | V
|  |  | LAYOUT |  |  |  | LAYOUT DRGS/ | LAYOUT DRGS/
[7 empty] | FAB.DRG. | FAB.DRG.
|  |  | 3.GENERAL & | MA | VISUAL | 100% | -DO- | -DO- | LOG BOOK | P | V | V
MARKING-
APPEARANCE
|  |  | 4.FITTING OF | MA | VISUAL | 100% | -DO- | -DO- | -DO- | P | V | V
INSPN.COVERS
|  |  | 5.ALIGNMENT OF | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
SECTION
|  |  | 6.EARTH BUS | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
ALIGNMENTS &
MARKING
LEGEND:
M: MANUFACTURER-VENDOR, T: CONSULTANT: TCE & BHEL, C: CUSTOMER: RRVUNL
P: PERFORM, W: WITNESS, V: VERIFICATION
CR - CRITICAL, MA - MAJOR, MI - MINOR
MANUFACTURER/ SIGNATURE |  |  | CHECK 9: APPROVED BY |  |  | APPROVAL SEAL
FORM NO. EPD-1000-101
|  | MANUFACTURER: | CHECK 5: MANUFACTURING QUALITY PLAN; CHECK 9: CUSTOMER : RAJASHTHAN RAJYA VIDUT UTPADAN
|  | BHARAT HEAVY ELECTRICALS LTD. | CHECK 9: NIGAM LTD. (RRVUNL)
|  | ELECTROPORCELAINS DIVISION | CHECK 5: ITEM :; CHECK 6: QUALITY PLAN NUMBER :; CHECK 8: PAGE NO.; CHECK 9: CONSULTANT : : TATA CONSULTING ENGINEERS LIMITED (TCE)
|  | BANGALORE 560012 | CHECK 5: LV BUSDUCT; CHECK 6: EP-3-QP-066-002 REV-00; CHECK 8: 6 OF 6; CHECK 9: PROJECT: 2x660 MW SURATGARH STPS UNIT 7&8
SL. | COMPONENT/OPERATION |  | CHARACTERISTICS | CAT. | TYPE/ | EXTENT OF | REFERENCE | ACCEPTANCE | FORMAT | AGENCY |  |  | REMARKS
NO. |  |  | CHECK |  | METHOD OF | CHECK | DOCUMENT | NORM | OF RECORD
|  |  | CHECK 5: CHECK; M 10: M | T | C
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11
|  |  | 7.MARKINGS ON | MA | VISUAL | 100% | -DO- | -DO- | - | P | V | V
THE SECTIONS
|  |  | 8.PAINT | MA | VISUAL | RANDOM | APPD.DRGS/ | APPD.DRGS/ | LOG BOOK | P | V | V
|  |  | THICKNESS |  |  | SAMPLE | SPEC. | SPEC.
SHADE
|  |  | 9.ADHESION | MA | SCRATCH TEST | RANDOM | -DO- | -DO- | -DO- | P | V | V
SAMPLE
4.2 | TESTS |  | 3: 1. ROUTINE TESTS
|  |  | A) INSULATOR CLEARANCE | MA | MEASURMENT | 100% | APPD.DRGS/ | APPD.DRGS/ | LOG BOOK | P | W | W
|  |  | B) CONTINUITY TEST |  | ELECTRICAL | 100% | APPD.DRGS/ | APPD.DRGS/ | LOG BOOK | P | W | W
|  |  | ON AUXILIARY CIRCUIT |  |  |  | SPEC. | SPEC.
|  |  | C) HV (2.5 kV for 1 min.)&IR | MA | ELECTRICAL | 100% | APPD.DRGS/ | APPD.DRGS/ | TC | P | W | W
|  |  | FOR BUSBAR |  |  |  | SPEC. | SPEC.
|  |  | D). HV (1.5 kV for 1 min.)&IR | MA | ELECTRICAL | 100% | -DO- | -DO- | TC | P | W | W
FORSPACE HEATER
|  |  | 2.MILLIVOLT DROP | MA | ELECTRICAL | SAMPLE | -DO- | -DO- | LOG BOOK | P | W | W
TEST
4.3 | TYPE TEST |  | 1. TEMPERATURE | MA | ELECTRICAL | SAMPLE | -DO- | -DO- | TC | P | V | V
RISE / HEAT RUN TEST
|  |  | 2. DEGREE OF | MA | AS PER SPEC | SAMPLE | -DO- | -DO- | TC | P | V | V
PROTECTION
|  |  | 3. SHORT CKT | MA | ELECTRICAL | SAMPLE | -DO- | -DO- | TC | P | V | V
TEST
5.0 | IDENTIFICATION, |  | 1.IDENTIFICATION | MA | VISUAL | 100% | PURCHASER'S | PURCHASER'S | LOG BOOK | P
| PRESERVATION |  | 3: MARKING ON; CHECK 7: INSTRUCTION; CHECK 8: INSTRUCTION
| & PACKING |  | 3: PACKING
CASES
LEGEND:
M: MANUFACTURER-VENDOR, T: CONSULTANT: TCE & BHEL, C: CUSTOMER: RRVUNL
P: PERFORM, W: WITNESS, V: VERIFICATION
CR - CRITICAL, MA - MAJOR, MI - MINOR
MANUFACTURER/ SIGNATURE |  |  | CHECK 9: APPROVED BY |  |  | APPROVAL SEAL