## Sheet1
FORM NO. EPD-1000-101
|  | MANUFACTURER: As Approved Vendor |  |  | MANUFACTURING QUALITY PLAN |  |  |  | CUSTOMER : RAJASHTHAN RAJYA VIDUT UTPADAN
NIGAM LTD. (RRVUNL)
[5 empty] | ITEM : FLAME | QUALITY PLAN NUMBER : |  | PAGE NO. | CONSULTANT : : TATA CONSULTING ENGINEERS LIMITED (TCE)
[5 empty] | PROOF LPBS TYPE-C | EP-3-QP-066-003 |  | 1 OF 1 | SUPPLSER : BHEL - EPD, BANGALORE
PROJECT: 2x660 MW SURATGARH STPS UNIT 7&8
SL. | COMPONENT/OPERATION |  | CHARACTERISTIC | CAT. | TYPE/ | EXTENT OF | REFERENCE | ACCEPTANCE | FORMAT | AGENCY |  |  |  | REMARKS
NO. |  |  | CHECK |  | METHOD OF | CHECK | DOCUMENT | NORM | OF RECORD | M | B | T | C
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  |  | 11
1.0 | RAW MATERIAL & BOUGHTOUT CONTROL
1.1 | AL ALLOY LM-6 CASTING |  | 1. CHEMICAL COMPOSITION | MA | CHEM. TEST | LOT WISE | RELEVANT IS | RELEVANT IS | LAB TEST REPORT | P | - | - | -
|  |  | 2. DIMENSIONS | MA | VISUAL | 100% | APPROVAD GAD | GAD | WORK RECORD | P | - | - | -
|  |  | 3. THICKNESS | MA | MEASUREMENT | 100% | APPROVAD GAD | GAD | WORK RECORD | P | - | - | -
1.2 | GASKET |  | 1. DIMENSIONS | MA | MEASUREMENT | 100% | COMP.DRAWING | COMP. DRAWING | WORK RECORD | P | - | - | -
1.3 | SCREW / HARDWARE |  | 1. DIMENSIONS | MA | VISUAL | SAMPLING | STANDARD GAUGE | STANDARD GAUGE | WORK RECORD | P | - | - | -
1.4 | ELECTRICAL / TERMINAL |  | 1. GENERAL | MI | VISUAL | SAMPLING | MFGR. STANDARD | MFGR. STANDARD | WORK RECORD | P | - | - | -
2 | IN-PROCESS CONTROLS
2.1 | HOUSING MACHINIG |  | 1. DIMENSIONS | MA | MEASURE | 100% | APPROVAD GAD | APPROVAD GAD | WORK RECORD | P | - | - | -
|  |  | 2. CABLE ENTRIES | CR | MEASURE | 100% | THREAD GAUGE | THREAD GAUGE | WORK RECORD | P | - | - | -
|  |  | 3. FLAME PATH & GAP | CR | MEASURE | 100% | IS/IEC 60079-1 | IS/IEC 60079-1 | WORK RECORD | P | - | - | -
2.2 | HYDRAULIC TEST |  | 1. UPTO 10 KG/CM2 | CR | TESTING | 100% | TYPE TEST CERTI. | IS/IEC 60079-1 | WORK RECORD | P | - | - | -
2.3 | PAINTING |  | 1. SURFACE PREPARATION | MA | VISUAL | 100% | VISUAL | VISUAL | WORK RECORD | P | - | - | -
|  |  | 2. FINAL FINISH | MA | VISUAL | 100% | VISUAL | VISUAL | WORK RECORD | P | - | - | -
2.4 | ASSEMBLY (Inclluding Electricals) |  | 1. COMPONENT MOUNTING | MA | VISUAL | 100% | APPROVAD GAD | APPROVAD GAD | WORK RECORD
3 | FINAL INSPECTION
3.1 | FINAL DIMENSIONS |  | 1. ENCLOSURE DIMENSION | MA | MEASURE | 100% | APPROVAD GAD | APPROVAD GAD | WORK RECORD | P | V | V | V
|  |  | 2. CABLE ENTRY | CR | MEASURE | 100% | APPROVAD GAD | THREAD GAUGE | WORK RECORD | P | V | V | V
|  |  | 3. COMPONENT MOUNTING | CR | VISUAL | 100% | APPROVAD GAD | APPROVAD GAD | WORK RECORD | P | V | V | V
3.2 | PAINTING |  | 1. SURFACE FINISH | MA | VISUAL | 100% | APPROVAD GAD | APPROVAD GAD | WORK RECORD | P | V | V | V
(Powder Coating)
|  |  | 2. PAINT FINISH | MA | VISUAL | 100% | APPROVAD GAD | APPROVAD GAD | WORK RECORD | P | V | V | V
3.3 | ROUTINE TEST |  | 1. HV ELECTRICAL RUN | MA | TEST | 100% | - | 2KV for 1Minute | WORK RECORD | P | W | W | W
|  |  | 2. IR ELECTRICAL RUN | MA | TEST | 100% | - | > 50 M Ω | WORK RECORD | P | W | W | W
4 | FINAL DOCUMENT
| TYPE TEST REPORTS (Flameproof to Ex d IIB T6 Gb as per IS/IEC 60079-1-2007) | [9 empty] | V | V | V | bar: 10
| SUPPLIER TC's OF BOUGHT OUT ITEM, if any | [9 empty] | V | V | V | bar: 10
| WORKS INSPECTION TEST REPORTS | [9 empty] | V | V | V | bar: 10
| AS BUILT DRAWING | [9 empty] | V | V | V | bar: 10
5 | MATERIAL RELEASE ORDER | [9 empty] | - | P | P | bar: 10
LEGEND:
M: MANUFACTURER-VENDOR, T: CONSULTANT: TCE & BHEL, C: CUSTOMER: RRVUNL
P: PERFORM, W: WITNESS, V: VERIFICATION
CR - CRITICAL, MA - MAJOR, MI - MINOR
MANUFACTURER/ SIGNATURE |  |  | 9: APPROVED BY |  |  | APPROVAL SEAL